## Cooling
Model | Tons | CFM | EAT DB (°F) | EAT WB (°F) | OA DB (°F) | MBh | S/T | ∆T (°F) | Sensible MBh | Total Input (kW) | Source Page
KJ037 | 3 | 750 | 65 | 62 | 75 | 33.8 | 0.456 | 19.01 | 15.4 | 1.8 | 25
KJ037 | 3 | 750 | 70 | 62 | 75 | 33.8 | 0.571 | 23.83 | 19.3 | 1.8 | 25
KJ037 | 3 | 750 | 75 | 62 | 75 | 33.8 | 0.683 | 28.52 | 23.1 | 1.8 | 25
KJ037 | 3 | 750 | 80 | 62 | 75 | 33.8 | 0.802 | 33.46 | 27.1 | 1.8 | 25
KJ037 | 3 | 750 | 85 | 62 | 75 | 33.8 | 0.959 | 40 | 32.4 | 1.8 | 25
KJ037 | 3 | 750 | 90 | 62 | 75 | 33.8 | 1 | 41.73 | 33.8 | 1.8 | 25
KJ037 | 3 | 750 | 70 | 67 | 75 | 37.7 | 0.403 | 18.77 | 15.2 | 1.8 | 25
KJ037 | 3 | 750 | 75 | 67 | 75 | 37.7 | 0.509 | 23.7 | 19.2 | 1.8 | 25
KJ037 | 3 | 750 | 80 | 67 | 75 | 37.7 | 0.615 | 28.64 | 23.2 | 1.8 | 25
KJ037 | 3 | 750 | 85 | 67 | 75 | 37.7 | 0.735 | 34.2 | 27.7 | 1.8 | 25
KJ037 | 3 | 750 | 90 | 67 | 75 | 37.7 | 0.854 | 39.75 | 32.2 | 1.8 | 25
KJ037 | 3 | 750 | 75 | 72 | 75 | 42.2 | 0.36 | 18.77 | 15.2 | 1.8 | 25
KJ037 | 3 | 750 | 80 | 72 | 75 | 42.2 | 0.457 | 23.83 | 19.3 | 1.8 | 25
KJ037 | 3 | 750 | 85 | 72 | 75 | 42.2 | 0.552 | 28.77 | 23.3 | 1.8 | 25
KJ037 | 3 | 750 | 90 | 72 | 75 | 42.2 | 0.649 | 33.83 | 27.4 | 1.8 | 25
KJ037 | 3 | 750 | 80 | 77 | 75 | 46.6 | 0.328 | 18.89 | 15.3 | 1.8 | 25
KJ037 | 3 | 750 | 85 | 77 | 75 | 46.6 | 0.408 | 23.46 | 19 | 1.8 | 25
KJ037 | 3 | 750 | 90 | 77 | 75 | 46.6 | 0.485 | 27.9 | 22.6 | 1.8 | 25
KJ037 | 3 | 750 | 65 | 62 | 85 | 33.1 | 0.426 | 17.41 | 14.1 | 2 | 25
KJ037 | 3 | 750 | 70 | 62 | 85 | 33.1 | 0.547 | 22.35 | 18.1 | 2 | 25
KJ037 | 3 | 750 | 75 | 62 | 85 | 33.1 | 0.671 | 27.41 | 22.2 | 2 | 25
KJ037 | 3 | 750 | 80 | 62 | 85 | 33.1 | 0.795 | 32.47 | 26.3 | 2 | 25
KJ037 | 3 | 750 | 85 | 62 | 85 | 33.1 | 0.934 | 38.15 | 30.9 | 2 | 25
KJ037 | 3 | 750 | 90 | 62 | 85 | 33.1 | 1 | 40.86 | 33.1 | 2 | 25
KJ037 | 3 | 750 | 70 | 67 | 85 | 35.5 | 0.403 | 17.65 | 14.3 | 2 | 25
KJ037 | 3 | 750 | 75 | 67 | 85 | 35.5 | 0.515 | 22.59 | 18.3 | 2 | 25
KJ037 | 3 | 750 | 80 | 67 | 85 | 35.5 | 0.628 | 27.53 | 22.3 | 2 | 25
KJ037 | 3 | 750 | 85 | 67 | 85 | 35.5 | 0.758 | 33.21 | 26.9 | 2 | 25
KJ037 | 3 | 750 | 90 | 67 | 85 | 35.5 | 0.885 | 38.77 | 31.4 | 2 | 25
KJ037 | 3 | 750 | 75 | 72 | 85 | 40 | 0.36 | 17.78 | 14.4 | 2 | 25
KJ037 | 3 | 750 | 80 | 72 | 85 | 40 | 0.46 | 22.72 | 18.4 | 2 | 25
KJ037 | 3 | 750 | 85 | 72 | 85 | 40 | 0.56 | 27.65 | 22.4 | 2 | 25
KJ037 | 3 | 750 | 90 | 72 | 85 | 40 | 0.66 | 32.59 | 26.4 | 2 | 25
KJ037 | 3 | 750 | 80 | 77 | 85 | 44.4 | 0.324 | 17.78 | 14.4 | 2 | 25
KJ037 | 3 | 750 | 85 | 77 | 85 | 44.4 | 0.403 | 22.1 | 17.9 | 2 | 25
KJ037 | 3 | 750 | 90 | 77 | 85 | 44.4 | 0.482 | 26.42 | 21.4 | 2 | 25
KJ037 | 3 | 750 | 65 | 62 | 95 | 32.5 | 0.391 | 15.68 | 12.7 | 2.3 | 26
KJ037 | 3 | 750 | 70 | 62 | 95 | 32.5 | 0.523 | 20.99 | 17 | 2.3 | 26
KJ037 | 3 | 750 | 75 | 62 | 95 | 32.5 | 0.652 | 26.17 | 21.2 | 2.3 | 26
KJ037 | 3 | 750 | 80 | 62 | 95 | 32.5 | 0.785 | 31.48 | 25.5 | 2.3 | 26
KJ037 | 3 | 750 | 85 | 62 | 95 | 32.5 | 0.905 | 36.3 | 29.4 | 2.3 | 26
KJ037 | 3 | 750 | 90 | 62 | 95 | 32.5 | 1 | 40.12 | 32.5 | 2.3 | 26
KJ037 | 3 | 750 | 70 | 67 | 95 | 33.3 | 0.399 | 16.42 | 13.3 | 2.3 | 26
KJ037 | 3 | 750 | 75 | 67 | 95 | 33.3 | 0.523 | 21.48 | 17.4 | 2.3 | 26
KJ037 | 3 | 750 | 80 | 67 | 95 | 33.3 | 0.646 | 26.54 | 21.5 | 2.3 | 26
KJ037 | 3 | 750 | 85 | 67 | 95 | 33.3 | 0.784 | 32.22 | 26.1 | 2.3 | 26
KJ037 | 3 | 750 | 90 | 67 | 95 | 33.3 | 0.922 | 37.9 | 30.7 | 2.3 | 26
KJ037 | 3 | 750 | 75 | 72 | 95 | 37.7 | 0.358 | 16.67 | 13.5 | 2.3 | 26
KJ037 | 3 | 750 | 80 | 72 | 95 | 37.7 | 0.464 | 21.6 | 17.5 | 2.3 | 26
KJ037 | 3 | 750 | 85 | 72 | 95 | 37.7 | 0.57 | 26.54 | 21.5 | 2.3 | 26
KJ037 | 3 | 750 | 90 | 72 | 95 | 37.7 | 0.674 | 31.36 | 25.4 | 2.3 | 26
KJ037 | 3 | 750 | 80 | 77 | 95 | 42.1 | 0.321 | 16.67 | 13.5 | 2.3 | 26
KJ037 | 3 | 750 | 85 | 77 | 95 | 42.1 | 0.401 | 20.86 | 16.9 | 2.3 | 26
KJ037 | 3 | 750 | 90 | 77 | 95 | 42.1 | 0.48 | 24.94 | 20.2 | 2.3 | 26
KJ037 | 3 | 750 | 65 | 62 | 105 | 30.5 | 0.38 | 14.32 | 11.6 | 2.7 | 26
KJ037 | 3 | 750 | 70 | 62 | 105 | 30.5 | 0.515 | 19.38 | 15.7 | 2.7 | 26
KJ037 | 3 | 750 | 75 | 62 | 105 | 30.5 | 0.652 | 24.57 | 19.9 | 2.7 | 26
KJ037 | 3 | 750 | 80 | 62 | 105 | 30.5 | 0.787 | 29.63 | 24 | 2.7 | 26
KJ037 | 3 | 750 | 85 | 62 | 105 | 30.5 | 0.911 | 34.32 | 27.8 | 2.7 | 26
KJ037 | 3 | 750 | 90 | 62 | 105 | 30.5 | 1 | 37.65 | 30.5 | 2.7 | 26
KJ037 | 3 | 750 | 70 | 67 | 105 | 31.1 | 0.386 | 14.81 | 12 | 2.7 | 26
KJ037 | 3 | 750 | 75 | 67 | 105 | 31.1 | 0.514 | 19.75 | 16 | 2.7 | 26
KJ037 | 3 | 750 | 80 | 67 | 105 | 31.1 | 0.646 | 24.81 | 20.1 | 2.7 | 26
KJ037 | 3 | 750 | 85 | 67 | 105 | 31.1 | 0.801 | 30.74 | 24.9 | 2.7 | 26
KJ037 | 3 | 750 | 90 | 67 | 105 | 31.1 | 0.955 | 36.67 | 29.7 | 2.7 | 26
KJ037 | 3 | 750 | 75 | 72 | 105 | 35.4 | 0.345 | 15.06 | 12.2 | 2.7 | 26
KJ037 | 3 | 750 | 80 | 72 | 105 | 35.4 | 0.458 | 20 | 16.2 | 2.7 | 26
KJ037 | 3 | 750 | 85 | 72 | 105 | 35.4 | 0.571 | 24.94 | 20.2 | 2.7 | 26
KJ037 | 3 | 750 | 90 | 72 | 105 | 35.4 | 0.686 | 30 | 24.3 | 2.7 | 26
KJ037 | 3 | 750 | 80 | 77 | 105 | 39.8 | 0.309 | 15.19 | 12.3 | 2.6 | 26
KJ037 | 3 | 750 | 85 | 77 | 105 | 39.8 | 0.392 | 19.26 | 15.6 | 2.6 | 26
KJ037 | 3 | 750 | 90 | 77 | 105 | 39.8 | 0.472 | 23.21 | 18.8 | 2.6 | 26
KJ037 | 3 | 750 | 65 | 62 | 115 | 28.5 | 0.368 | 12.96 | 10.5 | 3 | 26
KJ037 | 3 | 750 | 70 | 62 | 115 | 28.5 | 0.509 | 17.9 | 14.5 | 3 | 26
KJ037 | 3 | 750 | 75 | 62 | 115 | 28.5 | 0.649 | 22.84 | 18.5 | 3 | 26
KJ037 | 3 | 750 | 80 | 62 | 115 | 28.5 | 0.789 | 27.78 | 22.5 | 3 | 26
KJ037 | 3 | 750 | 85 | 62 | 115 | 28.5 | 0.923 | 32.47 | 26.3 | 3 | 26
KJ037 | 3 | 750 | 90 | 62 | 115 | 28.5 | 1 | 35.19 | 28.5 | 3 | 26
KJ037 | 3 | 750 | 70 | 67 | 115 | 28.8 | 0.368 | 13.09 | 10.6 | 3 | 26
KJ037 | 3 | 750 | 75 | 67 | 115 | 28.8 | 0.51 | 18.15 | 14.7 | 3 | 26
KJ037 | 3 | 750 | 80 | 67 | 115 | 28.8 | 0.649 | 23.09 | 18.7 | 3 | 26
KJ037 | 3 | 750 | 85 | 67 | 115 | 28.8 | 0.826 | 29.38 | 23.8 | 3 | 26
KJ037 | 3 | 750 | 90 | 67 | 115 | 28.8 | 1 | 35.56 | 28.8 | 3 | 26
KJ037 | 3 | 750 | 75 | 72 | 115 | 33.1 | 0.326 | 13.33 | 10.8 | 3 | 26
KJ037 | 3 | 750 | 80 | 72 | 115 | 33.1 | 0.45 | 18.4 | 14.9 | 3 | 26
KJ037 | 3 | 750 | 85 | 72 | 115 | 33.1 | 0.574 | 23.46 | 19 | 3 | 26
KJ037 | 3 | 750 | 90 | 72 | 115 | 33.1 | 0.698 | 28.52 | 23.1 | 3 | 26
KJ037 | 3 | 750 | 80 | 77 | 115 | 37.4 | 0.297 | 13.7 | 11.1 | 3 | 26
KJ037 | 3 | 750 | 85 | 77 | 115 | 37.4 | 0.382 | 17.65 | 14.3 | 3 | 26
KJ037 | 3 | 750 | 90 | 77 | 115 | 37.4 | 0.465 | 21.48 | 17.4 | 3 | 26
KJ037 | 3 | 750 | 65 | 62 | 125 | 26.6 | 0.35 | 11.48 | 9.3 | 3.4 | 26
KJ037 | 3 | 750 | 70 | 62 | 125 | 26.6 | 0.5 | 16.42 | 13.3 | 3.4 | 26
KJ037 | 3 | 750 | 75 | 62 | 125 | 26.6 | 0.647 | 21.23 | 17.2 | 3.4 | 26
KJ037 | 3 | 750 | 80 | 62 | 125 | 26.6 | 0.793 | 26.05 | 21.1 | 3.4 | 26
KJ037 | 3 | 750 | 85 | 62 | 125 | 26.6 | 0.929 | 30.49 | 24.7 | 3.4 | 26
KJ037 | 3 | 750 | 90 | 62 | 125 | 26.6 | 1 | 32.84 | 26.6 | 3.4 | 26
KJ037 | 3 | 750 | 70 | 67 | 125 | 26.6 | 0.35 | 11.48 | 9.3 | 3.4 | 26
KJ037 | 3 | 750 | 75 | 67 | 125 | 26.6 | 0.5 | 16.42 | 13.3 | 3.4 | 26
KJ037 | 3 | 750 | 80 | 67 | 125 | 26.6 | 0.654 | 21.48 | 17.4 | 3.4 | 26
KJ037 | 3 | 750 | 85 | 67 | 125 | 26.6 | 0.85 | 27.9 | 22.6 | 3.4 | 26
KJ037 | 3 | 750 | 90 | 67 | 125 | 26.6 | 1 | 32.84 | 26.6 | 3.4 | 26
KJ037 | 3 | 750 | 75 | 72 | 125 | 30.8 | 0.308 | 11.73 | 9.5 | 3.4 | 26
KJ037 | 3 | 750 | 80 | 72 | 125 | 30.8 | 0.442 | 16.79 | 13.6 | 3.4 | 26
KJ037 | 3 | 750 | 85 | 72 | 125 | 30.8 | 0.578 | 21.98 | 17.8 | 3.4 | 26
KJ037 | 3 | 750 | 90 | 72 | 125 | 30.8 | 0.711 | 27.04 | 21.9 | 3.4 | 26
KJ037 | 3 | 750 | 80 | 77 | 125 | 35.1 | 0.282 | 12.22 | 9.9 | 3.4 | 26
KJ037 | 3 | 750 | 85 | 77 | 125 | 35.1 | 0.37 | 16.05 | 13 | 3.4 | 26
KJ037 | 3 | 750 | 90 | 77 | 125 | 35.1 | 0.456 | 19.75 | 16 | 3.4 | 26
KJ037 | 3 | 900 | 65 | 57 | 75 | 32.8 | 0.634 | 21.4 | 20.8 | 1.8 | 25
KJ037 | 3 | 900 | 70 | 57 | 75 | 32.8 | 0.777 | 26.23 | 25.5 | 1.8 | 25
KJ037 | 3 | 900 | 75 | 57 | 75 | 32.8 | 0.921 | 31.07 | 30.2 | 1.8 | 25
KJ037 | 3 | 900 | 80 | 57 | 75 | 32.8 | 1 | 33.74 | 32.8 | 1.8 | 25
KJ037 | 3 | 900 | 85 | 57 | 75 | 32.8 | 1 | 33.74 | 32.8 | 1.8 | 25
KJ037 | 3 | 900 | 90 | 57 | 75 | 32.8 | 1 | 33.74 | 32.8 | 1.8 | 25
KJ037 | 3 | 900 | 65 | 62 | 75 | 36 | 0.442 | 16.36 | 15.9 | 1.8 | 25
KJ037 | 3 | 900 | 70 | 62 | 75 | 36 | 0.575 | 21.3 | 20.7 | 1.8 | 25
KJ037 | 3 | 900 | 75 | 62 | 75 | 36 | 0.703 | 26.03 | 25.3 | 1.8 | 25
KJ037 | 3 | 900 | 80 | 62 | 75 | 36 | 0.836 | 30.97 | 30.1 | 1.8 | 25
KJ037 | 3 | 900 | 85 | 62 | 75 | 36 | 0.908 | 33.64 | 32.7 | 1.8 | 25
KJ037 | 3 | 900 | 90 | 62 | 75 | 36 | 0.908 | 33.64 | 32.7 | 1.8 | 25
KJ037 | 3 | 900 | 70 | 67 | 75 | 39.2 | 0.403 | 16.26 | 15.8 | 1.8 | 25
KJ037 | 3 | 900 | 75 | 67 | 75 | 39.2 | 0.526 | 21.19 | 20.6 | 1.8 | 25
KJ037 | 3 | 900 | 80 | 67 | 75 | 39.2 | 0.648 | 26.13 | 25.4 | 1.8 | 25
KJ037 | 3 | 900 | 85 | 67 | 75 | 39.2 | 0.77 | 31.07 | 30.2 | 1.8 | 25
KJ037 | 3 | 900 | 90 | 67 | 75 | 39.2 | 0.832 | 33.54 | 32.6 | 1.8 | 25
KJ037 | 3 | 900 | 75 | 72 | 75 | 43.4 | 0.364 | 16.26 | 15.8 | 1.8 | 25
KJ037 | 3 | 900 | 80 | 72 | 75 | 43.4 | 0.475 | 21.19 | 20.6 | 1.8 | 25
KJ037 | 3 | 900 | 85 | 72 | 75 | 43.4 | 0.588 | 26.23 | 25.5 | 1.8 | 25
KJ037 | 3 | 900 | 90 | 72 | 75 | 43.4 | 0.698 | 31.17 | 30.3 | 1.8 | 25
KJ037 | 3 | 900 | 80 | 77 | 75 | 47.5 | 0.335 | 16.36 | 15.9 | 1.8 | 25
KJ037 | 3 | 900 | 85 | 77 | 75 | 47.5 | 0.436 | 21.3 | 20.7 | 1.8 | 25
KJ037 | 3 | 900 | 90 | 77 | 75 | 47.5 | 0.539 | 26.34 | 25.6 | 1.8 | 25
KJ037 | 3 | 900 | 65 | 57 | 85 | 33 | 0.582 | 19.75 | 19.2 | 2 | 25
KJ037 | 3 | 900 | 70 | 57 | 85 | 33 | 0.73 | 24.79 | 24.1 | 2 | 25
KJ037 | 3 | 900 | 75 | 57 | 85 | 33 | 0.882 | 29.94 | 29.1 | 2 | 25
KJ037 | 3 | 900 | 80 | 57 | 85 | 33 | 1 | 33.95 | 33 | 2 | 25
KJ037 | 3 | 900 | 85 | 57 | 85 | 33 | 1 | 33.95 | 33 | 2 | 25
KJ037 | 3 | 900 | 90 | 57 | 85 | 33 | 1 | 33.95 | 33 | 2 | 25
KJ037 | 3 | 900 | 65 | 62 | 85 | 35 | 0.417 | 15.02 | 14.6 | 2 | 25
KJ037 | 3 | 900 | 70 | 62 | 85 | 35 | 0.557 | 20.06 | 19.5 | 2 | 25
KJ037 | 3 | 900 | 75 | 62 | 85 | 35 | 0.694 | 25 | 24.3 | 2 | 25
KJ037 | 3 | 900 | 80 | 62 | 85 | 35 | 0.834 | 30.04 | 29.2 | 2 | 25
KJ037 | 3 | 900 | 85 | 62 | 85 | 35 | 0.854 | 30.76 | 29.9 | 2 | 25
KJ037 | 3 | 900 | 90 | 62 | 85 | 35 | 0.854 | 30.76 | 29.9 | 2 | 25
KJ037 | 3 | 900 | 70 | 67 | 85 | 37.1 | 0.399 | 15.23 | 14.8 | 2 | 25
KJ037 | 3 | 900 | 75 | 67 | 85 | 37.1 | 0.528 | 20.16 | 19.6 | 2 | 25
KJ037 | 3 | 900 | 80 | 67 | 85 | 37.1 | 0.658 | 25.1 | 24.4 | 2 | 25
KJ037 | 3 | 900 | 85 | 67 | 85 | 37.1 | 0.787 | 30.04 | 29.2 | 2 | 25
KJ037 | 3 | 900 | 90 | 67 | 85 | 37.1 | 0.803 | 30.66 | 29.8 | 2 | 25
KJ037 | 3 | 900 | 75 | 72 | 85 | 41.1 | 0.363 | 15.33 | 14.9 | 2 | 25
KJ037 | 3 | 900 | 80 | 72 | 85 | 41.1 | 0.479 | 20.27 | 19.7 | 2 | 25
KJ037 | 3 | 900 | 85 | 72 | 85 | 41.1 | 0.594 | 25.1 | 24.4 | 2 | 25
KJ037 | 3 | 900 | 90 | 72 | 85 | 41.1 | 0.71 | 30.04 | 29.2 | 2 | 25
KJ037 | 3 | 900 | 80 | 77 | 85 | 45.1 | 0.33 | 15.33 | 14.9 | 2 | 25
KJ037 | 3 | 900 | 85 | 77 | 85 | 45.1 | 0.437 | 20.27 | 19.7 | 2 | 25
KJ037 | 3 | 900 | 90 | 77 | 85 | 45.1 | 0.543 | 25.21 | 24.5 | 2 | 25
KJ037 | 3 | 900 | 65 | 57 | 95 | 33.3 | 0.529 | 18.11 | 17.6 | 2.3 | 26
KJ037 | 3 | 900 | 70 | 57 | 95 | 33.3 | 0.685 | 23.46 | 22.8 | 2.3 | 26
KJ037 | 3 | 900 | 75 | 57 | 95 | 33.3 | 0.841 | 28.81 | 28 | 2.3 | 26
KJ037 | 3 | 900 | 80 | 57 | 95 | 33.3 | 0.994 | 34.05 | 33.1 | 2.3 | 26
KJ037 | 3 | 900 | 85 | 57 | 95 | 33.3 | 1 | 34.26 | 33.3 | 2.3 | 26
KJ037 | 3 | 900 | 90 | 57 | 95 | 33.3 | 1 | 34.26 | 33.3 | 2.3 | 26
KJ037 | 3 | 900 | 65 | 62 | 95 | 34.1 | 0.39 | 13.68 | 13.3 | 2.3 | 26
KJ037 | 3 | 900 | 70 | 62 | 95 | 34.1 | 0.537 | 18.83 | 18.3 | 2.3 | 26
KJ037 | 3 | 900 | 75 | 62 | 95 | 34.1 | 0.683 | 23.97 | 23.3 | 2.3 | 26
KJ037 | 3 | 900 | 80 | 62 | 95 | 34.1 | 0.83 | 29.12 | 28.3 | 2.3 | 26
KJ037 | 3 | 900 | 85 | 62 | 95 | 34.1 | 0.927 | 32.51 | 31.6 | 2.3 | 26
KJ037 | 3 | 900 | 90 | 62 | 95 | 34.1 | 0.974 | 34.16 | 33.2 | 2.3 | 26
KJ037 | 3 | 900 | 70 | 67 | 95 | 34.9 | 0.395 | 14.2 | 13.8 | 2.3 | 26
KJ037 | 3 | 900 | 75 | 67 | 95 | 34.9 | 0.533 | 19.14 | 18.6 | 2.3 | 26
KJ037 | 3 | 900 | 80 | 67 | 95 | 34.9 | 0.673 | 24.18 | 23.5 | 2.3 | 26
KJ037 | 3 | 900 | 85 | 67 | 95 | 34.9 | 0.805 | 28.91 | 28.1 | 2.3 | 26
KJ037 | 3 | 900 | 90 | 67 | 95 | 34.9 | 0.94 | 33.74 | 32.8 | 2.3 | 26
KJ037 | 3 | 900 | 75 | 72 | 95 | 38.8 | 0.361 | 14.4 | 14 | 2.3 | 26
KJ037 | 3 | 900 | 80 | 72 | 95 | 38.8 | 0.482 | 19.24 | 18.7 | 2.3 | 26
KJ037 | 3 | 900 | 85 | 72 | 95 | 38.8 | 0.603 | 24.07 | 23.4 | 2.3 | 26
KJ037 | 3 | 900 | 90 | 72 | 95 | 38.8 | 0.724 | 28.91 | 28.1 | 2.3 | 26
KJ037 | 3 | 900 | 80 | 77 | 95 | 42.6 | 0.326 | 14.3 | 13.9 | 2.3 | 26
KJ037 | 3 | 900 | 85 | 77 | 95 | 42.6 | 0.439 | 19.24 | 18.7 | 2.3 | 26
KJ037 | 3 | 900 | 90 | 77 | 95 | 42.6 | 0.552 | 24.18 | 23.5 | 2.3 | 26
KJ037 | 3 | 900 | 65 | 57 | 105 | 31.5 | 0.527 | 17.08 | 16.6 | 2.7 | 26
KJ037 | 3 | 900 | 70 | 57 | 105 | 31.5 | 0.686 | 22.22 | 21.6 | 2.7 | 26
KJ037 | 3 | 900 | 75 | 57 | 105 | 31.5 | 0.841 | 27.26 | 26.5 | 2.7 | 26
KJ037 | 3 | 900 | 80 | 57 | 105 | 31.5 | 1 | 32.41 | 31.5 | 2.7 | 26
KJ037 | 3 | 900 | 85 | 57 | 105 | 31.5 | 1 | 32.41 | 31.5 | 2.7 | 26
KJ037 | 3 | 900 | 90 | 57 | 105 | 31.5 | 1 | 32.41 | 31.5 | 2.7 | 26
KJ037 | 3 | 900 | 65 | 62 | 105 | 32 | 0.378 | 12.45 | 12.1 | 2.7 | 26
KJ037 | 3 | 900 | 70 | 62 | 105 | 32 | 0.531 | 17.49 | 17 | 2.7 | 26
KJ037 | 3 | 900 | 75 | 62 | 105 | 32 | 0.684 | 22.53 | 21.9 | 2.7 | 26
KJ037 | 3 | 900 | 80 | 62 | 105 | 32 | 0.838 | 27.57 | 26.8 | 2.7 | 26
KJ037 | 3 | 900 | 85 | 62 | 105 | 32 | 0.938 | 30.86 | 30 | 2.7 | 26
KJ037 | 3 | 900 | 90 | 62 | 105 | 32 | 0.984 | 32.41 | 31.5 | 2.7 | 26
KJ037 | 3 | 900 | 70 | 67 | 105 | 32.5 | 0.382 | 12.76 | 12.4 | 2.7 | 26
KJ037 | 3 | 900 | 75 | 67 | 105 | 32.5 | 0.529 | 17.7 | 17.2 | 2.7 | 26
KJ037 | 3 | 900 | 80 | 67 | 105 | 32.5 | 0.68 | 22.74 | 22.1 | 2.7 | 26
KJ037 | 3 | 900 | 85 | 67 | 105 | 32.5 | 0.825 | 27.57 | 26.8 | 2.7 | 26
KJ037 | 3 | 900 | 90 | 67 | 105 | 32.5 | 0.969 | 32.41 | 31.5 | 2.7 | 26
KJ037 | 3 | 900 | 75 | 72 | 105 | 36.2 | 0.348 | 12.96 | 12.6 | 2.6 | 26
KJ037 | 3 | 900 | 80 | 72 | 105 | 36.2 | 0.481 | 17.9 | 17.4 | 2.6 | 26
KJ037 | 3 | 900 | 85 | 72 | 105 | 36.2 | 0.613 | 22.84 | 22.2 | 2.6 | 26
KJ037 | 3 | 900 | 90 | 72 | 105 | 36.2 | 0.743 | 27.67 | 26.9 | 2.6 | 26
KJ037 | 3 | 900 | 80 | 77 | 105 | 39.9 | 0.318 | 13.07 | 12.7 | 2.6 | 26
KJ037 | 3 | 900 | 85 | 77 | 105 | 39.9 | 0.439 | 18 | 17.5 | 2.6 | 26
KJ037 | 3 | 900 | 90 | 77 | 105 | 39.9 | 0.559 | 22.94 | 22.3 | 2.6 | 26
KJ037 | 3 | 900 | 65 | 57 | 115 | 29.7 | 0.522 | 15.95 | 15.5 | 3 | 26
KJ037 | 3 | 900 | 70 | 57 | 115 | 29.7 | 0.684 | 20.88 | 20.3 | 3 | 26
KJ037 | 3 | 900 | 75 | 57 | 115 | 29.7 | 0.845 | 25.82 | 25.1 | 3 | 26
KJ037 | 3 | 900 | 80 | 57 | 115 | 29.7 | 1 | 30.56 | 29.7 | 3 | 26
KJ037 | 3 | 900 | 85 | 57 | 115 | 29.7 | 1 | 30.56 | 29.7 | 3 | 26
KJ037 | 3 | 900 | 90 | 57 | 115 | 29.7 | 1 | 30.56 | 29.7 | 3 | 26
KJ037 | 3 | 900 | 65 | 62 | 115 | 29.9 | 0.365 | 11.21 | 10.9 | 3 | 26
KJ037 | 3 | 900 | 70 | 62 | 115 | 29.9 | 0.525 | 16.15 | 15.7 | 3 | 26
KJ037 | 3 | 900 | 75 | 62 | 115 | 29.9 | 0.686 | 21.09 | 20.5 | 3 | 26
KJ037 | 3 | 900 | 80 | 62 | 115 | 29.9 | 0.846 | 26.03 | 25.3 | 3 | 26
KJ037 | 3 | 900 | 85 | 62 | 115 | 29.9 | 0.946 | 29.12 | 28.3 | 3 | 26
KJ037 | 3 | 900 | 90 | 62 | 115 | 29.9 | 0.99 | 30.45 | 29.6 | 3 | 26
KJ037 | 3 | 900 | 70 | 67 | 115 | 30.2 | 0.364 | 11.32 | 11 | 3 | 26
KJ037 | 3 | 900 | 75 | 67 | 115 | 30.2 | 0.523 | 16.26 | 15.8 | 3 | 26
KJ037 | 3 | 900 | 80 | 67 | 115 | 30.2 | 0.685 | 21.3 | 20.7 | 3 | 26
KJ037 | 3 | 900 | 85 | 67 | 115 | 30.2 | 0.844 | 26.23 | 25.5 | 3 | 26
KJ037 | 3 | 900 | 90 | 67 | 115 | 30.2 | 0.977 | 30.35 | 29.5 | 3 | 26
KJ037 | 3 | 900 | 75 | 72 | 115 | 33.7 | 0.332 | 11.52 | 11.2 | 3 | 26
KJ037 | 3 | 900 | 80 | 72 | 115 | 33.7 | 0.475 | 16.46 | 16 | 3 | 26
KJ037 | 3 | 900 | 85 | 72 | 115 | 33.7 | 0.62 | 21.5 | 20.9 | 3 | 26
KJ037 | 3 | 900 | 90 | 72 | 115 | 33.7 | 0.763 | 26.44 | 25.7 | 3 | 26
KJ037 | 3 | 900 | 80 | 77 | 115 | 37.1 | 0.307 | 11.73 | 11.4 | 3 | 26
KJ037 | 3 | 900 | 85 | 77 | 115 | 37.1 | 0.439 | 16.77 | 16.3 | 3 | 26
KJ037 | 3 | 900 | 90 | 77 | 115 | 37.1 | 0.569 | 21.71 | 21.1 | 3 | 26
KJ037 | 3 | 900 | 65 | 57 | 125 | 27.9 | 0.52 | 14.92 | 14.5 | 3.4 | 26
KJ037 | 3 | 900 | 70 | 57 | 125 | 27.9 | 0.685 | 19.65 | 19.1 | 3.4 | 26
KJ037 | 3 | 900 | 75 | 57 | 125 | 27.9 | 0.849 | 24.38 | 23.7 | 3.4 | 26
KJ037 | 3 | 900 | 80 | 57 | 125 | 27.9 | 1 | 28.7 | 27.9 | 3.4 | 26
KJ037 | 3 | 900 | 85 | 57 | 125 | 27.9 | 1 | 28.7 | 27.9 | 3.4 | 26
KJ037 | 3 | 900 | 90 | 57 | 125 | 27.9 | 1 | 28.7 | 27.9 | 3.4 | 26
KJ037 | 3 | 900 | 65 | 62 | 125 | 27.9 | 0.348 | 9.98 | 9.7 | 3.4 | 26
KJ037 | 3 | 900 | 70 | 62 | 125 | 27.9 | 0.516 | 14.81 | 14.4 | 3.4 | 26
KJ037 | 3 | 900 | 75 | 62 | 125 | 27.9 | 0.685 | 19.65 | 19.1 | 3.4 | 26
KJ037 | 3 | 900 | 80 | 62 | 125 | 27.9 | 0.853 | 24.49 | 23.8 | 3.4 | 26
KJ037 | 3 | 900 | 85 | 62 | 125 | 27.9 | 0.953 | 27.37 | 26.6 | 3.4 | 26
KJ037 | 3 | 900 | 90 | 62 | 125 | 27.9 | 1 | 28.7 | 27.9 | 3.4 | 26
KJ037 | 3 | 900 | 70 | 67 | 125 | 27.8 | 0.345 | 9.88 | 9.6 | 3.3 | 26
KJ037 | 3 | 900 | 75 | 67 | 125 | 27.8 | 0.518 | 14.81 | 14.4 | 3.3 | 26
KJ037 | 3 | 900 | 80 | 67 | 125 | 27.8 | 0.691 | 19.75 | 19.2 | 3.3 | 26
KJ037 | 3 | 900 | 85 | 67 | 125 | 27.8 | 0.871 | 24.9 | 24.2 | 3.3 | 26
KJ037 | 3 | 900 | 90 | 67 | 125 | 27.8 | 1 | 28.6 | 27.8 | 3.3 | 26
KJ037 | 3 | 900 | 75 | 72 | 125 | 31.1 | 0.315 | 10.08 | 9.8 | 3.4 | 26
KJ037 | 3 | 900 | 80 | 72 | 125 | 31.1 | 0.473 | 15.12 | 14.7 | 3.4 | 26
KJ037 | 3 | 900 | 85 | 72 | 125 | 31.1 | 0.63 | 20.16 | 19.6 | 3.4 | 26
KJ037 | 3 | 900 | 90 | 72 | 125 | 31.1 | 0.788 | 25.21 | 24.5 | 3.4 | 26
KJ037 | 3 | 900 | 80 | 77 | 125 | 34.4 | 0.297 | 10.49 | 10.2 | 3.4 | 26
KJ037 | 3 | 900 | 85 | 77 | 125 | 34.4 | 0.439 | 15.53 | 15.1 | 3.4 | 26
KJ037 | 3 | 900 | 90 | 77 | 125 | 34.4 | 0.578 | 20.47 | 19.9 | 3.4 | 26
KJ037 | 3 | 1050 | 65 | 57 | 75 | 35.7 | 0.616 | 19.4 | 22 | 1.8 | 25
KJ037 | 3 | 1050 | 70 | 57 | 75 | 35.7 | 0.773 | 24.34 | 27.6 | 1.8 | 25
KJ037 | 3 | 1050 | 75 | 57 | 75 | 35.7 | 0.927 | 29.19 | 33.1 | 1.8 | 25
KJ037 | 3 | 1050 | 80 | 57 | 75 | 35.7 | 1 | 31.48 | 35.7 | 1.8 | 25
KJ037 | 3 | 1050 | 85 | 57 | 75 | 35.7 | 1 | 31.48 | 35.7 | 1.8 | 25
KJ037 | 3 | 1050 | 90 | 57 | 75 | 35.7 | 1 | 31.48 | 35.7 | 1.8 | 25
KJ037 | 3 | 1050 | 65 | 62 | 75 | 38.2 | 0.429 | 14.46 | 16.4 | 1.8 | 25
KJ037 | 3 | 1050 | 70 | 62 | 75 | 38.2 | 0.576 | 19.4 | 22 | 1.8 | 25
KJ037 | 3 | 1050 | 75 | 62 | 75 | 38.2 | 0.72 | 24.25 | 27.5 | 1.8 | 25
KJ037 | 3 | 1050 | 80 | 62 | 75 | 38.2 | 0.866 | 29.19 | 33.1 | 1.8 | 25
KJ037 | 3 | 1050 | 85 | 62 | 75 | 38.2 | 0.932 | 31.39 | 35.6 | 1.8 | 25
KJ037 | 3 | 1050 | 90 | 62 | 75 | 38.2 | 0.932 | 31.39 | 35.6 | 1.8 | 25
KJ037 | 3 | 1050 | 70 | 67 | 75 | 40.8 | 0.402 | 14.46 | 16.4 | 1.8 | 25
KJ037 | 3 | 1050 | 75 | 67 | 75 | 40.8 | 0.539 | 19.4 | 22 | 1.8 | 25
KJ037 | 3 | 1050 | 80 | 67 | 75 | 40.8 | 0.676 | 24.34 | 27.6 | 1.8 | 25
KJ037 | 3 | 1050 | 85 | 67 | 75 | 40.8 | 0.799 | 28.75 | 32.6 | 1.8 | 25
KJ037 | 3 | 1050 | 90 | 67 | 75 | 40.8 | 0.87 | 31.31 | 35.5 | 1.8 | 25
KJ037 | 3 | 1050 | 75 | 72 | 75 | 44.5 | 0.371 | 14.55 | 16.5 | 1.8 | 25
KJ037 | 3 | 1050 | 80 | 72 | 75 | 44.5 | 0.494 | 19.4 | 22 | 1.8 | 25
KJ037 | 3 | 1050 | 85 | 72 | 75 | 44.5 | 0.62 | 24.34 | 27.6 | 1.8 | 25
KJ037 | 3 | 1050 | 90 | 72 | 75 | 44.5 | 0.744 | 29.19 | 33.1 | 1.8 | 25
KJ037 | 3 | 1050 | 80 | 77 | 75 | 48.3 | 0.342 | 14.55 | 16.5 | 1.8 | 25
KJ037 | 3 | 1050 | 85 | 77 | 75 | 48.3 | 0.466 | 19.84 | 22.5 | 1.8 | 25
KJ037 | 3 | 1050 | 90 | 77 | 75 | 48.3 | 0.592 | 25.22 | 28.6 | 1.8 | 25
KJ037 | 3 | 1050 | 65 | 57 | 85 | 35.3 | 0.581 | 18.08 | 20.5 | 2 | 25
KJ037 | 3 | 1050 | 70 | 57 | 85 | 35.3 | 0.745 | 23.19 | 26.3 | 2 | 25
KJ037 | 3 | 1050 | 75 | 57 | 85 | 35.3 | 0.907 | 28.22 | 32 | 2 | 25
KJ037 | 3 | 1050 | 80 | 57 | 85 | 35.3 | 1 | 31.13 | 35.3 | 2 | 25
KJ037 | 3 | 1050 | 85 | 57 | 85 | 35.3 | 1 | 31.13 | 35.3 | 2 | 25
KJ037 | 3 | 1050 | 90 | 57 | 85 | 35.3 | 1 | 31.13 | 35.3 | 2 | 25
KJ037 | 3 | 1050 | 65 | 62 | 85 | 36.9 | 0.409 | 13.32 | 15.1 | 2 | 25
KJ037 | 3 | 1050 | 70 | 62 | 85 | 36.9 | 0.564 | 18.34 | 20.8 | 2 | 25
KJ037 | 3 | 1050 | 75 | 62 | 85 | 36.9 | 0.715 | 23.28 | 26.4 | 2 | 25
KJ037 | 3 | 1050 | 80 | 62 | 85 | 36.9 | 0.87 | 28.31 | 32.1 | 2 | 25
KJ037 | 3 | 1050 | 85 | 62 | 85 | 36.9 | 0.954 | 31.04 | 35.2 | 2 | 25
KJ037 | 3 | 1050 | 90 | 62 | 85 | 36.9 | 0.954 | 31.04 | 35.2 | 2 | 25
KJ037 | 3 | 1050 | 70 | 67 | 85 | 38.6 | 0.396 | 13.49 | 15.3 | 2 | 25
KJ037 | 3 | 1050 | 75 | 67 | 85 | 38.6 | 0.541 | 18.43 | 20.9 | 2 | 25
KJ037 | 3 | 1050 | 80 | 67 | 85 | 38.6 | 0.687 | 23.37 | 26.5 | 2 | 25
KJ037 | 3 | 1050 | 85 | 67 | 85 | 38.6 | 0.813 | 27.69 | 31.4 | 2 | 25
KJ037 | 3 | 1050 | 90 | 67 | 85 | 38.6 | 0.907 | 30.86 | 35 | 2 | 25
KJ037 | 3 | 1050 | 75 | 72 | 85 | 42.2 | 0.365 | 13.58 | 15.4 | 2 | 25
KJ037 | 3 | 1050 | 80 | 72 | 85 | 42.2 | 0.495 | 18.43 | 20.9 | 2 | 25
KJ037 | 3 | 1050 | 85 | 72 | 85 | 42.2 | 0.628 | 23.37 | 26.5 | 2 | 25
KJ037 | 3 | 1050 | 90 | 72 | 85 | 42.2 | 0.758 | 28.22 | 32 | 2 | 25
KJ037 | 3 | 1050 | 80 | 77 | 85 | 45.7 | 0.335 | 13.49 | 15.3 | 2 | 25
KJ037 | 3 | 1050 | 85 | 77 | 85 | 45.7 | 0.47 | 18.96 | 21.5 | 2 | 25
KJ037 | 3 | 1050 | 90 | 77 | 85 | 45.7 | 0.606 | 24.43 | 27.7 | 2 | 25
KJ037 | 3 | 1050 | 65 | 57 | 95 | 34.9 | 0.544 | 16.75 | 19 | 2.3 | 26
KJ037 | 3 | 1050 | 70 | 57 | 95 | 34.9 | 0.716 | 22.05 | 25 | 2.3 | 26
KJ037 | 3 | 1050 | 75 | 57 | 95 | 34.9 | 0.885 | 27.25 | 30.9 | 2.3 | 26
KJ037 | 3 | 1050 | 80 | 57 | 95 | 34.9 | 1 | 30.78 | 34.9 | 2.3 | 26
KJ037 | 3 | 1050 | 85 | 57 | 95 | 34.9 | 1 | 30.78 | 34.9 | 2.3 | 26
KJ037 | 3 | 1050 | 90 | 57 | 95 | 34.9 | 1 | 30.78 | 34.9 | 2.3 | 26
KJ037 | 3 | 1050 | 65 | 62 | 95 | 35.7 | 0.387 | 12.17 | 13.8 | 2.3 | 26
KJ037 | 3 | 1050 | 70 | 62 | 95 | 35.7 | 0.549 | 17.28 | 19.6 | 2.3 | 26
KJ037 | 3 | 1050 | 75 | 62 | 95 | 35.7 | 0.711 | 22.4 | 25.4 | 2.3 | 26
KJ037 | 3 | 1050 | 80 | 62 | 95 | 35.7 | 0.874 | 27.51 | 31.2 | 2.3 | 26
KJ037 | 3 | 1050 | 85 | 62 | 95 | 35.7 | 0.95 | 29.89 | 33.9 | 2.3 | 26
KJ037 | 3 | 1050 | 90 | 62 | 95 | 35.7 | 0.978 | 30.78 | 34.9 | 2.3 | 26
KJ037 | 3 | 1050 | 70 | 67 | 95 | 36.5 | 0.389 | 12.52 | 14.2 | 2.3 | 26
KJ037 | 3 | 1050 | 75 | 67 | 95 | 36.5 | 0.545 | 17.55 | 19.9 | 2.3 | 26
KJ037 | 3 | 1050 | 80 | 67 | 95 | 36.5 | 0.699 | 22.49 | 25.5 | 2.3 | 26
KJ037 | 3 | 1050 | 85 | 67 | 95 | 36.5 | 0.827 | 26.63 | 30.2 | 2.3 | 26
KJ037 | 3 | 1050 | 90 | 67 | 95 | 36.5 | 0.956 | 30.78 | 34.9 | 2.3 | 26
KJ037 | 3 | 1050 | 75 | 72 | 95 | 39.8 | 0.362 | 12.7 | 14.4 | 2.3 | 26
KJ037 | 3 | 1050 | 80 | 72 | 95 | 39.8 | 0.5 | 17.55 | 19.9 | 2.3 | 26
KJ037 | 3 | 1050 | 85 | 72 | 95 | 39.8 | 0.638 | 22.4 | 25.4 | 2.3 | 26
KJ037 | 3 | 1050 | 90 | 72 | 95 | 39.8 | 0.776 | 27.25 | 30.9 | 2.3 | 26
KJ037 | 3 | 1050 | 80 | 77 | 95 | 43.1 | 0.329 | 12.52 | 14.2 | 2.3 | 26
KJ037 | 3 | 1050 | 85 | 77 | 95 | 43.1 | 0.476 | 18.08 | 20.5 | 2.3 | 26
KJ037 | 3 | 1050 | 90 | 77 | 95 | 43.1 | 0.622 | 23.63 | 26.8 | 2.3 | 26
KJ037 | 3 | 1050 | 65 | 57 | 105 | 33 | 0.542 | 15.78 | 17.9 | 2.7 | 26
KJ037 | 3 | 1050 | 70 | 57 | 105 | 33 | 0.715 | 20.81 | 23.6 | 2.7 | 26
KJ037 | 3 | 1050 | 75 | 57 | 105 | 33 | 0.891 | 25.93 | 29.4 | 2.7 | 26
KJ037 | 3 | 1050 | 80 | 57 | 105 | 33 | 1 | 29.1 | 33 | 2.7 | 26
KJ037 | 3 | 1050 | 85 | 57 | 105 | 33 | 1 | 29.1 | 33 | 2.7 | 26
KJ037 | 3 | 1050 | 90 | 57 | 105 | 33 | 1 | 29.1 | 33 | 2.7 | 26
KJ037 | 3 | 1050 | 65 | 62 | 105 | 33.5 | 0.373 | 11.02 | 12.5 | 2.6 | 26
KJ037 | 3 | 1050 | 70 | 62 | 105 | 33.5 | 0.543 | 16.05 | 18.2 | 2.6 | 26
KJ037 | 3 | 1050 | 75 | 62 | 105 | 33.5 | 0.713 | 21.08 | 23.9 | 2.6 | 26
KJ037 | 3 | 1050 | 80 | 62 | 105 | 33.5 | 0.884 | 26.1 | 29.6 | 2.6 | 26
KJ037 | 3 | 1050 | 85 | 62 | 105 | 33.5 | 0.958 | 28.31 | 32.1 | 2.6 | 26
KJ037 | 3 | 1050 | 90 | 62 | 105 | 33.5 | 0.985 | 29.1 | 33 | 2.6 | 26
KJ037 | 3 | 1050 | 70 | 67 | 105 | 34 | 0.376 | 11.29 | 12.8 | 2.6 | 26
KJ037 | 3 | 1050 | 75 | 67 | 105 | 34 | 0.541 | 16.23 | 18.4 | 2.6 | 26
KJ037 | 3 | 1050 | 80 | 67 | 105 | 34 | 0.709 | 21.25 | 24.1 | 2.6 | 26
KJ037 | 3 | 1050 | 85 | 67 | 105 | 34 | 0.844 | 25.31 | 28.7 | 2.6 | 26
KJ037 | 3 | 1050 | 90 | 67 | 105 | 34 | 0.971 | 29.1 | 33 | 2.6 | 26
KJ037 | 3 | 1050 | 75 | 72 | 105 | 37 | 0.351 | 11.46 | 13 | 2.6 | 26
KJ037 | 3 | 1050 | 80 | 72 | 105 | 37 | 0.5 | 16.31 | 18.5 | 2.6 | 26
KJ037 | 3 | 1050 | 85 | 72 | 105 | 37 | 0.651 | 21.25 | 24.1 | 2.6 | 26
KJ037 | 3 | 1050 | 90 | 72 | 105 | 37 | 0.8 | 26.1 | 29.6 | 2.6 | 26
KJ037 | 3 | 1050 | 80 | 77 | 105 | 40 | 0.325 | 11.46 | 13 | 2.6 | 26
KJ037 | 3 | 1050 | 85 | 77 | 105 | 40 | 0.485 | 17.11 | 19.4 | 2.6 | 26
KJ037 | 3 | 1050 | 90 | 77 | 105 | 40 | 0.647 | 22.84 | 25.9 | 2.6 | 26
KJ037 | 3 | 1050 | 65 | 57 | 115 | 31.1 | 0.537 | 14.73 | 16.7 | 3 | 26
KJ037 | 3 | 1050 | 70 | 57 | 115 | 31.1 | 0.717 | 19.66 | 22.3 | 3 | 26
KJ037 | 3 | 1050 | 75 | 57 | 115 | 31.1 | 0.897 | 24.6 | 27.9 | 3 | 26
KJ037 | 3 | 1050 | 80 | 57 | 115 | 31.1 | 1 | 27.43 | 31.1 | 3 | 26
KJ037 | 3 | 1050 | 85 | 57 | 115 | 31.1 | 1 | 27.43 | 31.1 | 3 | 26
KJ037 | 3 | 1050 | 90 | 57 | 115 | 31.1 | 1 | 27.43 | 31.1 | 3 | 26
KJ037 | 3 | 1050 | 65 | 62 | 115 | 31.3 | 0.361 | 9.96 | 11.3 | 3 | 26
KJ037 | 3 | 1050 | 70 | 62 | 115 | 31.3 | 0.537 | 14.81 | 16.8 | 3 | 26
KJ037 | 3 | 1050 | 75 | 62 | 115 | 31.3 | 0.716 | 19.75 | 22.4 | 3 | 26
KJ037 | 3 | 1050 | 80 | 62 | 115 | 31.3 | 0.895 | 24.69 | 28 | 3 | 26
KJ037 | 3 | 1050 | 85 | 62 | 115 | 31.3 | 0.968 | 26.72 | 30.3 | 3 | 26
KJ037 | 3 | 1050 | 90 | 62 | 115 | 31.3 | 0.994 | 27.43 | 31.1 | 3 | 26
KJ037 | 3 | 1050 | 70 | 67 | 115 | 31.6 | 0.361 | 10.05 | 11.4 | 3 | 26
KJ037 | 3 | 1050 | 75 | 67 | 115 | 31.6 | 0.538 | 14.99 | 17 | 3 | 26
KJ037 | 3 | 1050 | 80 | 67 | 115 | 31.6 | 0.715 | 19.93 | 22.6 | 3 | 26
KJ037 | 3 | 1050 | 85 | 67 | 115 | 31.6 | 0.861 | 23.99 | 27.2 | 3 | 26
KJ037 | 3 | 1050 | 90 | 67 | 115 | 31.6 | 0.981 | 27.34 | 31 | 3 | 26
KJ037 | 3 | 1050 | 75 | 72 | 115 | 34.2 | 0.339 | 10.23 | 11.6 | 3 | 26
KJ037 | 3 | 1050 | 80 | 72 | 115 | 34.2 | 0.503 | 15.17 | 17.2 | 3 | 26
KJ037 | 3 | 1050 | 85 | 72 | 115 | 34.2 | 0.667 | 20.11 | 22.8 | 3 | 26
KJ037 | 3 | 1050 | 90 | 72 | 115 | 34.2 | 0.83 | 25.04 | 28.4 | 3 | 26
KJ037 | 3 | 1050 | 80 | 77 | 115 | 36.8 | 0.318 | 10.32 | 11.7 | 3 | 26
KJ037 | 3 | 1050 | 85 | 77 | 115 | 36.8 | 0.497 | 16.14 | 18.3 | 3 | 26
KJ037 | 3 | 1050 | 90 | 77 | 115 | 36.8 | 0.677 | 21.96 | 24.9 | 3 | 26
KJ037 | 3 | 1050 | 65 | 57 | 125 | 29.2 | 0.534 | 13.76 | 15.6 | 3.4 | 26
KJ037 | 3 | 1050 | 70 | 57 | 125 | 29.2 | 0.719 | 18.52 | 21 | 3.4 | 26
KJ037 | 3 | 1050 | 75 | 57 | 125 | 29.2 | 0.904 | 23.28 | 26.4 | 3.4 | 26
KJ037 | 3 | 1050 | 80 | 57 | 125 | 29.2 | 1 | 25.75 | 29.2 | 3.4 | 26
KJ037 | 3 | 1050 | 85 | 57 | 125 | 29.2 | 1 | 25.75 | 29.2 | 3.4 | 26
KJ037 | 3 | 1050 | 90 | 57 | 125 | 29.2 | 1 | 25.75 | 29.2 | 3.4 | 26
KJ037 | 3 | 1050 | 65 | 62 | 125 | 29.2 | 0.342 | 8.82 | 10 | 3.4 | 26
KJ037 | 3 | 1050 | 70 | 62 | 125 | 29.2 | 0.531 | 13.67 | 15.5 | 3.4 | 26
KJ037 | 3 | 1050 | 75 | 62 | 125 | 29.2 | 0.719 | 18.52 | 21 | 3.4 | 26
KJ037 | 3 | 1050 | 80 | 62 | 125 | 29.2 | 0.904 | 23.28 | 26.4 | 3.4 | 26
KJ037 | 3 | 1050 | 85 | 62 | 125 | 29.2 | 0.976 | 25.13 | 28.5 | 3.4 | 26
KJ037 | 3 | 1050 | 90 | 62 | 125 | 29.2 | 1 | 25.75 | 29.2 | 3.4 | 26
KJ037 | 3 | 1050 | 70 | 67 | 125 | 29.1 | 0.344 | 8.82 | 10 | 3.3 | 26
KJ037 | 3 | 1050 | 75 | 67 | 125 | 29.1 | 0.536 | 13.76 | 15.6 | 3.3 | 26
KJ037 | 3 | 1050 | 80 | 67 | 125 | 29.1 | 0.725 | 18.61 | 21.1 | 3.3 | 26
KJ037 | 3 | 1050 | 85 | 67 | 125 | 29.1 | 0.883 | 22.66 | 25.7 | 3.3 | 26
KJ037 | 3 | 1050 | 90 | 67 | 125 | 29.1 | 1 | 25.66 | 29.1 | 3.3 | 26
KJ037 | 3 | 1050 | 75 | 72 | 125 | 31.4 | 0.325 | 8.99 | 10.2 | 3.3 | 26
KJ037 | 3 | 1050 | 80 | 72 | 125 | 31.4 | 0.503 | 13.93 | 15.8 | 3.3 | 26
KJ037 | 3 | 1050 | 85 | 72 | 125 | 31.4 | 0.685 | 18.96 | 21.5 | 3.3 | 26
KJ037 | 3 | 1050 | 90 | 72 | 125 | 31.4 | 0.863 | 23.9 | 27.1 | 3.3 | 26
KJ037 | 3 | 1050 | 80 | 77 | 125 | 33.7 | 0.312 | 9.26 | 10.5 | 3.4 | 26
KJ037 | 3 | 1050 | 85 | 77 | 125 | 33.7 | 0.51 | 15.17 | 17.2 | 3.4 | 26
KJ037 | 3 | 1050 | 90 | 77 | 125 | 33.7 | 0.709 | 21.08 | 23.9 | 3.4 | 26
KJ037 | 3 | 1200 | 65 | 57 | 75 | 38.6 | 0.601 | 17.9 | 23.2 | 1.8 | 25
KJ037 | 3 | 1200 | 70 | 57 | 75 | 38.6 | 0.767 | 22.84 | 29.6 | 1.8 | 25
KJ037 | 3 | 1200 | 75 | 57 | 75 | 38.6 | 0.935 | 27.85 | 36.1 | 1.8 | 25
KJ037 | 3 | 1200 | 80 | 57 | 75 | 38.6 | 1 | 29.78 | 38.6 | 1.8 | 25
KJ037 | 3 | 1200 | 85 | 57 | 75 | 38.6 | 1 | 29.78 | 38.6 | 1.8 | 25
KJ037 | 3 | 1200 | 90 | 57 | 75 | 38.6 | 1 | 29.78 | 38.6 | 1.8 | 25
KJ037 | 3 | 1200 | 65 | 62 | 75 | 40.4 | 0.418 | 13.04 | 16.9 | 1.8 | 25
KJ037 | 3 | 1200 | 70 | 62 | 75 | 40.4 | 0.577 | 17.98 | 23.3 | 1.8 | 25
KJ037 | 3 | 1200 | 75 | 62 | 75 | 40.4 | 0.735 | 22.92 | 29.7 | 1.8 | 25
KJ037 | 3 | 1200 | 80 | 62 | 75 | 40.4 | 0.894 | 27.85 | 36.1 | 1.8 | 25
KJ037 | 3 | 1200 | 85 | 62 | 75 | 40.4 | 0.953 | 29.71 | 38.5 | 1.8 | 25
KJ037 | 3 | 1200 | 90 | 62 | 75 | 40.4 | 0.953 | 29.71 | 38.5 | 1.8 | 25
KJ037 | 3 | 1200 | 70 | 67 | 75 | 42.3 | 0.404 | 13.19 | 17.1 | 1.8 | 25
KJ037 | 3 | 1200 | 75 | 67 | 75 | 42.3 | 0.553 | 18.06 | 23.4 | 1.8 | 25
KJ037 | 3 | 1200 | 80 | 67 | 75 | 42.3 | 0.704 | 22.99 | 29.8 | 1.8 | 25
KJ037 | 3 | 1200 | 85 | 67 | 75 | 42.3 | 0.83 | 27.08 | 35.1 | 1.8 | 25
KJ037 | 3 | 1200 | 90 | 67 | 75 | 42.3 | 0.908 | 29.63 | 38.4 | 1.8 | 25
KJ037 | 3 | 1200 | 75 | 72 | 75 | 45.7 | 0.374 | 13.19 | 17.1 | 1.8 | 25
KJ037 | 3 | 1200 | 80 | 72 | 75 | 45.7 | 0.512 | 18.06 | 23.4 | 1.8 | 25
KJ037 | 3 | 1200 | 85 | 72 | 75 | 45.7 | 0.65 | 22.92 | 29.7 | 1.8 | 25
KJ037 | 3 | 1200 | 90 | 72 | 75 | 45.7 | 0.788 | 27.78 | 36 | 1.8 | 25
KJ037 | 3 | 1200 | 80 | 77 | 75 | 49.2 | 0.346 | 13.12 | 17 | 1.8 | 25
KJ037 | 3 | 1200 | 85 | 77 | 75 | 49.2 | 0.494 | 18.75 | 24.3 | 1.8 | 25
KJ037 | 3 | 1200 | 90 | 77 | 75 | 49.2 | 0.642 | 24.38 | 31.6 | 1.8 | 25
KJ037 | 3 | 1200 | 65 | 57 | 85 | 37.5 | 0.581 | 16.82 | 21.8 | 2 | 25
KJ037 | 3 | 1200 | 70 | 57 | 85 | 37.5 | 0.757 | 21.91 | 28.4 | 2 | 25
KJ037 | 3 | 1200 | 75 | 57 | 85 | 37.5 | 0.931 | 26.93 | 34.9 | 2 | 25
KJ037 | 3 | 1200 | 80 | 57 | 85 | 37.5 | 1 | 28.94 | 37.5 | 2 | 25
KJ037 | 3 | 1200 | 85 | 57 | 85 | 37.5 | 1 | 28.94 | 37.5 | 2 | 25
KJ037 | 3 | 1200 | 90 | 57 | 85 | 37.5 | 1 | 28.94 | 37.5 | 2 | 25
KJ037 | 3 | 1200 | 65 | 62 | 85 | 38.9 | 0.404 | 12.11 | 15.7 | 2 | 25
KJ037 | 3 | 1200 | 70 | 62 | 85 | 38.9 | 0.568 | 17.05 | 22.1 | 2 | 25
KJ037 | 3 | 1200 | 75 | 62 | 85 | 38.9 | 0.735 | 22.07 | 28.6 | 2 | 25
KJ037 | 3 | 1200 | 80 | 62 | 85 | 38.9 | 0.902 | 27.08 | 35.1 | 2 | 25
KJ037 | 3 | 1200 | 85 | 62 | 85 | 38.9 | 0.961 | 28.86 | 37.4 | 2 | 25
KJ037 | 3 | 1200 | 90 | 62 | 85 | 38.9 | 0.961 | 28.86 | 37.4 | 2 | 25
KJ037 | 3 | 1200 | 70 | 67 | 85 | 40.2 | 0.396 | 12.27 | 15.9 | 2 | 25
KJ037 | 3 | 1200 | 75 | 67 | 85 | 40.2 | 0.555 | 17.21 | 22.3 | 2 | 25
KJ037 | 3 | 1200 | 80 | 67 | 85 | 40.2 | 0.714 | 22.15 | 28.7 | 2 | 25
KJ037 | 3 | 1200 | 85 | 67 | 85 | 40.2 | 0.838 | 26 | 33.7 | 2 | 25
KJ037 | 3 | 1200 | 90 | 67 | 85 | 40.2 | 0.928 | 28.78 | 37.3 | 2 | 25
KJ037 | 3 | 1200 | 75 | 72 | 85 | 43.3 | 0.367 | 12.27 | 15.9 | 2 | 25
KJ037 | 3 | 1200 | 80 | 72 | 85 | 43.3 | 0.513 | 17.13 | 22.2 | 2 | 25
KJ037 | 3 | 1200 | 85 | 72 | 85 | 43.3 | 0.658 | 21.99 | 28.5 | 2 | 25
KJ037 | 3 | 1200 | 90 | 72 | 85 | 43.3 | 0.804 | 26.85 | 34.8 | 2 | 25
KJ037 | 3 | 1200 | 80 | 77 | 85 | 46.4 | 0.341 | 12.19 | 15.8 | 2 | 25
KJ037 | 3 | 1200 | 85 | 77 | 85 | 46.4 | 0.502 | 17.98 | 23.3 | 2 | 25
KJ037 | 3 | 1200 | 90 | 77 | 85 | 46.4 | 0.666 | 23.84 | 30.9 | 2 | 25
KJ037 | 3 | 1200 | 65 | 57 | 95 | 36.5 | 0.559 | 15.74 | 20.4 | 2.3 | 26
KJ037 | 3 | 1200 | 70 | 57 | 95 | 36.5 | 0.742 | 20.91 | 27.1 | 2.3 | 26
KJ037 | 3 | 1200 | 75 | 57 | 95 | 36.5 | 0.926 | 26.08 | 33.8 | 2.3 | 26
KJ037 | 3 | 1200 | 80 | 57 | 95 | 36.5 | 1 | 28.16 | 36.5 | 2.3 | 26
KJ037 | 3 | 1200 | 85 | 57 | 95 | 36.5 | 1 | 28.16 | 36.5 | 2.3 | 26
KJ037 | 3 | 1200 | 90 | 57 | 95 | 36.5 | 1 | 28.16 | 36.5 | 2.3 | 26
KJ037 | 3 | 1200 | 65 | 62 | 95 | 37.3 | 0.386 | 11.11 | 14.4 | 2.3 | 26
KJ037 | 3 | 1200 | 70 | 62 | 95 | 37.3 | 0.56 | 16.13 | 20.9 | 2.3 | 26
KJ037 | 3 | 1200 | 75 | 62 | 95 | 37.3 | 0.737 | 21.22 | 27.5 | 2.3 | 26
KJ037 | 3 | 1200 | 80 | 62 | 95 | 37.3 | 0.912 | 26.23 | 34 | 2.3 | 26
KJ037 | 3 | 1200 | 85 | 62 | 95 | 37.3 | 0.968 | 27.85 | 36.1 | 2.3 | 26
KJ037 | 3 | 1200 | 90 | 62 | 95 | 37.3 | 0.976 | 28.09 | 36.4 | 2.3 | 26
KJ037 | 3 | 1200 | 70 | 67 | 95 | 38 | 0.387 | 11.34 | 14.7 | 2.3 | 26
KJ037 | 3 | 1200 | 75 | 67 | 95 | 38 | 0.555 | 16.28 | 21.1 | 2.3 | 26
KJ037 | 3 | 1200 | 80 | 67 | 95 | 38 | 0.724 | 21.22 | 27.5 | 2.3 | 26
KJ037 | 3 | 1200 | 85 | 67 | 95 | 38 | 0.85 | 24.92 | 32.3 | 2.3 | 26
KJ037 | 3 | 1200 | 90 | 67 | 95 | 38 | 0.955 | 28.01 | 36.3 | 2.3 | 26
KJ037 | 3 | 1200 | 75 | 72 | 95 | 40.8 | 0.363 | 11.42 | 14.8 | 2.3 | 26
KJ037 | 3 | 1200 | 80 | 72 | 95 | 40.8 | 0.517 | 16.28 | 21.1 | 2.3 | 26
KJ037 | 3 | 1200 | 85 | 72 | 95 | 40.8 | 0.669 | 21.06 | 27.3 | 2.3 | 26
KJ037 | 3 | 1200 | 90 | 72 | 95 | 40.8 | 0.824 | 25.93 | 33.6 | 2.3 | 26
KJ037 | 3 | 1200 | 80 | 77 | 95 | 43.6 | 0.335 | 11.27 | 14.6 | 2.3 | 26
KJ037 | 3 | 1200 | 85 | 77 | 95 | 43.6 | 0.514 | 17.28 | 22.4 | 2.3 | 26
KJ037 | 3 | 1200 | 90 | 77 | 95 | 43.6 | 0.69 | 23.23 | 30.1 | 2.3 | 26
KJ037 | 3 | 1200 | 65 | 57 | 105 | 34.5 | 0.557 | 14.81 | 19.2 | 2.6 | 26
KJ037 | 3 | 1200 | 70 | 57 | 105 | 34.5 | 0.745 | 19.83 | 25.7 | 2.6 | 26
KJ037 | 3 | 1200 | 75 | 57 | 105 | 34.5 | 0.933 | 24.85 | 32.2 | 2.6 | 26
KJ037 | 3 | 1200 | 80 | 57 | 105 | 34.5 | 1 | 26.62 | 34.5 | 2.6 | 26
KJ037 | 3 | 1200 | 85 | 57 | 105 | 34.5 | 1 | 26.62 | 34.5 | 2.6 | 26
KJ037 | 3 | 1200 | 90 | 57 | 105 | 34.5 | 1 | 26.62 | 34.5 | 2.6 | 26
KJ037 | 3 | 1200 | 65 | 62 | 105 | 35 | 0.371 | 10.03 | 13 | 2.6 | 26
KJ037 | 3 | 1200 | 70 | 62 | 105 | 35 | 0.557 | 15.05 | 19.5 | 2.6 | 26
KJ037 | 3 | 1200 | 75 | 62 | 105 | 35 | 0.74 | 19.98 | 25.9 | 2.6 | 26
KJ037 | 3 | 1200 | 80 | 62 | 105 | 35 | 0.926 | 25 | 32.4 | 2.6 | 26
KJ037 | 3 | 1200 | 85 | 62 | 105 | 35 | 0.977 | 26.39 | 34.2 | 2.6 | 26
KJ037 | 3 | 1200 | 90 | 62 | 105 | 35 | 0.983 | 26.54 | 34.4 | 2.6 | 26
KJ037 | 3 | 1200 | 70 | 67 | 105 | 35.5 | 0.375 | 10.26 | 13.3 | 2.6 | 26
KJ037 | 3 | 1200 | 75 | 67 | 105 | 35.5 | 0.552 | 15.12 | 19.6 | 2.6 | 26
KJ037 | 3 | 1200 | 80 | 67 | 105 | 35.5 | 0.732 | 20.06 | 26 | 2.6 | 26
KJ037 | 3 | 1200 | 85 | 67 | 105 | 35.5 | 0.862 | 23.61 | 30.6 | 2.6 | 26
KJ037 | 3 | 1200 | 90 | 67 | 105 | 35.5 | 0.966 | 26.47 | 34.3 | 2.6 | 26
KJ037 | 3 | 1200 | 75 | 72 | 105 | 37.8 | 0.354 | 10.34 | 13.4 | 2.6 | 26
KJ037 | 3 | 1200 | 80 | 72 | 105 | 37.8 | 0.521 | 15.2 | 19.7 | 2.6 | 26
KJ037 | 3 | 1200 | 85 | 72 | 105 | 37.8 | 0.688 | 20.06 | 26 | 2.6 | 26
KJ037 | 3 | 1200 | 90 | 72 | 105 | 37.8 | 0.854 | 24.92 | 32.3 | 2.6 | 26
KJ037 | 3 | 1200 | 80 | 77 | 105 | 40.1 | 0.332 | 10.26 | 13.3 | 2.6 | 26
KJ037 | 3 | 1200 | 85 | 77 | 105 | 40.1 | 0.531 | 16.44 | 21.3 | 2.6 | 26
KJ037 | 3 | 1200 | 90 | 77 | 105 | 40.1 | 0.733 | 22.69 | 29.4 | 2.6 | 26
KJ037 | 3 | 1200 | 65 | 57 | 115 | 32.5 | 0.551 | 13.81 | 17.9 | 3 | 26
KJ037 | 3 | 1200 | 70 | 57 | 115 | 32.5 | 0.748 | 18.75 | 24.3 | 3 | 26
KJ037 | 3 | 1200 | 75 | 57 | 115 | 32.5 | 0.942 | 23.61 | 30.6 | 3 | 26
KJ037 | 3 | 1200 | 80 | 57 | 115 | 32.5 | 1 | 25.08 | 32.5 | 3 | 26
KJ037 | 3 | 1200 | 85 | 57 | 115 | 32.5 | 1 | 25.08 | 32.5 | 3 | 26
KJ037 | 3 | 1200 | 90 | 57 | 115 | 32.5 | 1 | 25.08 | 32.5 | 3 | 26
KJ037 | 3 | 1200 | 65 | 62 | 115 | 32.7 | 0.358 | 9.03 | 11.7 | 3 | 26
KJ037 | 3 | 1200 | 70 | 62 | 115 | 32.7 | 0.55 | 13.89 | 18 | 3 | 26
KJ037 | 3 | 1200 | 75 | 62 | 115 | 32.7 | 0.746 | 18.83 | 24.4 | 3 | 26
KJ037 | 3 | 1200 | 80 | 62 | 115 | 32.7 | 0.939 | 23.69 | 30.7 | 3 | 26
KJ037 | 3 | 1200 | 85 | 62 | 115 | 32.7 | 0.988 | 24.92 | 32.3 | 3 | 26
KJ037 | 3 | 1200 | 90 | 62 | 115 | 32.7 | 0.991 | 25 | 32.4 | 3 | 26
KJ037 | 3 | 1200 | 70 | 67 | 115 | 32.9 | 0.359 | 9.1 | 11.8 | 3 | 26
KJ037 | 3 | 1200 | 75 | 67 | 115 | 32.9 | 0.553 | 14.04 | 18.2 | 3 | 26
KJ037 | 3 | 1200 | 80 | 67 | 115 | 32.9 | 0.745 | 18.9 | 24.5 | 3 | 26
KJ037 | 3 | 1200 | 85 | 67 | 115 | 32.9 | 0.878 | 22.3 | 28.9 | 3 | 26
KJ037 | 3 | 1200 | 90 | 67 | 115 | 32.9 | 0.982 | 24.92 | 32.3 | 3 | 26
KJ037 | 3 | 1200 | 75 | 72 | 115 | 34.7 | 0.343 | 9.18 | 11.9 | 3 | 26
KJ037 | 3 | 1200 | 80 | 72 | 115 | 34.7 | 0.527 | 14.12 | 18.3 | 3 | 26
KJ037 | 3 | 1200 | 85 | 72 | 115 | 34.7 | 0.709 | 18.98 | 24.6 | 3 | 26
KJ037 | 3 | 1200 | 90 | 72 | 115 | 34.7 | 0.893 | 23.92 | 31 | 3 | 26
KJ037 | 3 | 1200 | 80 | 77 | 115 | 36.5 | 0.329 | 9.26 | 12 | 3 | 26
KJ037 | 3 | 1200 | 85 | 77 | 115 | 36.5 | 0.556 | 15.66 | 20.3 | 3 | 26
KJ037 | 3 | 1200 | 90 | 77 | 115 | 36.5 | 0.784 | 22.07 | 28.6 | 3 | 26
KJ037 | 3 | 1200 | 65 | 57 | 125 | 30.5 | 0.544 | 12.81 | 16.6 | 3.4 | 26
KJ037 | 3 | 1200 | 70 | 57 | 125 | 30.5 | 0.748 | 17.59 | 22.8 | 3.4 | 26
KJ037 | 3 | 1200 | 75 | 57 | 125 | 30.5 | 0.951 | 22.38 | 29 | 3.4 | 26
KJ037 | 3 | 1200 | 80 | 57 | 125 | 30.5 | 1 | 23.53 | 30.5 | 3.4 | 26
KJ037 | 3 | 1200 | 85 | 57 | 125 | 30.5 | 1 | 23.53 | 30.5 | 3.4 | 26
KJ037 | 3 | 1200 | 90 | 57 | 125 | 30.5 | 1 | 23.53 | 30.5 | 3.4 | 26
KJ037 | 3 | 1200 | 65 | 62 | 125 | 30.5 | 0.338 | 7.95 | 10.3 | 3.4 | 26
KJ037 | 3 | 1200 | 70 | 62 | 125 | 30.5 | 0.544 | 12.81 | 16.6 | 3.4 | 26
KJ037 | 3 | 1200 | 75 | 62 | 125 | 30.5 | 0.748 | 17.59 | 22.8 | 3.4 | 26
KJ037 | 3 | 1200 | 80 | 62 | 125 | 30.5 | 0.954 | 22.45 | 29.1 | 3.4 | 26
KJ037 | 3 | 1200 | 85 | 62 | 125 | 30.5 | 0.997 | 23.46 | 30.4 | 3.4 | 26
KJ037 | 3 | 1200 | 90 | 62 | 125 | 30.5 | 1 | 23.53 | 30.5 | 3.4 | 26
KJ037 | 3 | 1200 | 70 | 67 | 125 | 30.4 | 0.339 | 7.95 | 10.3 | 3.3 | 26
KJ037 | 3 | 1200 | 75 | 67 | 125 | 30.4 | 0.549 | 12.89 | 16.7 | 3.3 | 26
KJ037 | 3 | 1200 | 80 | 67 | 125 | 30.4 | 0.757 | 17.75 | 23 | 3.3 | 26
KJ037 | 3 | 1200 | 85 | 67 | 125 | 30.4 | 0.898 | 21.06 | 27.3 | 3.3 | 26
KJ037 | 3 | 1200 | 90 | 67 | 125 | 30.4 | 1 | 23.46 | 30.4 | 3.3 | 26
KJ037 | 3 | 1200 | 75 | 72 | 125 | 31.7 | 0.331 | 8.1 | 10.5 | 3.3 | 26
KJ037 | 3 | 1200 | 80 | 72 | 125 | 31.7 | 0.533 | 13.04 | 16.9 | 3.3 | 26
KJ037 | 3 | 1200 | 85 | 72 | 125 | 31.7 | 0.735 | 17.98 | 23.3 | 3.3 | 26
KJ037 | 3 | 1200 | 90 | 72 | 125 | 31.7 | 0.937 | 22.92 | 29.7 | 3.3 | 26
KJ037 | 3 | 1200 | 80 | 77 | 125 | 33 | 0.327 | 8.33 | 10.8 | 3.3 | 26
KJ037 | 3 | 1200 | 85 | 77 | 125 | 33 | 0.585 | 14.89 | 19.3 | 3.3 | 26
KJ037 | 3 | 1200 | 90 | 77 | 125 | 33 | 0.845 | 21.53 | 27.9 | 3.3 | 26
KJ037 | 3 | 1350 | 65 | 57 | 75 | 41.5 | 0.588 | 16.74 | 24.4 | 1.8 | 25
KJ037 | 3 | 1350 | 70 | 57 | 75 | 41.5 | 0.764 | 21.74 | 31.7 | 1.8 | 25
KJ037 | 3 | 1350 | 75 | 57 | 75 | 41.5 | 0.94 | 26.75 | 39 | 1.8 | 25
KJ037 | 3 | 1350 | 80 | 57 | 75 | 41.5 | 1 | 28.46 | 41.5 | 1.8 | 25
KJ037 | 3 | 1350 | 85 | 57 | 75 | 41.5 | 1 | 28.46 | 41.5 | 1.8 | 25
KJ037 | 3 | 1350 | 90 | 57 | 75 | 41.5 | 1 | 28.46 | 41.5 | 1.8 | 25
KJ037 | 3 | 1350 | 65 | 62 | 75 | 42.7 | 0.41 | 12 | 17.5 | 1.8 | 25
KJ037 | 3 | 1350 | 70 | 62 | 75 | 42.7 | 0.578 | 16.94 | 24.7 | 1.8 | 25
KJ037 | 3 | 1350 | 75 | 62 | 75 | 42.7 | 0.747 | 21.88 | 31.9 | 1.8 | 25
KJ037 | 3 | 1350 | 80 | 62 | 75 | 42.7 | 0.916 | 26.82 | 39.1 | 1.8 | 25
KJ037 | 3 | 1350 | 85 | 62 | 75 | 42.7 | 0.97 | 28.4 | 41.4 | 1.8 | 25
KJ037 | 3 | 1350 | 90 | 62 | 75 | 42.7 | 0.97 | 28.4 | 41.4 | 1.8 | 25
KJ037 | 3 | 1350 | 70 | 67 | 75 | 43.8 | 0.404 | 12.14 | 17.7 | 1.8 | 25
KJ037 | 3 | 1350 | 75 | 67 | 75 | 43.8 | 0.566 | 17.01 | 24.8 | 1.8 | 25
KJ037 | 3 | 1350 | 80 | 67 | 75 | 43.8 | 0.731 | 21.95 | 32 | 1.8 | 25
KJ037 | 3 | 1350 | 85 | 67 | 75 | 43.8 | 0.858 | 25.79 | 37.6 | 1.8 | 25
KJ037 | 3 | 1350 | 90 | 67 | 75 | 43.8 | 0.936 | 28.12 | 41 | 1.8 | 25
KJ037 | 3 | 1350 | 75 | 72 | 75 | 46.9 | 0.377 | 12.14 | 17.7 | 1.8 | 25
KJ037 | 3 | 1350 | 80 | 72 | 75 | 46.9 | 0.529 | 17.01 | 24.8 | 1.8 | 25
KJ037 | 3 | 1350 | 85 | 72 | 75 | 46.9 | 0.678 | 21.81 | 31.8 | 1.8 | 25
KJ037 | 3 | 1350 | 90 | 72 | 75 | 46.9 | 0.829 | 26.68 | 38.9 | 1.8 | 25
KJ037 | 3 | 1350 | 65 | 57 | 85 | 39.8 | 0.58 | 15.84 | 23.1 | 2 | 25
KJ037 | 3 | 1350 | 70 | 57 | 85 | 39.8 | 0.766 | 20.92 | 30.5 | 2 | 25
KJ037 | 3 | 1350 | 75 | 57 | 85 | 39.8 | 0.952 | 25.99 | 37.9 | 2 | 25
KJ037 | 3 | 1350 | 80 | 57 | 85 | 39.8 | 1 | 27.3 | 39.8 | 2 | 25
KJ037 | 3 | 1350 | 85 | 57 | 85 | 39.8 | 1 | 27.3 | 39.8 | 2 | 25
KJ037 | 3 | 1350 | 90 | 57 | 85 | 39.8 | 1 | 27.3 | 39.8 | 2 | 25
KJ037 | 3 | 1350 | 65 | 62 | 85 | 40.8 | 0.397 | 11.11 | 16.2 | 2 | 25
KJ037 | 3 | 1350 | 70 | 62 | 85 | 40.8 | 0.576 | 16.12 | 23.5 | 2 | 25
KJ037 | 3 | 1350 | 75 | 62 | 85 | 40.8 | 0.752 | 21.06 | 30.7 | 2 | 25
KJ037 | 3 | 1350 | 80 | 62 | 85 | 40.8 | 0.931 | 26.06 | 38 | 2 | 25
KJ037 | 3 | 1350 | 85 | 62 | 85 | 40.8 | 0.973 | 27.23 | 39.7 | 2 | 25
KJ037 | 3 | 1350 | 90 | 62 | 85 | 40.8 | 0.973 | 27.23 | 39.7 | 2 | 25
KJ037 | 3 | 1350 | 70 | 67 | 85 | 41.7 | 0.393 | 11.25 | 16.4 | 2 | 25
KJ037 | 3 | 1350 | 75 | 67 | 85 | 41.7 | 0.566 | 16.19 | 23.6 | 2 | 25
KJ037 | 3 | 1350 | 80 | 67 | 85 | 41.7 | 0.739 | 21.12 | 30.8 | 2 | 25
KJ037 | 3 | 1350 | 85 | 67 | 85 | 41.7 | 0.863 | 24.69 | 36 | 2 | 25
KJ037 | 3 | 1350 | 90 | 67 | 85 | 41.7 | 0.95 | 27.16 | 39.6 | 2 | 25
KJ037 | 3 | 1350 | 75 | 72 | 85 | 44.4 | 0.372 | 11.32 | 16.5 | 2 | 25
KJ037 | 3 | 1350 | 80 | 72 | 85 | 44.4 | 0.529 | 16.12 | 23.5 | 2 | 25
KJ037 | 3 | 1350 | 85 | 72 | 85 | 44.4 | 0.689 | 20.99 | 30.6 | 2 | 25
KJ037 | 3 | 1350 | 90 | 72 | 85 | 44.4 | 0.847 | 25.79 | 37.6 | 2 | 25
KJ037 | 3 | 1350 | 65 | 57 | 95 | 38.1 | 0.572 | 14.95 | 21.8 | 2.3 | 26
KJ037 | 3 | 1350 | 70 | 57 | 95 | 38.1 | 0.769 | 20.1 | 29.3 | 2.3 | 26
KJ037 | 3 | 1350 | 75 | 57 | 95 | 38.1 | 0.963 | 25.17 | 36.7 | 2.3 | 26
KJ037 | 3 | 1350 | 80 | 57 | 95 | 38.1 | 1 | 26.13 | 38.1 | 2.3 | 26
KJ037 | 3 | 1350 | 85 | 57 | 95 | 38.1 | 1 | 26.13 | 38.1 | 2.3 | 26
KJ037 | 3 | 1350 | 90 | 57 | 95 | 38.1 | 1 | 26.13 | 38.1 | 2.3 | 26
KJ037 | 3 | 1350 | 65 | 62 | 95 | 38.8 | 0.384 | 10.22 | 14.9 | 2.3 | 26
KJ037 | 3 | 1350 | 70 | 62 | 95 | 38.8 | 0.575 | 15.29 | 22.3 | 2.3 | 26
KJ037 | 3 | 1350 | 75 | 62 | 95 | 38.8 | 0.763 | 20.3 | 29.6 | 2.3 | 26
KJ037 | 3 | 1350 | 80 | 62 | 95 | 38.8 | 0.951 | 25.31 | 36.9 | 2.3 | 26
KJ037 | 3 | 1350 | 85 | 62 | 95 | 38.8 | 0.982 | 26.13 | 38.1 | 2.3 | 26
KJ037 | 3 | 1350 | 90 | 62 | 95 | 38.8 | 0.982 | 26.13 | 38.1 | 2.3 | 26
KJ037 | 3 | 1350 | 70 | 67 | 95 | 39.6 | 0.384 | 10.43 | 15.2 | 2.3 | 26
KJ037 | 3 | 1350 | 75 | 67 | 95 | 39.6 | 0.566 | 15.36 | 22.4 | 2.3 | 26
KJ037 | 3 | 1350 | 80 | 67 | 95 | 39.6 | 0.747 | 20.3 | 29.6 | 2.3 | 26
KJ037 | 3 | 1350 | 85 | 67 | 95 | 39.6 | 0.866 | 23.53 | 34.3 | 2.3 | 26
KJ037 | 3 | 1350 | 90 | 67 | 95 | 39.6 | 0.96 | 26.06 | 38 | 2.3 | 26
KJ037 | 3 | 1350 | 75 | 72 | 95 | 41.8 | 0.364 | 10.43 | 15.2 | 2.3 | 26
KJ037 | 3 | 1350 | 80 | 72 | 95 | 41.8 | 0.531 | 15.23 | 22.2 | 2.3 | 26
KJ037 | 3 | 1350 | 85 | 72 | 95 | 41.8 | 0.701 | 20.1 | 29.3 | 2.3 | 26
KJ037 | 3 | 1350 | 90 | 72 | 95 | 41.8 | 0.868 | 24.9 | 36.3 | 2.3 | 26
KJ037 | 3 | 1350 | 65 | 57 | 105 | 36 | 0.569 | 14.06 | 20.5 | 2.6 | 26
KJ037 | 3 | 1350 | 70 | 57 | 105 | 36 | 0.772 | 19.07 | 27.8 | 2.6 | 26
KJ037 | 3 | 1350 | 75 | 57 | 105 | 36 | 0.975 | 24.07 | 35.1 | 2.6 | 26
KJ037 | 3 | 1350 | 80 | 57 | 105 | 36 | 1 | 24.69 | 36 | 2.6 | 26
KJ037 | 3 | 1350 | 85 | 57 | 105 | 36 | 1 | 24.69 | 36 | 2.6 | 26
KJ037 | 3 | 1350 | 90 | 57 | 105 | 36 | 1 | 24.69 | 36 | 2.6 | 26
KJ037 | 3 | 1350 | 65 | 62 | 105 | 36.5 | 0.37 | 9.26 | 13.5 | 2.6 | 26
KJ037 | 3 | 1350 | 70 | 62 | 105 | 36.5 | 0.567 | 14.2 | 20.7 | 2.6 | 26
KJ037 | 3 | 1350 | 75 | 62 | 105 | 36.5 | 0.764 | 19.14 | 27.9 | 2.6 | 26
KJ037 | 3 | 1350 | 80 | 62 | 105 | 36.5 | 0.964 | 24.14 | 35.2 | 2.6 | 26
KJ037 | 3 | 1350 | 85 | 62 | 105 | 36.5 | 0.986 | 24.69 | 36 | 2.6 | 26
KJ037 | 3 | 1350 | 90 | 62 | 105 | 36.5 | 0.986 | 24.69 | 36 | 2.6 | 26
KJ037 | 3 | 1350 | 70 | 67 | 105 | 36.9 | 0.371 | 9.4 | 13.7 | 2.6 | 26
KJ037 | 3 | 1350 | 75 | 67 | 105 | 36.9 | 0.564 | 14.27 | 20.8 | 2.6 | 26
KJ037 | 3 | 1350 | 80 | 67 | 105 | 36.9 | 0.759 | 19.2 | 28 | 2.6 | 26
KJ037 | 3 | 1350 | 85 | 67 | 105 | 36.9 | 0.881 | 22.29 | 32.5 | 2.6 | 26
KJ037 | 3 | 1350 | 90 | 67 | 105 | 36.9 | 0.976 | 24.69 | 36 | 2.6 | 26
KJ037 | 3 | 1350 | 75 | 72 | 105 | 38.5 | 0.356 | 9.4 | 13.7 | 2.6 | 26
KJ037 | 3 | 1350 | 80 | 72 | 105 | 38.5 | 0.54 | 14.27 | 20.8 | 2.6 | 26
KJ037 | 3 | 1350 | 85 | 72 | 105 | 38.5 | 0.725 | 19.14 | 27.9 | 2.6 | 26
KJ037 | 3 | 1350 | 90 | 72 | 105 | 38.5 | 0.909 | 24.01 | 35 | 2.6 | 26
KJ037 | 3 | 1350 | 65 | 57 | 115 | 33.9 | 0.563 | 13.1 | 19.1 | 3 | 26
KJ037 | 3 | 1350 | 70 | 57 | 115 | 33.9 | 0.773 | 17.97 | 26.2 | 3 | 26
KJ037 | 3 | 1350 | 75 | 57 | 115 | 33.9 | 0.985 | 22.91 | 33.4 | 3 | 26
KJ037 | 3 | 1350 | 80 | 57 | 115 | 33.9 | 1 | 23.25 | 33.9 | 3 | 26
KJ037 | 3 | 1350 | 85 | 57 | 115 | 33.9 | 1 | 23.25 | 33.9 | 3 | 26
KJ037 | 3 | 1350 | 90 | 57 | 115 | 33.9 | 1 | 23.25 | 33.9 | 3 | 26
KJ037 | 3 | 1350 | 65 | 62 | 115 | 34.1 | 0.355 | 8.3 | 12.1 | 3 | 26
KJ037 | 3 | 1350 | 70 | 62 | 115 | 34.1 | 0.563 | 13.17 | 19.2 | 3 | 26
KJ037 | 3 | 1350 | 75 | 62 | 115 | 34.1 | 0.771 | 18.04 | 26.3 | 3 | 26
KJ037 | 3 | 1350 | 80 | 62 | 115 | 34.1 | 0.982 | 22.98 | 33.5 | 3 | 26
KJ037 | 3 | 1350 | 85 | 62 | 115 | 34.1 | 0.994 | 23.25 | 33.9 | 3 | 26
KJ037 | 3 | 1350 | 90 | 62 | 115 | 34.1 | 0.994 | 23.25 | 33.9 | 3 | 26
KJ037 | 3 | 1350 | 70 | 67 | 115 | 34.3 | 0.356 | 8.37 | 12.2 | 3 | 26
KJ037 | 3 | 1350 | 75 | 67 | 115 | 34.3 | 0.563 | 13.24 | 19.3 | 3 | 26
KJ037 | 3 | 1350 | 80 | 67 | 115 | 34.3 | 0.77 | 18.11 | 26.4 | 3 | 26
KJ037 | 3 | 1350 | 85 | 67 | 115 | 34.3 | 0.895 | 21.06 | 30.7 | 3 | 26
KJ037 | 3 | 1350 | 90 | 67 | 115 | 34.3 | 0.985 | 23.18 | 33.8 | 3 | 26
KJ037 | 3 | 1350 | 75 | 72 | 115 | 35.3 | 0.348 | 8.44 | 12.3 | 3 | 26
KJ037 | 3 | 1350 | 80 | 72 | 115 | 35.3 | 0.55 | 13.31 | 19.4 | 3 | 26
KJ037 | 3 | 1350 | 85 | 72 | 115 | 35.3 | 0.751 | 18.18 | 26.5 | 3 | 26
KJ037 | 3 | 1350 | 90 | 72 | 115 | 35.3 | 0.952 | 23.05 | 33.6 | 3 | 26
KJ037 | 3 | 1350 | 65 | 57 | 125 | 31.8 | 0.557 | 12.14 | 17.7 | 3.4 | 26
KJ037 | 3 | 1350 | 70 | 57 | 125 | 31.8 | 0.777 | 16.94 | 24.7 | 3.4 | 26
KJ037 | 3 | 1350 | 75 | 57 | 125 | 31.8 | 0.997 | 21.74 | 31.7 | 3.4 | 26
KJ037 | 3 | 1350 | 80 | 57 | 125 | 31.8 | 1 | 21.81 | 31.8 | 3.4 | 26
KJ037 | 3 | 1350 | 85 | 57 | 125 | 31.8 | 1 | 21.81 | 31.8 | 3.4 | 26
KJ037 | 3 | 1350 | 90 | 57 | 125 | 31.8 | 1 | 21.81 | 31.8 | 3.4 | 26
KJ037 | 3 | 1350 | 65 | 62 | 125 | 31.7 | 0.334 | 7.27 | 10.6 | 3.3 | 26
KJ037 | 3 | 1350 | 70 | 62 | 125 | 31.7 | 0.558 | 12.14 | 17.7 | 3.3 | 26
KJ037 | 3 | 1350 | 75 | 62 | 125 | 31.7 | 0.779 | 16.94 | 24.7 | 3.3 | 26
KJ037 | 3 | 1350 | 80 | 62 | 125 | 31.7 | 1 | 21.74 | 31.7 | 3.3 | 26
KJ037 | 3 | 1350 | 85 | 62 | 125 | 31.7 | 1 | 21.74 | 31.7 | 3.3 | 26
KJ037 | 3 | 1350 | 90 | 62 | 125 | 31.7 | 1 | 21.74 | 31.7 | 3.3 | 26
KJ037 | 3 | 1350 | 70 | 67 | 125 | 31.7 | 0.338 | 7.34 | 10.7 | 3.3 | 26
KJ037 | 3 | 1350 | 75 | 67 | 125 | 31.7 | 0.562 | 12.21 | 17.8 | 3.3 | 26
KJ037 | 3 | 1350 | 80 | 67 | 125 | 31.7 | 0.785 | 17.08 | 24.9 | 3.3 | 26
KJ037 | 3 | 1350 | 85 | 67 | 125 | 31.7 | 0.909 | 19.75 | 28.8 | 3.3 | 26
KJ037 | 3 | 1350 | 90 | 67 | 125 | 31.7 | 1 | 21.74 | 31.7 | 3.3 | 26
KJ037 | 3 | 1350 | 75 | 72 | 125 | 32 | 0.338 | 7.41 | 10.8 | 3.3 | 26
KJ037 | 3 | 1350 | 80 | 72 | 125 | 32 | 0.562 | 12.35 | 18 | 3.3 | 26
KJ037 | 3 | 1350 | 85 | 72 | 125 | 32 | 0.784 | 17.22 | 25.1 | 3.3 | 26
KJ037 | 3 | 1350 | 90 | 72 | 125 | 32 | 1 | 21.95 | 32 | 3.3 | 26
KJ037 | 3 | 1500 | 65 | 57 | 75 | 44.4 | 0.577 | 15.8 | 25.6 | 1.8 | 25
KJ037 | 3 | 1500 | 70 | 57 | 75 | 44.4 | 0.761 | 20.86 | 33.8 | 1.8 | 25
KJ037 | 3 | 1500 | 75 | 57 | 75 | 44.4 | 0.946 | 25.93 | 42 | 1.8 | 25
KJ037 | 3 | 1500 | 80 | 57 | 75 | 44.4 | 1 | 27.41 | 44.4 | 1.8 | 25
KJ037 | 3 | 1500 | 85 | 57 | 75 | 44.4 | 1 | 27.41 | 44.4 | 1.8 | 25
KJ037 | 3 | 1500 | 90 | 57 | 75 | 44.4 | 1 | 27.41 | 44.4 | 1.8 | 25
KJ037 | 3 | 1500 | 65 | 62 | 75 | 44.9 | 0.401 | 11.11 | 18 | 1.8 | 25
KJ037 | 3 | 1500 | 70 | 62 | 75 | 44.9 | 0.579 | 16.05 | 26 | 1.8 | 25
KJ037 | 3 | 1500 | 75 | 62 | 75 | 44.9 | 0.759 | 21.05 | 34.1 | 1.8 | 25
KJ037 | 3 | 1500 | 80 | 62 | 75 | 44.9 | 0.94 | 26.05 | 42.2 | 1.8 | 25
KJ037 | 3 | 1500 | 85 | 62 | 75 | 44.9 | 0.98 | 27.16 | 44 | 1.8 | 25
KJ037 | 3 | 1500 | 90 | 62 | 75 | 44.9 | 0.987 | 27.35 | 44.3 | 1.8 | 25
KJ037 | 3 | 1500 | 70 | 67 | 75 | 45.4 | 0.403 | 11.3 | 18.3 | 1.8 | 25
KJ037 | 3 | 1500 | 75 | 67 | 75 | 45.4 | 0.577 | 16.17 | 26.2 | 1.8 | 25
KJ037 | 3 | 1500 | 80 | 67 | 75 | 45.4 | 0.751 | 21.05 | 34.1 | 1.8 | 25
KJ037 | 3 | 1500 | 85 | 67 | 75 | 45.4 | 0.883 | 24.75 | 40.1 | 1.8 | 25
KJ037 | 3 | 1500 | 90 | 67 | 75 | 45.4 | 0.971 | 27.22 | 44.1 | 1.8 | 25
KJ037 | 3 | 1500 | 75 | 72 | 75 | 48.1 | 0.38 | 11.3 | 18.3 | 1.8 | 25
KJ037 | 3 | 1500 | 80 | 72 | 75 | 48.1 | 0.543 | 16.11 | 26.1 | 1.8 | 25
KJ037 | 3 | 1500 | 85 | 72 | 75 | 48.1 | 0.707 | 20.99 | 34 | 1.8 | 25
KJ037 | 3 | 1500 | 90 | 72 | 75 | 48.1 | 0.869 | 25.8 | 41.8 | 1.8 | 25
KJ037 | 3 | 1500 | 65 | 57 | 85 | 42.1 | 0.58 | 15.06 | 24.4 | 2 | 25
KJ037 | 3 | 1500 | 70 | 57 | 85 | 42.1 | 0.774 | 20.12 | 32.6 | 2 | 25
KJ037 | 3 | 1500 | 75 | 57 | 85 | 42.1 | 0.969 | 25.19 | 40.8 | 2 | 25
KJ037 | 3 | 1500 | 80 | 57 | 85 | 42.1 | 1 | 25.99 | 42.1 | 2 | 25
KJ037 | 3 | 1500 | 85 | 57 | 85 | 42.1 | 1 | 25.99 | 42.1 | 2 | 25
KJ037 | 3 | 1500 | 90 | 57 | 85 | 42.1 | 1 | 25.99 | 42.1 | 2 | 25
KJ037 | 3 | 1500 | 65 | 62 | 85 | 42.7 | 0.391 | 10.31 | 16.7 | 2 | 25
KJ037 | 3 | 1500 | 70 | 62 | 85 | 42.7 | 0.581 | 15.31 | 24.8 | 2 | 25
KJ037 | 3 | 1500 | 75 | 62 | 85 | 42.7 | 0.77 | 20.31 | 32.9 | 2 | 25
KJ037 | 3 | 1500 | 80 | 62 | 85 | 42.7 | 0.958 | 25.25 | 40.9 | 2 | 25
KJ037 | 3 | 1500 | 85 | 62 | 85 | 42.7 | 0.984 | 25.93 | 42 | 2 | 25
KJ037 | 3 | 1500 | 90 | 62 | 85 | 42.7 | 0.984 | 25.93 | 42 | 2 | 25
KJ037 | 3 | 1500 | 70 | 67 | 85 | 43.3 | 0.393 | 10.49 | 17 | 2 | 25
KJ037 | 3 | 1500 | 75 | 67 | 85 | 43.3 | 0.575 | 15.37 | 24.9 | 2 | 25
KJ037 | 3 | 1500 | 80 | 67 | 85 | 43.3 | 0.76 | 20.31 | 32.9 | 2 | 25
KJ037 | 3 | 1500 | 85 | 67 | 85 | 43.3 | 0.882 | 23.58 | 38.2 | 2 | 25
KJ037 | 3 | 1500 | 90 | 67 | 85 | 43.3 | 0.968 | 25.86 | 41.9 | 2 | 25
KJ037 | 3 | 1500 | 75 | 72 | 85 | 45.5 | 0.374 | 10.49 | 17 | 2 | 25
KJ037 | 3 | 1500 | 80 | 72 | 85 | 45.5 | 0.545 | 15.31 | 24.8 | 2 | 25
KJ037 | 3 | 1500 | 85 | 72 | 85 | 45.5 | 0.716 | 20.12 | 32.6 | 2 | 25
KJ037 | 3 | 1500 | 90 | 72 | 85 | 45.5 | 0.888 | 24.94 | 40.4 | 2 | 25
KJ037 | 3 | 1500 | 65 | 57 | 95 | 39.7 | 0.584 | 14.32 | 23.2 | 2.3 | 26
KJ037 | 3 | 1500 | 70 | 57 | 95 | 39.7 | 0.791 | 19.38 | 31.4 | 2.3 | 26
KJ037 | 3 | 1500 | 75 | 57 | 95 | 39.7 | 1 | 24.51 | 39.7 | 2.3 | 26
KJ037 | 3 | 1500 | 80 | 57 | 95 | 39.7 | 1 | 24.51 | 39.7 | 2.3 | 26
KJ037 | 3 | 1500 | 85 | 57 | 95 | 39.7 | 1 | 24.51 | 39.7 | 2.3 | 26
KJ037 | 3 | 1500 | 90 | 57 | 95 | 39.7 | 1 | 24.51 | 39.7 | 2.3 | 26
KJ037 | 3 | 1500 | 65 | 62 | 95 | 40.4 | 0.384 | 9.57 | 15.5 | 2.3 | 26
KJ037 | 3 | 1500 | 70 | 62 | 95 | 40.4 | 0.584 | 14.57 | 23.6 | 2.3 | 26
KJ037 | 3 | 1500 | 75 | 62 | 95 | 40.4 | 0.782 | 19.51 | 31.6 | 2.3 | 26
KJ037 | 3 | 1500 | 80 | 62 | 95 | 40.4 | 0.98 | 24.44 | 39.6 | 2.3 | 26
KJ037 | 3 | 1500 | 85 | 62 | 95 | 40.4 | 0.98 | 24.44 | 39.6 | 2.3 | 26
KJ037 | 3 | 1500 | 90 | 62 | 95 | 40.4 | 0.98 | 24.44 | 39.6 | 2.3 | 26
KJ037 | 3 | 1500 | 70 | 67 | 95 | 41.1 | 0.382 | 9.69 | 15.7 | 2.3 | 26
KJ037 | 3 | 1500 | 75 | 67 | 95 | 41.1 | 0.574 | 14.57 | 23.6 | 2.3 | 26
KJ037 | 3 | 1500 | 80 | 67 | 95 | 41.1 | 0.769 | 19.51 | 31.6 | 2.3 | 26
KJ037 | 3 | 1500 | 85 | 67 | 95 | 41.1 | 0.886 | 22.47 | 36.4 | 2.3 | 26
KJ037 | 3 | 1500 | 90 | 67 | 95 | 41.1 | 0.961 | 24.38 | 39.5 | 2.3 | 26
KJ037 | 3 | 1500 | 75 | 72 | 95 | 42.8 | 0.364 | 9.63 | 15.6 | 2.3 | 26
KJ037 | 3 | 1500 | 80 | 72 | 95 | 42.8 | 0.547 | 14.44 | 23.4 | 2.3 | 26
KJ037 | 3 | 1500 | 85 | 72 | 95 | 42.8 | 0.729 | 19.26 | 31.2 | 2.3 | 26
KJ037 | 3 | 1500 | 90 | 72 | 95 | 42.8 | 0.911 | 24.07 | 39 | 2.3 | 26
KJ037 | 3 | 1500 | 65 | 57 | 105 | 37.5 | 0.581 | 13.46 | 21.8 | 2.6 | 26
KJ037 | 3 | 1500 | 70 | 57 | 105 | 37.5 | 0.795 | 18.4 | 29.8 | 2.6 | 26
KJ037 | 3 | 1500 | 75 | 57 | 105 | 37.5 | 1 | 23.15 | 37.5 | 2.6 | 26
KJ037 | 3 | 1500 | 80 | 57 | 105 | 37.5 | 1 | 23.15 | 37.5 | 2.6 | 26
KJ037 | 3 | 1500 | 85 | 57 | 105 | 37.5 | 1 | 23.15 | 37.5 | 2.6 | 26
KJ037 | 3 | 1500 | 90 | 57 | 105 | 37.5 | 1 | 23.15 | 37.5 | 2.6 | 26
KJ037 | 3 | 1500 | 65 | 62 | 105 | 38 | 0.368 | 8.64 | 14 | 2.6 | 26
KJ037 | 3 | 1500 | 70 | 62 | 105 | 38 | 0.579 | 13.58 | 22 | 2.6 | 26
KJ037 | 3 | 1500 | 75 | 62 | 105 | 38 | 0.789 | 18.52 | 30 | 2.6 | 26
KJ037 | 3 | 1500 | 80 | 62 | 105 | 38 | 0.984 | 23.09 | 37.4 | 2.6 | 26
KJ037 | 3 | 1500 | 85 | 62 | 105 | 38 | 0.984 | 23.09 | 37.4 | 2.6 | 26
KJ037 | 3 | 1500 | 90 | 62 | 105 | 38 | 0.984 | 23.09 | 37.4 | 2.6 | 26
KJ037 | 3 | 1500 | 70 | 67 | 105 | 38.4 | 0.367 | 8.7 | 14.1 | 2.6 | 26
KJ037 | 3 | 1500 | 75 | 67 | 105 | 38.4 | 0.576 | 13.64 | 22.1 | 2.6 | 26
KJ037 | 3 | 1500 | 80 | 67 | 105 | 38.4 | 0.781 | 18.52 | 30 | 2.6 | 26
KJ037 | 3 | 1500 | 85 | 67 | 105 | 38.4 | 0.896 | 21.23 | 34.4 | 2.6 | 26
KJ037 | 3 | 1500 | 90 | 67 | 105 | 38.4 | 0.971 | 23.02 | 37.3 | 2.6 | 26
KJ037 | 3 | 1500 | 75 | 72 | 105 | 39.3 | 0.359 | 8.7 | 14.1 | 2.6 | 26
KJ037 | 3 | 1500 | 80 | 72 | 105 | 39.3 | 0.56 | 13.58 | 22 | 2.6 | 26
KJ037 | 3 | 1500 | 85 | 72 | 105 | 39.3 | 0.758 | 18.4 | 29.8 | 2.6 | 26
KJ037 | 3 | 1500 | 90 | 72 | 105 | 39.3 | 0.957 | 23.21 | 37.6 | 2.6 | 26
KJ037 | 3 | 1500 | 65 | 57 | 115 | 35.3 | 0.575 | 12.53 | 20.3 | 3 | 26
KJ037 | 3 | 1500 | 70 | 57 | 115 | 35.3 | 0.799 | 17.41 | 28.2 | 3 | 26
KJ037 | 3 | 1500 | 75 | 57 | 115 | 35.3 | 1 | 21.79 | 35.3 | 3 | 26
KJ037 | 3 | 1500 | 80 | 57 | 115 | 35.3 | 1 | 21.79 | 35.3 | 3 | 26
KJ037 | 3 | 1500 | 85 | 57 | 115 | 35.3 | 1 | 21.79 | 35.3 | 3 | 26
KJ037 | 3 | 1500 | 90 | 57 | 115 | 35.3 | 1 | 21.79 | 35.3 | 3 | 26
KJ037 | 3 | 1500 | 65 | 62 | 115 | 35.5 | 0.352 | 7.72 | 12.5 | 3 | 26
KJ037 | 3 | 1500 | 70 | 62 | 115 | 35.5 | 0.575 | 12.59 | 20.4 | 3 | 26
KJ037 | 3 | 1500 | 75 | 62 | 115 | 35.5 | 0.797 | 17.47 | 28.3 | 3 | 26
KJ037 | 3 | 1500 | 80 | 62 | 115 | 35.5 | 0.994 | 21.79 | 35.3 | 3 | 26
KJ037 | 3 | 1500 | 85 | 62 | 115 | 35.5 | 0.994 | 21.79 | 35.3 | 3 | 26
KJ037 | 3 | 1500 | 90 | 62 | 115 | 35.5 | 0.994 | 21.79 | 35.3 | 3 | 26
KJ037 | 3 | 1500 | 70 | 67 | 115 | 35.7 | 0.353 | 7.78 | 12.6 | 3 | 26
KJ037 | 3 | 1500 | 75 | 67 | 115 | 35.7 | 0.574 | 12.65 | 20.5 | 3 | 26
KJ037 | 3 | 1500 | 80 | 67 | 115 | 35.7 | 0.796 | 17.53 | 28.4 | 3 | 26
KJ037 | 3 | 1500 | 85 | 67 | 115 | 35.7 | 0.908 | 20 | 32.4 | 3 | 26
KJ037 | 3 | 1500 | 90 | 67 | 115 | 35.7 | 0.986 | 21.73 | 35.2 | 3 | 26
KJ037 | 3 | 1500 | 75 | 72 | 115 | 35.8 | 0.352 | 7.78 | 12.6 | 3 | 26
KJ037 | 3 | 1500 | 80 | 72 | 115 | 35.8 | 0.573 | 12.65 | 20.5 | 3 | 26
KJ037 | 3 | 1500 | 85 | 72 | 115 | 35.8 | 0.793 | 17.53 | 28.4 | 3 | 26
KJ037 | 3 | 1500 | 90 | 72 | 115 | 35.8 | 1 | 22.1 | 35.8 | 3 | 26
KJ037 | 3 | 1500 | 65 | 57 | 125 | 33.1 | 0.568 | 11.6 | 18.8 | 3.3 | 26
KJ037 | 3 | 1500 | 70 | 57 | 125 | 33.1 | 0.804 | 16.42 | 26.6 | 3.3 | 26
KJ037 | 3 | 1500 | 75 | 57 | 125 | 33.1 | 1 | 20.43 | 33.1 | 3.3 | 26
KJ037 | 3 | 1500 | 80 | 57 | 125 | 33.1 | 1 | 20.43 | 33.1 | 3.3 | 26
KJ037 | 3 | 1500 | 85 | 57 | 125 | 33.1 | 1 | 20.43 | 33.1 | 3.3 | 26
KJ037 | 3 | 1500 | 90 | 57 | 125 | 33.1 | 1 | 20.43 | 33.1 | 3.3 | 26
KJ037 | 3 | 1500 | 65 | 62 | 125 | 33 | 0.333 | 6.79 | 11 | 3.3 | 26
KJ037 | 3 | 1500 | 70 | 62 | 125 | 33 | 0.57 | 11.6 | 18.8 | 3.3 | 26
KJ037 | 3 | 1500 | 75 | 62 | 125 | 33 | 0.806 | 16.42 | 26.6 | 3.3 | 26
KJ037 | 3 | 1500 | 80 | 62 | 125 | 33 | 1 | 20.37 | 33 | 3.3 | 26
KJ037 | 3 | 1500 | 85 | 62 | 125 | 33 | 1 | 20.37 | 33 | 3.3 | 26
KJ037 | 3 | 1500 | 90 | 62 | 125 | 33 | 1 | 20.37 | 33 | 3.3 | 26
KJ037 | 3 | 1500 | 70 | 67 | 125 | 33 | 0.333 | 6.79 | 11 | 3.3 | 26
KJ037 | 3 | 1500 | 75 | 67 | 125 | 33 | 0.573 | 11.67 | 18.9 | 3.3 | 26
KJ037 | 3 | 1500 | 80 | 67 | 125 | 33 | 0.812 | 16.54 | 26.8 | 3.3 | 26
KJ037 | 3 | 1500 | 85 | 67 | 125 | 33 | 0.921 | 18.77 | 30.4 | 3.3 | 26
KJ037 | 3 | 1500 | 90 | 67 | 125 | 33 | 1 | 20.37 | 33 | 3.3 | 26
KJ037 | 3 | 1500 | 75 | 72 | 125 | 32.3 | 0.344 | 6.85 | 11.1 | 3.3 | 26
KJ037 | 3 | 1500 | 80 | 72 | 125 | 32.3 | 0.591 | 11.79 | 19.1 | 3.3 | 26
KJ037 | 3 | 1500 | 85 | 72 | 125 | 32.3 | 0.836 | 16.67 | 27 | 3.3 | 26
KJ037 | 3 | 1500 | 90 | 72 | 125 | 32.3 | 1 | 19.94 | 32.3 | 3.3 | 26
KJ049 | 4 | 1000 | 65 | 62 | 75 | 47 | 0.434 | 18.89 | 20.4 | 2.5 | 27
KJ049 | 4 | 1000 | 70 | 62 | 75 | 47 | 0.553 | 24.07 | 26 | 2.5 | 27
KJ049 | 4 | 1000 | 75 | 62 | 75 | 47 | 0.657 | 28.61 | 30.9 | 2.5 | 27
KJ049 | 4 | 1000 | 80 | 62 | 75 | 47 | 0.789 | 34.35 | 37.1 | 2.5 | 27
KJ049 | 4 | 1000 | 85 | 62 | 75 | 47 | 0.921 | 40.09 | 43.3 | 2.5 | 27
KJ049 | 4 | 1000 | 90 | 62 | 75 | 47 | 1 | 43.52 | 47 | 2.5 | 27
KJ049 | 4 | 1000 | 70 | 67 | 75 | 52 | 0.398 | 19.17 | 20.7 | 2.5 | 27
KJ049 | 4 | 1000 | 75 | 67 | 75 | 52 | 0.502 | 24.17 | 26.1 | 2.5 | 27
KJ049 | 4 | 1000 | 80 | 67 | 75 | 52 | 0.608 | 29.26 | 31.6 | 2.5 | 27
KJ049 | 4 | 1000 | 85 | 67 | 75 | 52 | 0.723 | 34.81 | 37.6 | 2.5 | 27
KJ049 | 4 | 1000 | 90 | 67 | 75 | 52 | 0.838 | 40.37 | 43.6 | 2.5 | 27
KJ049 | 4 | 1000 | 75 | 72 | 75 | 57.7 | 0.36 | 19.26 | 20.8 | 2.5 | 27
KJ049 | 4 | 1000 | 80 | 72 | 75 | 57.7 | 0.452 | 24.17 | 26.1 | 2.5 | 27
KJ049 | 4 | 1000 | 85 | 72 | 75 | 57.7 | 0.542 | 28.98 | 31.3 | 2.5 | 27
KJ049 | 4 | 1000 | 90 | 72 | 75 | 57.7 | 0.634 | 33.89 | 36.6 | 2.5 | 27
KJ049 | 4 | 1000 | 80 | 77 | 75 | 63.3 | 0.324 | 18.98 | 20.5 | 2.5 | 27
KJ049 | 4 | 1000 | 85 | 77 | 75 | 63.3 | 0.395 | 23.15 | 25 | 2.5 | 27
KJ049 | 4 | 1000 | 90 | 77 | 75 | 63.3 | 0.466 | 27.31 | 29.5 | 2.5 | 27
KJ049 | 4 | 1000 | 65 | 62 | 85 | 43.4 | 0.435 | 17.5 | 18.9 | 2.8 | 27
KJ049 | 4 | 1000 | 70 | 62 | 85 | 43.4 | 0.562 | 22.59 | 24.4 | 2.8 | 27
KJ049 | 4 | 1000 | 75 | 62 | 85 | 43.4 | 0.682 | 27.41 | 29.6 | 2.8 | 27
KJ049 | 4 | 1000 | 80 | 62 | 85 | 43.4 | 0.818 | 32.87 | 35.5 | 2.8 | 27
KJ049 | 4 | 1000 | 85 | 62 | 85 | 43.4 | 0.975 | 39.17 | 42.3 | 2.8 | 27
KJ049 | 4 | 1000 | 90 | 62 | 85 | 43.4 | 1 | 40.19 | 43.4 | 2.8 | 27
KJ049 | 4 | 1000 | 70 | 67 | 85 | 48.2 | 0.398 | 17.78 | 19.2 | 2.8 | 27
KJ049 | 4 | 1000 | 75 | 67 | 85 | 48.2 | 0.51 | 22.78 | 24.6 | 2.8 | 27
KJ049 | 4 | 1000 | 80 | 67 | 85 | 48.2 | 0.622 | 27.78 | 30 | 2.8 | 27
KJ049 | 4 | 1000 | 85 | 67 | 85 | 48.2 | 0.749 | 33.43 | 36.1 | 2.8 | 27
KJ049 | 4 | 1000 | 90 | 67 | 85 | 48.2 | 0.878 | 39.17 | 42.3 | 2.8 | 27
KJ049 | 4 | 1000 | 75 | 72 | 85 | 53.8 | 0.357 | 17.78 | 19.2 | 2.8 | 27
KJ049 | 4 | 1000 | 80 | 72 | 85 | 53.8 | 0.455 | 22.69 | 24.5 | 2.8 | 27
KJ049 | 4 | 1000 | 85 | 72 | 85 | 53.8 | 0.554 | 27.59 | 29.8 | 2.8 | 27
KJ049 | 4 | 1000 | 90 | 72 | 85 | 53.8 | 0.652 | 32.5 | 35.1 | 2.8 | 27
KJ049 | 4 | 1000 | 80 | 77 | 85 | 59.4 | 0.32 | 17.59 | 19 | 2.8 | 27
KJ049 | 4 | 1000 | 85 | 77 | 85 | 59.4 | 0.396 | 21.76 | 23.5 | 2.8 | 27
KJ049 | 4 | 1000 | 90 | 77 | 85 | 59.4 | 0.47 | 25.83 | 27.9 | 2.8 | 27
KJ049 | 4 | 1000 | 65 | 62 | 95 | 39.8 | 0.437 | 16.11 | 17.4 | 3.1 | 27
KJ049 | 4 | 1000 | 70 | 62 | 95 | 39.8 | 0.575 | 21.2 | 22.9 | 3.1 | 27
KJ049 | 4 | 1000 | 75 | 62 | 95 | 39.8 | 0.714 | 26.3 | 28.4 | 3.1 | 27
KJ049 | 4 | 1000 | 80 | 62 | 95 | 39.8 | 0.852 | 31.39 | 33.9 | 3.1 | 27
KJ049 | 4 | 1000 | 85 | 62 | 95 | 39.8 | 1 | 36.85 | 39.8 | 3.1 | 27
KJ049 | 4 | 1000 | 90 | 62 | 95 | 39.8 | 1 | 36.85 | 39.8 | 3.1 | 27
KJ049 | 4 | 1000 | 70 | 67 | 95 | 44.3 | 0.397 | 16.3 | 17.6 | 3.2 | 27
KJ049 | 4 | 1000 | 75 | 67 | 95 | 44.3 | 0.519 | 21.3 | 23 | 3.2 | 27
KJ049 | 4 | 1000 | 80 | 67 | 95 | 44.3 | 0.641 | 26.3 | 28.4 | 3.2 | 27
KJ049 | 4 | 1000 | 85 | 67 | 95 | 44.3 | 0.783 | 32.13 | 34.7 | 3.2 | 27
KJ049 | 4 | 1000 | 90 | 67 | 95 | 44.3 | 0.923 | 37.87 | 40.9 | 3.2 | 27
KJ049 | 4 | 1000 | 75 | 72 | 95 | 49.9 | 0.353 | 16.3 | 17.6 | 3.2 | 27
KJ049 | 4 | 1000 | 80 | 72 | 95 | 49.9 | 0.461 | 21.3 | 23 | 3.2 | 27
KJ049 | 4 | 1000 | 85 | 72 | 95 | 49.9 | 0.567 | 26.2 | 28.3 | 3.2 | 27
KJ049 | 4 | 1000 | 90 | 72 | 95 | 49.9 | 0.673 | 31.11 | 33.6 | 3.2 | 27
KJ049 | 4 | 1000 | 80 | 77 | 95 | 55.5 | 0.315 | 16.2 | 17.5 | 3.1 | 27
KJ049 | 4 | 1000 | 85 | 77 | 95 | 55.5 | 0.395 | 20.28 | 21.9 | 3.1 | 27
KJ049 | 4 | 1000 | 90 | 77 | 95 | 55.5 | 0.474 | 24.35 | 26.3 | 3.1 | 27
KJ049 | 4 | 1000 | 65 | 62 | 105 | 38.2 | 0.406 | 14.35 | 15.5 | 3.7 | 27
KJ049 | 4 | 1000 | 70 | 62 | 105 | 38.2 | 0.547 | 19.35 | 20.9 | 3.7 | 27
KJ049 | 4 | 1000 | 75 | 62 | 105 | 38.2 | 0.688 | 24.35 | 26.3 | 3.7 | 27
KJ049 | 4 | 1000 | 80 | 62 | 105 | 38.2 | 0.83 | 29.35 | 31.7 | 3.7 | 27
KJ049 | 4 | 1000 | 85 | 62 | 105 | 38.2 | 1 | 35.37 | 38.2 | 3.7 | 27
KJ049 | 4 | 1000 | 90 | 62 | 105 | 38.2 | 1 | 35.37 | 38.2 | 3.7 | 27
KJ049 | 4 | 1000 | 70 | 67 | 105 | 41.4 | 0.386 | 14.81 | 16 | 3.7 | 27
KJ049 | 4 | 1000 | 75 | 67 | 105 | 41.4 | 0.514 | 19.72 | 21.3 | 3.7 | 27
KJ049 | 4 | 1000 | 80 | 67 | 105 | 41.4 | 0.645 | 24.72 | 26.7 | 3.7 | 27
KJ049 | 4 | 1000 | 85 | 67 | 105 | 41.4 | 0.797 | 30.56 | 33 | 3.7 | 27
KJ049 | 4 | 1000 | 90 | 67 | 105 | 41.4 | 0.952 | 36.48 | 39.4 | 3.7 | 27
KJ049 | 4 | 1000 | 75 | 72 | 105 | 46.2 | 0.355 | 15.19 | 16.4 | 3.7 | 27
KJ049 | 4 | 1000 | 80 | 72 | 105 | 46.2 | 0.468 | 20 | 21.6 | 3.7 | 27
KJ049 | 4 | 1000 | 85 | 72 | 105 | 46.2 | 0.58 | 24.81 | 26.8 | 3.7 | 27
KJ049 | 4 | 1000 | 90 | 72 | 105 | 46.2 | 0.693 | 29.63 | 32 | 3.7 | 27
KJ049 | 4 | 1000 | 80 | 77 | 105 | 51 | 0.324 | 15.28 | 16.5 | 3.7 | 27
KJ049 | 4 | 1000 | 85 | 77 | 105 | 51 | 0.404 | 19.07 | 20.6 | 3.7 | 27
KJ049 | 4 | 1000 | 90 | 77 | 105 | 51 | 0.482 | 22.78 | 24.6 | 3.7 | 27
KJ049 | 4 | 1000 | 65 | 62 | 115 | 36.6 | 0.369 | 12.5 | 13.5 | 4.2 | 28
KJ049 | 4 | 1000 | 70 | 62 | 115 | 36.6 | 0.516 | 17.5 | 18.9 | 4.2 | 28
KJ049 | 4 | 1000 | 75 | 62 | 115 | 36.6 | 0.661 | 22.41 | 24.2 | 4.2 | 28
KJ049 | 4 | 1000 | 80 | 62 | 115 | 36.6 | 0.806 | 27.31 | 29.5 | 4.2 | 28
KJ049 | 4 | 1000 | 85 | 62 | 115 | 36.6 | 0.956 | 32.41 | 35 | 4.2 | 28
KJ049 | 4 | 1000 | 90 | 62 | 115 | 36.6 | 1 | 33.89 | 36.6 | 4.2 | 28
KJ049 | 4 | 1000 | 70 | 67 | 115 | 38.5 | 0.377 | 13.43 | 14.5 | 4.2 | 28
KJ049 | 4 | 1000 | 75 | 67 | 115 | 38.5 | 0.512 | 18.24 | 19.7 | 4.2 | 28
KJ049 | 4 | 1000 | 80 | 67 | 115 | 38.5 | 0.647 | 23.06 | 24.9 | 4.2 | 28
KJ049 | 4 | 1000 | 85 | 67 | 115 | 38.5 | 0.813 | 28.98 | 31.3 | 4.2 | 28
KJ049 | 4 | 1000 | 90 | 67 | 115 | 38.5 | 0.982 | 35 | 37.8 | 4.2 | 28
KJ049 | 4 | 1000 | 75 | 72 | 115 | 42.5 | 0.355 | 13.98 | 15.1 | 4.2 | 28
KJ049 | 4 | 1000 | 80 | 72 | 115 | 42.5 | 0.475 | 18.7 | 20.2 | 4.2 | 28
KJ049 | 4 | 1000 | 85 | 72 | 115 | 42.5 | 0.595 | 23.43 | 25.3 | 4.2 | 28
KJ049 | 4 | 1000 | 90 | 72 | 115 | 42.5 | 0.715 | 28.15 | 30.4 | 4.2 | 28
KJ049 | 4 | 1000 | 80 | 77 | 115 | 46.5 | 0.335 | 14.44 | 15.6 | 4.3 | 28
KJ049 | 4 | 1000 | 85 | 77 | 115 | 46.5 | 0.413 | 17.78 | 19.2 | 4.3 | 28
KJ049 | 4 | 1000 | 90 | 77 | 115 | 46.5 | 0.492 | 21.2 | 22.9 | 4.3 | 28
KJ049 | 4 | 1000 | 65 | 62 | 125 | 35 | 0.331 | 10.74 | 11.6 | 4.7 | 28
KJ049 | 4 | 1000 | 70 | 62 | 125 | 35 | 0.483 | 15.65 | 16.9 | 4.7 | 28
KJ049 | 4 | 1000 | 75 | 62 | 125 | 35 | 0.631 | 20.46 | 22.1 | 4.7 | 28
KJ049 | 4 | 1000 | 80 | 62 | 125 | 35 | 0.783 | 25.37 | 27.4 | 4.7 | 28
KJ049 | 4 | 1000 | 85 | 62 | 125 | 35 | 0.911 | 29.54 | 31.9 | 4.7 | 28
KJ049 | 4 | 1000 | 90 | 62 | 125 | 35 | 1 | 32.41 | 35 | 4.7 | 28
KJ049 | 4 | 1000 | 70 | 67 | 125 | 35.6 | 0.362 | 11.94 | 12.9 | 4.7 | 28
KJ049 | 4 | 1000 | 75 | 67 | 125 | 35.6 | 0.506 | 16.67 | 18 | 4.7 | 28
KJ049 | 4 | 1000 | 80 | 67 | 125 | 35.6 | 0.649 | 21.39 | 23.1 | 4.7 | 28
KJ049 | 4 | 1000 | 85 | 67 | 125 | 35.6 | 0.834 | 27.5 | 29.7 | 4.7 | 28
KJ049 | 4 | 1000 | 90 | 67 | 125 | 35.6 | 1 | 32.96 | 35.6 | 4.7 | 28
KJ049 | 4 | 1000 | 75 | 72 | 125 | 38.8 | 0.358 | 12.87 | 13.9 | 4.8 | 28
KJ049 | 4 | 1000 | 80 | 72 | 125 | 38.8 | 0.485 | 17.41 | 18.8 | 4.8 | 28
KJ049 | 4 | 1000 | 85 | 72 | 125 | 38.8 | 0.613 | 22.04 | 23.8 | 4.8 | 28
KJ049 | 4 | 1000 | 90 | 72 | 125 | 38.8 | 0.74 | 26.57 | 28.7 | 4.8 | 28
KJ049 | 4 | 1000 | 80 | 77 | 125 | 41.9 | 0.348 | 13.52 | 14.6 | 4.8 | 28
KJ049 | 4 | 1000 | 85 | 77 | 125 | 41.9 | 0.427 | 16.57 | 17.9 | 4.8 | 28
KJ049 | 4 | 1000 | 90 | 77 | 125 | 41.9 | 0.508 | 19.72 | 21.3 | 4.8 | 28
KJ049 | 4 | 1200 | 65 | 57 | 75 | 45.5 | 0.598 | 20.99 | 27.2 | 2.5 | 27
KJ049 | 4 | 1200 | 70 | 57 | 75 | 45.5 | 0.747 | 26.23 | 34 | 2.5 | 27
KJ049 | 4 | 1200 | 75 | 57 | 75 | 45.5 | 0.895 | 31.4 | 40.7 | 2.5 | 27
KJ049 | 4 | 1200 | 80 | 57 | 75 | 45.5 | 1 | 35.11 | 45.5 | 2.5 | 27
KJ049 | 4 | 1200 | 85 | 57 | 75 | 45.5 | 1 | 35.11 | 45.5 | 2.5 | 27
KJ049 | 4 | 1200 | 90 | 57 | 75 | 45.5 | 1 | 35.11 | 45.5 | 2.5 | 27
KJ049 | 4 | 1200 | 65 | 62 | 75 | 49.6 | 0.425 | 16.28 | 21.1 | 2.5 | 27
KJ049 | 4 | 1200 | 70 | 62 | 75 | 49.6 | 0.558 | 21.37 | 27.7 | 2.5 | 27
KJ049 | 4 | 1200 | 75 | 62 | 75 | 49.6 | 0.681 | 26.08 | 33.8 | 2.5 | 27
KJ049 | 4 | 1200 | 80 | 62 | 75 | 49.6 | 0.825 | 31.56 | 40.9 | 2.5 | 27
KJ049 | 4 | 1200 | 85 | 62 | 75 | 49.6 | 0.935 | 35.8 | 46.4 | 2.5 | 27
KJ049 | 4 | 1200 | 90 | 62 | 75 | 49.6 | 1 | 38.27 | 49.6 | 2.5 | 27
KJ049 | 4 | 1200 | 70 | 67 | 75 | 53.7 | 0.4 | 16.59 | 21.5 | 2.5 | 27
KJ049 | 4 | 1200 | 75 | 67 | 75 | 53.7 | 0.52 | 21.53 | 27.9 | 2.5 | 27
KJ049 | 4 | 1200 | 80 | 67 | 75 | 53.7 | 0.641 | 26.54 | 34.4 | 2.5 | 27
KJ049 | 4 | 1200 | 85 | 67 | 75 | 53.7 | 0.76 | 31.48 | 40.8 | 2.5 | 27
KJ049 | 4 | 1200 | 90 | 67 | 75 | 53.7 | 0.881 | 36.5 | 47.3 | 2.5 | 27
KJ049 | 4 | 1200 | 75 | 72 | 75 | 58.9 | 0.367 | 16.67 | 21.6 | 2.5 | 27
KJ049 | 4 | 1200 | 80 | 72 | 75 | 58.9 | 0.474 | 21.53 | 27.9 | 2.5 | 27
KJ049 | 4 | 1200 | 85 | 72 | 75 | 58.9 | 0.581 | 26.39 | 34.2 | 2.5 | 27
KJ049 | 4 | 1200 | 90 | 72 | 75 | 58.9 | 0.688 | 31.25 | 40.5 | 2.5 | 27
KJ049 | 4 | 1200 | 80 | 77 | 75 | 64.2 | 0.333 | 16.51 | 21.4 | 2.5 | 27
KJ049 | 4 | 1200 | 85 | 77 | 75 | 64.2 | 0.43 | 21.3 | 27.6 | 2.5 | 27
KJ049 | 4 | 1200 | 90 | 77 | 75 | 64.2 | 0.526 | 26.08 | 33.8 | 2.5 | 27
KJ049 | 4 | 1200 | 65 | 57 | 85 | 42.3 | 0.608 | 19.83 | 25.7 | 2.8 | 27
KJ049 | 4 | 1200 | 70 | 57 | 85 | 42.3 | 0.766 | 25 | 32.4 | 2.8 | 27
KJ049 | 4 | 1200 | 75 | 57 | 85 | 42.3 | 0.924 | 30.17 | 39.1 | 2.8 | 27
KJ049 | 4 | 1200 | 80 | 57 | 85 | 42.3 | 1 | 32.64 | 42.3 | 2.8 | 27
KJ049 | 4 | 1200 | 85 | 57 | 85 | 42.3 | 1 | 32.64 | 42.3 | 2.8 | 27
KJ049 | 4 | 1200 | 90 | 57 | 85 | 42.3 | 1 | 32.64 | 42.3 | 2.8 | 27
KJ049 | 4 | 1200 | 65 | 62 | 85 | 46.3 | 0.423 | 15.12 | 19.6 | 2.8 | 27
KJ049 | 4 | 1200 | 70 | 62 | 85 | 46.3 | 0.564 | 20.14 | 26.1 | 2.8 | 27
KJ049 | 4 | 1200 | 75 | 62 | 85 | 46.3 | 0.702 | 25.08 | 32.5 | 2.8 | 27
KJ049 | 4 | 1200 | 80 | 62 | 85 | 46.3 | 0.849 | 30.32 | 39.3 | 2.8 | 27
KJ049 | 4 | 1200 | 85 | 62 | 85 | 46.3 | 0.976 | 34.88 | 45.2 | 2.8 | 27
KJ049 | 4 | 1200 | 90 | 62 | 85 | 46.3 | 1 | 35.73 | 46.3 | 2.8 | 27
KJ049 | 4 | 1200 | 70 | 67 | 85 | 50.2 | 0.396 | 15.35 | 19.9 | 2.8 | 27
KJ049 | 4 | 1200 | 75 | 67 | 85 | 50.2 | 0.524 | 20.29 | 26.3 | 2.8 | 27
KJ049 | 4 | 1200 | 80 | 67 | 85 | 50.2 | 0.653 | 25.31 | 32.8 | 2.8 | 27
KJ049 | 4 | 1200 | 85 | 67 | 85 | 50.2 | 0.781 | 30.25 | 39.2 | 2.8 | 27
KJ049 | 4 | 1200 | 90 | 67 | 85 | 50.2 | 0.908 | 35.19 | 45.6 | 2.8 | 27
KJ049 | 4 | 1200 | 75 | 72 | 85 | 55.2 | 0.361 | 15.35 | 19.9 | 2.8 | 27
KJ049 | 4 | 1200 | 80 | 72 | 85 | 55.2 | 0.476 | 20.29 | 26.3 | 2.8 | 27
KJ049 | 4 | 1200 | 85 | 72 | 85 | 55.2 | 0.592 | 25.23 | 32.7 | 2.8 | 27
KJ049 | 4 | 1200 | 90 | 72 | 85 | 55.2 | 0.707 | 30.09 | 39 | 2.8 | 27
KJ049 | 4 | 1200 | 80 | 77 | 85 | 60.3 | 0.328 | 15.28 | 19.8 | 2.8 | 27
KJ049 | 4 | 1200 | 85 | 77 | 85 | 60.3 | 0.433 | 20.14 | 26.1 | 2.8 | 27
KJ049 | 4 | 1200 | 90 | 77 | 85 | 60.3 | 0.539 | 25.08 | 32.5 | 2.8 | 27
KJ049 | 4 | 1200 | 65 | 57 | 95 | 39.2 | 0.617 | 18.67 | 24.2 | 3.1 | 27
KJ049 | 4 | 1200 | 70 | 57 | 95 | 39.2 | 0.788 | 23.84 | 30.9 | 3.1 | 27
KJ049 | 4 | 1200 | 75 | 57 | 95 | 39.2 | 0.959 | 29.01 | 37.6 | 3.1 | 27
KJ049 | 4 | 1200 | 80 | 57 | 95 | 39.2 | 1 | 30.25 | 39.2 | 3.1 | 27
KJ049 | 4 | 1200 | 85 | 57 | 95 | 39.2 | 1 | 30.25 | 39.2 | 3.1 | 27
KJ049 | 4 | 1200 | 90 | 57 | 95 | 39.2 | 1 | 30.25 | 39.2 | 3.1 | 27
KJ049 | 4 | 1200 | 65 | 62 | 95 | 42.9 | 0.42 | 13.89 | 18 | 3.2 | 27
KJ049 | 4 | 1200 | 70 | 62 | 95 | 42.9 | 0.573 | 18.98 | 24.6 | 3.2 | 27
KJ049 | 4 | 1200 | 75 | 62 | 95 | 42.9 | 0.727 | 24.07 | 31.2 | 3.2 | 27
KJ049 | 4 | 1200 | 80 | 62 | 95 | 42.9 | 0.881 | 29.17 | 37.8 | 3.2 | 27
KJ049 | 4 | 1200 | 85 | 62 | 95 | 42.9 | 1 | 33.1 | 42.9 | 3.2 | 27
KJ049 | 4 | 1200 | 90 | 62 | 95 | 42.9 | 1 | 33.1 | 42.9 | 3.2 | 27
KJ049 | 4 | 1200 | 70 | 67 | 95 | 46.7 | 0.392 | 14.12 | 18.3 | 3.2 | 27
KJ049 | 4 | 1200 | 75 | 67 | 95 | 46.7 | 0.531 | 19.14 | 24.8 | 3.2 | 27
KJ049 | 4 | 1200 | 80 | 67 | 95 | 46.7 | 0.668 | 24.07 | 31.2 | 3.2 | 27
KJ049 | 4 | 1200 | 85 | 67 | 95 | 46.7 | 0.805 | 29.01 | 37.6 | 3.2 | 27
KJ049 | 4 | 1200 | 90 | 67 | 95 | 46.7 | 0.94 | 33.87 | 43.9 | 3.2 | 27
KJ049 | 4 | 1200 | 75 | 72 | 95 | 51.5 | 0.355 | 14.12 | 18.3 | 3.2 | 27
KJ049 | 4 | 1200 | 80 | 72 | 95 | 51.5 | 0.48 | 19.06 | 24.7 | 3.2 | 27
KJ049 | 4 | 1200 | 85 | 72 | 95 | 51.5 | 0.604 | 24 | 31.1 | 3.2 | 27
KJ049 | 4 | 1200 | 90 | 72 | 95 | 51.5 | 0.728 | 28.94 | 37.5 | 3.2 | 27
KJ049 | 4 | 1200 | 80 | 77 | 95 | 56.4 | 0.323 | 14.04 | 18.2 | 3.1 | 27
KJ049 | 4 | 1200 | 85 | 77 | 95 | 56.4 | 0.438 | 19.06 | 24.7 | 3.1 | 27
KJ049 | 4 | 1200 | 90 | 77 | 95 | 56.4 | 0.551 | 24 | 31.1 | 3.1 | 27
KJ049 | 4 | 1200 | 65 | 57 | 105 | 38.3 | 0.574 | 16.98 | 22 | 3.6 | 27
KJ049 | 4 | 1200 | 70 | 57 | 105 | 38.3 | 0.749 | 22.15 | 28.7 | 3.6 | 27
KJ049 | 4 | 1200 | 75 | 57 | 105 | 38.3 | 0.924 | 27.31 | 35.4 | 3.6 | 27
KJ049 | 4 | 1200 | 80 | 57 | 105 | 38.3 | 1 | 29.55 | 38.3 | 3.6 | 27
KJ049 | 4 | 1200 | 85 | 57 | 105 | 38.3 | 1 | 29.55 | 38.3 | 3.6 | 27
KJ049 | 4 | 1200 | 90 | 57 | 105 | 38.3 | 1 | 29.55 | 38.3 | 3.6 | 27
KJ049 | 4 | 1200 | 65 | 62 | 105 | 41 | 0.39 | 12.35 | 16 | 3.7 | 27
KJ049 | 4 | 1200 | 70 | 62 | 105 | 41 | 0.551 | 17.44 | 22.6 | 3.7 | 27
KJ049 | 4 | 1200 | 75 | 62 | 105 | 41 | 0.712 | 22.53 | 29.2 | 3.7 | 27
KJ049 | 4 | 1200 | 80 | 62 | 105 | 41 | 0.873 | 27.62 | 35.8 | 3.7 | 27
KJ049 | 4 | 1200 | 85 | 62 | 105 | 41 | 1 | 31.64 | 41 | 3.7 | 27
KJ049 | 4 | 1200 | 90 | 62 | 105 | 41 | 1 | 31.64 | 41 | 3.7 | 27
KJ049 | 4 | 1200 | 70 | 67 | 105 | 43.7 | 0.38 | 12.81 | 16.6 | 3.7 | 27
KJ049 | 4 | 1200 | 75 | 67 | 105 | 43.7 | 0.526 | 17.75 | 23 | 3.7 | 27
KJ049 | 4 | 1200 | 80 | 67 | 105 | 43.7 | 0.675 | 22.76 | 29.5 | 3.7 | 27
KJ049 | 4 | 1200 | 85 | 67 | 105 | 43.7 | 0.819 | 27.62 | 35.8 | 3.7 | 27
KJ049 | 4 | 1200 | 90 | 67 | 105 | 43.7 | 0.963 | 32.48 | 42.1 | 3.7 | 27
KJ049 | 4 | 1200 | 75 | 72 | 105 | 47.8 | 0.351 | 12.96 | 16.8 | 3.7 | 27
KJ049 | 4 | 1200 | 80 | 72 | 105 | 47.8 | 0.483 | 17.82 | 23.1 | 3.7 | 27
KJ049 | 4 | 1200 | 85 | 72 | 105 | 47.8 | 0.617 | 22.76 | 29.5 | 3.7 | 27
KJ049 | 4 | 1200 | 90 | 72 | 105 | 47.8 | 0.749 | 27.62 | 35.8 | 3.7 | 27
KJ049 | 4 | 1200 | 80 | 77 | 105 | 51.9 | 0.324 | 12.96 | 16.8 | 3.7 | 27
KJ049 | 4 | 1200 | 85 | 77 | 105 | 51.9 | 0.445 | 17.82 | 23.1 | 3.7 | 27
KJ049 | 4 | 1200 | 90 | 77 | 105 | 51.9 | 0.568 | 22.76 | 29.5 | 3.7 | 27
KJ049 | 4 | 1200 | 65 | 57 | 115 | 37.5 | 0.525 | 15.2 | 19.7 | 4.2 | 28
KJ049 | 4 | 1200 | 70 | 57 | 115 | 37.5 | 0.707 | 20.45 | 26.5 | 4.2 | 28
KJ049 | 4 | 1200 | 75 | 57 | 115 | 37.5 | 0.888 | 25.69 | 33.3 | 4.2 | 28
KJ049 | 4 | 1200 | 80 | 57 | 115 | 37.5 | 1 | 28.94 | 37.5 | 4.2 | 28
KJ049 | 4 | 1200 | 85 | 57 | 115 | 37.5 | 1 | 28.94 | 37.5 | 4.2 | 28
KJ049 | 4 | 1200 | 90 | 57 | 115 | 37.5 | 1 | 28.94 | 37.5 | 4.2 | 28
KJ049 | 4 | 1200 | 65 | 62 | 115 | 39.1 | 0.361 | 10.88 | 14.1 | 4.2 | 28
KJ049 | 4 | 1200 | 70 | 62 | 115 | 39.1 | 0.529 | 15.97 | 20.7 | 4.2 | 28
KJ049 | 4 | 1200 | 75 | 62 | 115 | 39.1 | 0.698 | 21.06 | 27.3 | 4.2 | 28
KJ049 | 4 | 1200 | 80 | 62 | 115 | 39.1 | 0.867 | 26.16 | 33.9 | 4.2 | 28
KJ049 | 4 | 1200 | 85 | 62 | 115 | 39.1 | 0.977 | 29.48 | 38.2 | 4.2 | 28
KJ049 | 4 | 1200 | 90 | 62 | 115 | 39.1 | 1 | 30.17 | 39.1 | 4.2 | 28
KJ049 | 4 | 1200 | 70 | 67 | 115 | 40.7 | 0.364 | 11.42 | 14.8 | 4.2 | 28
KJ049 | 4 | 1200 | 75 | 67 | 115 | 40.7 | 0.523 | 16.44 | 21.3 | 4.2 | 28
KJ049 | 4 | 1200 | 80 | 67 | 115 | 40.7 | 0.681 | 21.37 | 27.7 | 4.2 | 28
KJ049 | 4 | 1200 | 85 | 67 | 115 | 40.7 | 0.835 | 26.23 | 34 | 4.2 | 28
KJ049 | 4 | 1200 | 90 | 67 | 115 | 40.7 | 0.99 | 31.1 | 40.3 | 4.2 | 28
KJ049 | 4 | 1200 | 75 | 72 | 115 | 44 | 0.348 | 11.81 | 15.3 | 4.2 | 28
KJ049 | 4 | 1200 | 80 | 72 | 115 | 44 | 0.489 | 16.59 | 21.5 | 4.2 | 28
KJ049 | 4 | 1200 | 85 | 72 | 115 | 44 | 0.632 | 21.45 | 27.8 | 4.2 | 28
KJ049 | 4 | 1200 | 90 | 72 | 115 | 44 | 0.775 | 26.31 | 34.1 | 4.2 | 28
KJ049 | 4 | 1200 | 80 | 77 | 115 | 47.4 | 0.325 | 11.88 | 15.4 | 4.3 | 28
KJ049 | 4 | 1200 | 85 | 77 | 115 | 47.4 | 0.456 | 16.67 | 21.6 | 4.3 | 28
KJ049 | 4 | 1200 | 90 | 77 | 115 | 47.4 | 0.589 | 21.53 | 27.9 | 4.3 | 28
KJ049 | 4 | 1200 | 65 | 57 | 125 | 36.6 | 0.478 | 13.5 | 17.5 | 4.7 | 28
KJ049 | 4 | 1200 | 70 | 57 | 125 | 36.6 | 0.664 | 18.75 | 24.3 | 4.7 | 28
KJ049 | 4 | 1200 | 75 | 57 | 125 | 36.6 | 0.85 | 24 | 31.1 | 4.7 | 28
KJ049 | 4 | 1200 | 80 | 57 | 125 | 36.6 | 1 | 28.24 | 36.6 | 4.7 | 28
KJ049 | 4 | 1200 | 85 | 57 | 125 | 36.6 | 1 | 28.24 | 36.6 | 4.7 | 28
KJ049 | 4 | 1200 | 90 | 57 | 125 | 36.6 | 1 | 28.24 | 36.6 | 4.7 | 28
KJ049 | 4 | 1200 | 65 | 62 | 125 | 37.2 | 0.325 | 9.34 | 12.1 | 4.7 | 28
KJ049 | 4 | 1200 | 70 | 62 | 125 | 37.2 | 0.503 | 14.43 | 18.7 | 4.7 | 28
KJ049 | 4 | 1200 | 75 | 62 | 125 | 37.2 | 0.68 | 19.52 | 25.3 | 4.7 | 28
KJ049 | 4 | 1200 | 80 | 62 | 125 | 37.2 | 0.86 | 24.69 | 32 | 4.7 | 28
KJ049 | 4 | 1200 | 85 | 62 | 125 | 37.2 | 0.946 | 27.16 | 35.2 | 4.7 | 28
KJ049 | 4 | 1200 | 90 | 62 | 125 | 37.2 | 1 | 28.7 | 37.2 | 4.7 | 28
KJ049 | 4 | 1200 | 70 | 67 | 125 | 37.7 | 0.347 | 10.11 | 13.1 | 4.7 | 28
KJ049 | 4 | 1200 | 75 | 67 | 125 | 37.7 | 0.517 | 15.05 | 19.5 | 4.7 | 28
KJ049 | 4 | 1200 | 80 | 67 | 125 | 37.7 | 0.69 | 20.06 | 26 | 4.7 | 28
KJ049 | 4 | 1200 | 85 | 67 | 125 | 37.7 | 0.854 | 24.85 | 32.2 | 4.7 | 28
KJ049 | 4 | 1200 | 90 | 67 | 125 | 37.7 | 1 | 29.09 | 37.7 | 4.7 | 28
KJ049 | 4 | 1200 | 75 | 72 | 125 | 40.3 | 0.34 | 10.57 | 13.7 | 4.8 | 28
KJ049 | 4 | 1200 | 80 | 72 | 125 | 40.3 | 0.494 | 15.35 | 19.9 | 4.8 | 28
KJ049 | 4 | 1200 | 85 | 72 | 125 | 40.3 | 0.65 | 20.22 | 26.2 | 4.8 | 28
KJ049 | 4 | 1200 | 90 | 72 | 125 | 40.3 | 0.804 | 25 | 32.4 | 4.8 | 28
KJ049 | 4 | 1200 | 80 | 77 | 125 | 42.9 | 0.324 | 10.73 | 13.9 | 4.8 | 28
KJ049 | 4 | 1200 | 85 | 77 | 125 | 42.9 | 0.469 | 15.51 | 20.1 | 4.8 | 28
KJ049 | 4 | 1200 | 90 | 77 | 125 | 42.9 | 0.613 | 20.29 | 26.3 | 4.8 | 28
KJ049 | 4 | 1400 | 65 | 57 | 75 | 49 | 0.59 | 19.11 | 28.9 | 2.5 | 27
KJ049 | 4 | 1400 | 70 | 57 | 75 | 49 | 0.749 | 24.27 | 36.7 | 2.5 | 27
KJ049 | 4 | 1400 | 75 | 57 | 75 | 49 | 0.908 | 29.43 | 44.5 | 2.5 | 27
KJ049 | 4 | 1400 | 80 | 57 | 75 | 49 | 1 | 32.41 | 49 | 2.5 | 27
KJ049 | 4 | 1400 | 85 | 57 | 75 | 49 | 1 | 32.41 | 49 | 2.5 | 27
KJ049 | 4 | 1400 | 90 | 57 | 75 | 49 | 1 | 32.41 | 49 | 2.5 | 27
KJ049 | 4 | 1400 | 65 | 62 | 75 | 52.2 | 0.418 | 14.42 | 21.8 | 2.5 | 27
KJ049 | 4 | 1400 | 70 | 62 | 75 | 52.2 | 0.565 | 19.51 | 29.5 | 2.5 | 27
KJ049 | 4 | 1400 | 75 | 62 | 75 | 52.2 | 0.703 | 24.27 | 36.7 | 2.5 | 27
KJ049 | 4 | 1400 | 80 | 62 | 75 | 52.2 | 0.856 | 29.56 | 44.7 | 2.5 | 27
KJ049 | 4 | 1400 | 85 | 62 | 75 | 52.2 | 0.95 | 32.8 | 49.6 | 2.5 | 27
KJ049 | 4 | 1400 | 90 | 62 | 75 | 52.2 | 1 | 34.52 | 52.2 | 2.5 | 27
KJ049 | 4 | 1400 | 70 | 67 | 75 | 55.4 | 0.401 | 14.68 | 22.2 | 2.5 | 27
KJ049 | 4 | 1400 | 75 | 67 | 75 | 55.4 | 0.536 | 19.64 | 29.7 | 2.5 | 27
KJ049 | 4 | 1400 | 80 | 67 | 75 | 55.4 | 0.671 | 24.6 | 37.2 | 2.5 | 27
KJ049 | 4 | 1400 | 85 | 67 | 75 | 55.4 | 0.796 | 29.17 | 44.1 | 2.5 | 27
KJ049 | 4 | 1400 | 90 | 67 | 75 | 55.4 | 0.919 | 33.66 | 50.9 | 2.5 | 27
KJ049 | 4 | 1400 | 75 | 72 | 75 | 60.2 | 0.37 | 14.75 | 22.3 | 2.5 | 27
KJ049 | 4 | 1400 | 80 | 72 | 75 | 60.2 | 0.493 | 19.64 | 29.7 | 2.5 | 27
KJ049 | 4 | 1400 | 85 | 72 | 75 | 60.2 | 0.616 | 24.54 | 37.1 | 2.5 | 27
KJ049 | 4 | 1400 | 90 | 72 | 75 | 60.2 | 0.739 | 29.43 | 44.5 | 2.5 | 27
KJ049 | 4 | 1400 | 80 | 77 | 75 | 65 | 0.342 | 14.68 | 22.2 | 2.5 | 27
KJ049 | 4 | 1400 | 85 | 77 | 75 | 65 | 0.465 | 19.97 | 30.2 | 2.5 | 27
KJ049 | 4 | 1400 | 90 | 77 | 75 | 65 | 0.586 | 25.2 | 38.1 | 2.5 | 27
KJ049 | 4 | 1400 | 65 | 57 | 85 | 46.1 | 0.594 | 18.12 | 27.4 | 2.8 | 27
KJ049 | 4 | 1400 | 70 | 57 | 85 | 46.1 | 0.764 | 23.28 | 35.2 | 2.8 | 27
KJ049 | 4 | 1400 | 75 | 57 | 85 | 46.1 | 0.931 | 28.37 | 42.9 | 2.8 | 27
KJ049 | 4 | 1400 | 80 | 57 | 85 | 46.1 | 1 | 30.49 | 46.1 | 2.8 | 27
KJ049 | 4 | 1400 | 85 | 57 | 85 | 46.1 | 1 | 30.49 | 46.1 | 2.8 | 27
KJ049 | 4 | 1400 | 90 | 57 | 85 | 46.1 | 1 | 30.49 | 46.1 | 2.8 | 27
KJ049 | 4 | 1400 | 65 | 62 | 85 | 49.1 | 0.411 | 13.36 | 20.2 | 2.8 | 27
KJ049 | 4 | 1400 | 70 | 62 | 85 | 49.1 | 0.568 | 18.45 | 27.9 | 2.8 | 27
KJ049 | 4 | 1400 | 75 | 62 | 85 | 49.1 | 0.719 | 23.35 | 35.3 | 2.8 | 27
KJ049 | 4 | 1400 | 80 | 62 | 85 | 49.1 | 0.88 | 28.57 | 43.2 | 2.8 | 27
KJ049 | 4 | 1400 | 85 | 62 | 85 | 49.1 | 0.982 | 31.88 | 48.2 | 2.8 | 27
KJ049 | 4 | 1400 | 90 | 62 | 85 | 49.1 | 1 | 32.47 | 49.1 | 2.8 | 27
KJ049 | 4 | 1400 | 70 | 67 | 85 | 52.2 | 0.395 | 13.62 | 20.6 | 2.8 | 27
KJ049 | 4 | 1400 | 75 | 67 | 85 | 52.2 | 0.538 | 18.58 | 28.1 | 2.8 | 27
KJ049 | 4 | 1400 | 80 | 67 | 85 | 52.2 | 0.682 | 23.54 | 35.6 | 2.8 | 27
KJ049 | 4 | 1400 | 85 | 67 | 85 | 52.2 | 0.81 | 27.98 | 42.3 | 2.8 | 27
KJ049 | 4 | 1400 | 90 | 67 | 85 | 52.2 | 0.937 | 32.34 | 48.9 | 2.8 | 27
KJ049 | 4 | 1400 | 75 | 72 | 85 | 56.7 | 0.365 | 13.69 | 20.7 | 2.8 | 27
KJ049 | 4 | 1400 | 80 | 72 | 85 | 56.7 | 0.496 | 18.58 | 28.1 | 2.8 | 27
KJ049 | 4 | 1400 | 85 | 72 | 85 | 56.7 | 0.626 | 23.48 | 35.5 | 2.8 | 27
KJ049 | 4 | 1400 | 90 | 72 | 85 | 56.7 | 0.758 | 28.44 | 43 | 2.8 | 27
KJ049 | 4 | 1400 | 80 | 77 | 85 | 61.1 | 0.337 | 13.62 | 20.6 | 2.8 | 27
KJ049 | 4 | 1400 | 85 | 77 | 85 | 61.1 | 0.471 | 19.05 | 28.8 | 2.8 | 27
KJ049 | 4 | 1400 | 90 | 77 | 85 | 61.1 | 0.606 | 24.47 | 37 | 2.8 | 27
KJ049 | 4 | 1400 | 65 | 57 | 95 | 43.1 | 0.601 | 17.13 | 25.9 | 3.1 | 27
KJ049 | 4 | 1400 | 70 | 57 | 95 | 43.1 | 0.78 | 22.22 | 33.6 | 3.1 | 27
KJ049 | 4 | 1400 | 75 | 57 | 95 | 43.1 | 0.961 | 27.38 | 41.4 | 3.1 | 27
KJ049 | 4 | 1400 | 80 | 57 | 95 | 43.1 | 1 | 28.51 | 43.1 | 3.1 | 27
KJ049 | 4 | 1400 | 85 | 57 | 95 | 43.1 | 1 | 28.51 | 43.1 | 3.1 | 27
KJ049 | 4 | 1400 | 90 | 57 | 95 | 43.1 | 1 | 28.51 | 43.1 | 3.1 | 27
KJ049 | 4 | 1400 | 65 | 62 | 95 | 46.1 | 0.403 | 12.3 | 18.6 | 3.2 | 27
KJ049 | 4 | 1400 | 70 | 62 | 95 | 46.1 | 0.57 | 17.39 | 26.3 | 3.2 | 27
KJ049 | 4 | 1400 | 75 | 62 | 95 | 46.1 | 0.735 | 22.42 | 33.9 | 3.2 | 27
KJ049 | 4 | 1400 | 80 | 62 | 95 | 46.1 | 0.902 | 27.51 | 41.6 | 3.2 | 27
KJ049 | 4 | 1400 | 85 | 62 | 95 | 46.1 | 1 | 30.49 | 46.1 | 3.2 | 27
KJ049 | 4 | 1400 | 90 | 62 | 95 | 46.1 | 1 | 30.49 | 46.1 | 3.2 | 27
KJ049 | 4 | 1400 | 70 | 67 | 95 | 49 | 0.386 | 12.5 | 18.9 | 3.2 | 27
KJ049 | 4 | 1400 | 75 | 67 | 95 | 49 | 0.541 | 17.53 | 26.5 | 3.2 | 27
KJ049 | 4 | 1400 | 80 | 67 | 95 | 49 | 0.696 | 22.55 | 34.1 | 3.2 | 27
KJ049 | 4 | 1400 | 85 | 67 | 95 | 49 | 0.827 | 26.79 | 40.5 | 3.2 | 27
KJ049 | 4 | 1400 | 90 | 67 | 95 | 49 | 0.959 | 31.08 | 47 | 3.2 | 27
KJ049 | 4 | 1400 | 75 | 72 | 95 | 53.1 | 0.358 | 12.57 | 19 | 3.2 | 27
KJ049 | 4 | 1400 | 80 | 72 | 95 | 53.1 | 0.499 | 17.53 | 26.5 | 3.2 | 27
KJ049 | 4 | 1400 | 85 | 72 | 95 | 53.1 | 0.64 | 22.49 | 34 | 3.2 | 27
KJ049 | 4 | 1400 | 90 | 72 | 95 | 53.1 | 0.78 | 27.38 | 41.4 | 3.2 | 27
KJ049 | 4 | 1400 | 80 | 77 | 95 | 57.2 | 0.332 | 12.57 | 19 | 3.2 | 27
KJ049 | 4 | 1400 | 85 | 77 | 95 | 57.2 | 0.479 | 18.12 | 27.4 | 3.2 | 27
KJ049 | 4 | 1400 | 90 | 77 | 95 | 57.2 | 0.628 | 23.74 | 35.9 | 3.2 | 27
KJ049 | 4 | 1400 | 65 | 57 | 105 | 41.7 | 0.568 | 15.67 | 23.7 | 3.7 | 27
KJ049 | 4 | 1400 | 70 | 57 | 105 | 41.7 | 0.76 | 20.97 | 31.7 | 3.7 | 27
KJ049 | 4 | 1400 | 75 | 57 | 105 | 41.7 | 0.95 | 26.19 | 39.6 | 3.7 | 27
KJ049 | 4 | 1400 | 80 | 57 | 105 | 41.7 | 1 | 27.58 | 41.7 | 3.7 | 27
KJ049 | 4 | 1400 | 85 | 57 | 105 | 41.7 | 1 | 27.58 | 41.7 | 3.7 | 27
KJ049 | 4 | 1400 | 90 | 57 | 105 | 41.7 | 1 | 27.58 | 41.7 | 3.7 | 27
KJ049 | 4 | 1400 | 65 | 62 | 105 | 43.8 | 0.379 | 10.98 | 16.6 | 3.7 | 27
KJ049 | 4 | 1400 | 70 | 62 | 105 | 43.8 | 0.557 | 16.14 | 24.4 | 3.7 | 27
KJ049 | 4 | 1400 | 75 | 62 | 105 | 43.8 | 0.735 | 21.3 | 32.2 | 3.7 | 27
KJ049 | 4 | 1400 | 80 | 62 | 105 | 43.8 | 0.911 | 26.39 | 39.9 | 3.7 | 27
KJ049 | 4 | 1400 | 85 | 62 | 105 | 43.8 | 1 | 28.97 | 43.8 | 3.7 | 27
KJ049 | 4 | 1400 | 90 | 62 | 105 | 43.8 | 1 | 28.97 | 43.8 | 3.7 | 27
KJ049 | 4 | 1400 | 70 | 67 | 105 | 45.9 | 0.373 | 11.31 | 17.1 | 3.7 | 27
KJ049 | 4 | 1400 | 75 | 67 | 105 | 45.9 | 0.538 | 16.34 | 24.7 | 3.7 | 27
KJ049 | 4 | 1400 | 80 | 67 | 105 | 45.9 | 0.704 | 21.36 | 32.3 | 3.7 | 27
KJ049 | 4 | 1400 | 85 | 67 | 105 | 45.9 | 0.841 | 25.53 | 38.6 | 3.7 | 27
KJ049 | 4 | 1400 | 90 | 67 | 105 | 45.9 | 0.978 | 29.7 | 44.9 | 3.7 | 27
KJ049 | 4 | 1400 | 75 | 72 | 105 | 49.4 | 0.348 | 11.38 | 17.2 | 3.7 | 27
KJ049 | 4 | 1400 | 80 | 72 | 105 | 49.4 | 0.5 | 16.34 | 24.7 | 3.7 | 27
KJ049 | 4 | 1400 | 85 | 72 | 105 | 49.4 | 0.652 | 21.3 | 32.2 | 3.7 | 27
KJ049 | 4 | 1400 | 90 | 72 | 105 | 49.4 | 0.802 | 26.19 | 39.6 | 3.7 | 27
KJ049 | 4 | 1400 | 80 | 77 | 105 | 52.8 | 0.324 | 11.31 | 17.1 | 3.7 | 27
KJ049 | 4 | 1400 | 85 | 77 | 105 | 52.8 | 0.487 | 17 | 25.7 | 3.7 | 27
KJ049 | 4 | 1400 | 90 | 77 | 105 | 52.8 | 0.652 | 22.75 | 34.4 | 3.7 | 27
KJ049 | 4 | 1400 | 65 | 57 | 115 | 40.3 | 0.536 | 14.29 | 21.6 | 4.2 | 28
KJ049 | 4 | 1400 | 70 | 57 | 115 | 40.3 | 0.737 | 19.64 | 29.7 | 4.2 | 28
KJ049 | 4 | 1400 | 75 | 57 | 115 | 40.3 | 0.94 | 25.07 | 37.9 | 4.2 | 28
KJ049 | 4 | 1400 | 80 | 57 | 115 | 40.3 | 1 | 26.65 | 40.3 | 4.2 | 28
KJ049 | 4 | 1400 | 85 | 57 | 115 | 40.3 | 1 | 26.65 | 40.3 | 4.2 | 28
KJ049 | 4 | 1400 | 90 | 57 | 115 | 40.3 | 1 | 26.65 | 40.3 | 4.2 | 28
KJ049 | 4 | 1400 | 65 | 62 | 115 | 41.6 | 0.351 | 9.66 | 14.6 | 4.2 | 28
KJ049 | 4 | 1400 | 70 | 62 | 115 | 41.6 | 0.541 | 14.88 | 22.5 | 4.2 | 28
KJ049 | 4 | 1400 | 75 | 62 | 115 | 41.6 | 0.731 | 20.11 | 30.4 | 4.2 | 28
KJ049 | 4 | 1400 | 80 | 62 | 115 | 41.6 | 0.921 | 25.33 | 38.3 | 4.2 | 28
KJ049 | 4 | 1400 | 85 | 62 | 115 | 41.6 | 0.993 | 27.31 | 41.3 | 4.2 | 28
KJ049 | 4 | 1400 | 90 | 62 | 115 | 41.6 | 1 | 27.51 | 41.6 | 4.2 | 28
KJ049 | 4 | 1400 | 70 | 67 | 115 | 42.8 | 0.355 | 10.05 | 15.2 | 4.2 | 28
KJ049 | 4 | 1400 | 75 | 67 | 115 | 42.8 | 0.535 | 15.15 | 22.9 | 4.2 | 28
KJ049 | 4 | 1400 | 80 | 67 | 115 | 42.8 | 0.715 | 20.24 | 30.6 | 4.2 | 28
KJ049 | 4 | 1400 | 85 | 67 | 115 | 42.8 | 0.857 | 24.27 | 36.7 | 4.2 | 28
KJ049 | 4 | 1400 | 90 | 67 | 115 | 42.8 | 1 | 28.31 | 42.8 | 4.2 | 28
KJ049 | 4 | 1400 | 75 | 72 | 115 | 45.6 | 0.338 | 10.19 | 15.4 | 4.2 | 28
KJ049 | 4 | 1400 | 80 | 72 | 115 | 45.6 | 0.502 | 15.15 | 22.9 | 4.2 | 28
KJ049 | 4 | 1400 | 85 | 72 | 115 | 45.6 | 0.664 | 20.04 | 30.3 | 4.2 | 28
KJ049 | 4 | 1400 | 90 | 72 | 115 | 45.6 | 0.829 | 25 | 37.8 | 4.2 | 28
KJ049 | 4 | 1400 | 80 | 77 | 115 | 48.4 | 0.314 | 10.05 | 15.2 | 4.3 | 28
KJ049 | 4 | 1400 | 85 | 77 | 115 | 48.4 | 0.496 | 15.87 | 24 | 4.3 | 28
KJ049 | 4 | 1400 | 90 | 77 | 115 | 48.4 | 0.678 | 21.69 | 32.8 | 4.3 | 28
KJ049 | 4 | 1400 | 65 | 57 | 125 | 39 | 0.5 | 12.9 | 19.5 | 4.7 | 28
KJ049 | 4 | 1400 | 70 | 57 | 125 | 39 | 0.713 | 18.39 | 27.8 | 4.7 | 28
KJ049 | 4 | 1400 | 75 | 57 | 125 | 39 | 0.926 | 23.88 | 36.1 | 4.7 | 28
KJ049 | 4 | 1400 | 80 | 57 | 125 | 39 | 1 | 25.79 | 39 | 4.7 | 28
KJ049 | 4 | 1400 | 85 | 57 | 125 | 39 | 1 | 25.79 | 39 | 4.7 | 28
KJ049 | 4 | 1400 | 90 | 57 | 125 | 39 | 1 | 25.79 | 39 | 4.7 | 28
KJ049 | 4 | 1400 | 65 | 62 | 125 | 39.3 | 0.321 | 8.33 | 12.6 | 4.7 | 28
KJ049 | 4 | 1400 | 70 | 62 | 125 | 39.3 | 0.524 | 13.62 | 20.6 | 4.7 | 28
KJ049 | 4 | 1400 | 75 | 62 | 125 | 39.3 | 0.728 | 18.92 | 28.6 | 4.7 | 28
KJ049 | 4 | 1400 | 80 | 62 | 125 | 39.3 | 0.931 | 24.21 | 36.6 | 4.7 | 28
KJ049 | 4 | 1400 | 85 | 62 | 125 | 39.3 | 0.982 | 25.53 | 38.6 | 4.7 | 28
KJ049 | 4 | 1400 | 90 | 62 | 125 | 39.3 | 1 | 25.99 | 39.3 | 4.7 | 28
KJ049 | 4 | 1400 | 70 | 67 | 125 | 39.7 | 0.335 | 8.8 | 13.3 | 4.7 | 28
KJ049 | 4 | 1400 | 75 | 67 | 125 | 39.7 | 0.531 | 13.96 | 21.1 | 4.7 | 28
KJ049 | 4 | 1400 | 80 | 67 | 125 | 39.7 | 0.725 | 19.05 | 28.8 | 4.7 | 28
KJ049 | 4 | 1400 | 85 | 67 | 125 | 39.7 | 0.874 | 22.95 | 34.7 | 4.7 | 28
KJ049 | 4 | 1400 | 90 | 67 | 125 | 39.7 | 1 | 26.26 | 39.7 | 4.7 | 28
KJ049 | 4 | 1400 | 75 | 72 | 125 | 41.8 | 0.325 | 8.99 | 13.6 | 4.8 | 28
KJ049 | 4 | 1400 | 80 | 72 | 125 | 41.8 | 0.502 | 13.89 | 21 | 4.8 | 28
KJ049 | 4 | 1400 | 85 | 72 | 125 | 41.8 | 0.682 | 18.85 | 28.5 | 4.8 | 28
KJ049 | 4 | 1400 | 90 | 72 | 125 | 41.8 | 0.861 | 23.81 | 36 | 4.8 | 28
KJ049 | 4 | 1400 | 80 | 77 | 125 | 43.9 | 0.303 | 8.8 | 13.3 | 4.8 | 28
KJ049 | 4 | 1400 | 85 | 77 | 125 | 43.9 | 0.508 | 14.75 | 22.3 | 4.8 | 28
KJ049 | 4 | 1400 | 90 | 77 | 125 | 43.9 | 0.713 | 20.7 | 31.3 | 4.8 | 28
KJ049 | 4 | 1600 | 65 | 57 | 75 | 52.6 | 0.584 | 17.77 | 30.7 | 2.5 | 27
KJ049 | 4 | 1600 | 70 | 57 | 75 | 52.6 | 0.751 | 22.86 | 39.5 | 2.5 | 27
KJ049 | 4 | 1600 | 75 | 57 | 75 | 52.6 | 0.918 | 27.95 | 48.3 | 2.5 | 27
KJ049 | 4 | 1600 | 80 | 57 | 75 | 52.6 | 1 | 30.44 | 52.6 | 2.5 | 27
KJ049 | 4 | 1600 | 85 | 57 | 75 | 52.6 | 1 | 30.44 | 52.6 | 2.5 | 27
KJ049 | 4 | 1600 | 90 | 57 | 75 | 52.6 | 1 | 30.44 | 52.6 | 2.5 | 27
KJ049 | 4 | 1600 | 65 | 62 | 75 | 54.8 | 0.411 | 13.02 | 22.5 | 2.5 | 27
KJ049 | 4 | 1600 | 70 | 62 | 75 | 54.8 | 0.569 | 18.06 | 31.2 | 2.5 | 27
KJ049 | 4 | 1600 | 75 | 62 | 75 | 54.8 | 0.723 | 22.92 | 39.6 | 2.5 | 27
KJ049 | 4 | 1600 | 80 | 62 | 75 | 54.8 | 0.887 | 28.12 | 48.6 | 2.5 | 27
KJ049 | 4 | 1600 | 85 | 62 | 75 | 54.8 | 0.962 | 30.5 | 52.7 | 2.5 | 27
KJ049 | 4 | 1600 | 90 | 62 | 75 | 54.8 | 1 | 31.71 | 54.8 | 2.5 | 27
KJ049 | 4 | 1600 | 70 | 67 | 75 | 57.1 | 0.401 | 13.25 | 22.9 | 2.5 | 27
KJ049 | 4 | 1600 | 75 | 67 | 75 | 57.1 | 0.552 | 18.23 | 31.5 | 2.5 | 27
KJ049 | 4 | 1600 | 80 | 67 | 75 | 57.1 | 0.702 | 23.21 | 40.1 | 2.5 | 27
KJ049 | 4 | 1600 | 85 | 67 | 75 | 57.1 | 0.828 | 27.37 | 47.3 | 2.5 | 27
KJ049 | 4 | 1600 | 90 | 67 | 75 | 57.1 | 0.954 | 31.54 | 54.5 | 2.5 | 27
KJ049 | 4 | 1600 | 75 | 72 | 75 | 61.5 | 0.376 | 13.37 | 23.1 | 2.5 | 27
KJ049 | 4 | 1600 | 80 | 72 | 75 | 61.5 | 0.514 | 18.29 | 31.6 | 2.5 | 27
KJ049 | 4 | 1600 | 85 | 72 | 75 | 61.5 | 0.65 | 23.15 | 40 | 2.5 | 27
KJ049 | 4 | 1600 | 90 | 72 | 75 | 61.5 | 0.789 | 28.07 | 48.5 | 2.5 | 27
KJ049 | 4 | 1600 | 80 | 77 | 75 | 65.8 | 0.351 | 13.37 | 23.1 | 2.5 | 27
KJ049 | 4 | 1600 | 85 | 77 | 75 | 65.8 | 0.497 | 18.92 | 32.7 | 2.5 | 27
KJ049 | 4 | 1600 | 90 | 77 | 75 | 65.8 | 0.644 | 24.54 | 42.4 | 2.5 | 27
KJ049 | 4 | 1600 | 65 | 57 | 85 | 49.8 | 0.584 | 16.84 | 29.1 | 2.8 | 27
KJ049 | 4 | 1600 | 70 | 57 | 85 | 49.8 | 0.761 | 21.93 | 37.9 | 2.8 | 27
KJ049 | 4 | 1600 | 75 | 57 | 85 | 49.8 | 0.938 | 27.03 | 46.7 | 2.8 | 27
KJ049 | 4 | 1600 | 80 | 57 | 85 | 49.8 | 1 | 28.82 | 49.8 | 2.8 | 27
KJ049 | 4 | 1600 | 85 | 57 | 85 | 49.8 | 1 | 28.82 | 49.8 | 2.8 | 27
KJ049 | 4 | 1600 | 90 | 57 | 85 | 49.8 | 1 | 28.82 | 49.8 | 2.8 | 27
KJ049 | 4 | 1600 | 65 | 62 | 85 | 52 | 0.402 | 12.09 | 20.9 | 2.8 | 27
KJ049 | 4 | 1600 | 70 | 62 | 85 | 52 | 0.569 | 17.13 | 29.6 | 2.8 | 27
KJ049 | 4 | 1600 | 75 | 62 | 85 | 52 | 0.735 | 22.11 | 38.2 | 2.8 | 27
KJ049 | 4 | 1600 | 80 | 62 | 85 | 52 | 0.904 | 27.2 | 47 | 2.8 | 27
KJ049 | 4 | 1600 | 85 | 62 | 85 | 52 | 0.983 | 29.57 | 51.1 | 2.8 | 27
KJ049 | 4 | 1600 | 90 | 62 | 85 | 52 | 1 | 30.09 | 52 | 2.8 | 27
KJ049 | 4 | 1600 | 70 | 67 | 85 | 54.2 | 0.393 | 12.33 | 21.3 | 2.8 | 27
KJ049 | 4 | 1600 | 75 | 67 | 85 | 54.2 | 0.552 | 17.3 | 29.9 | 2.8 | 27
KJ049 | 4 | 1600 | 80 | 67 | 85 | 54.2 | 0.71 | 22.28 | 38.5 | 2.8 | 27
KJ049 | 4 | 1600 | 85 | 67 | 85 | 54.2 | 0.838 | 26.27 | 45.4 | 2.8 | 27
KJ049 | 4 | 1600 | 90 | 67 | 85 | 54.2 | 0.963 | 30.21 | 52.2 | 2.8 | 27
KJ049 | 4 | 1600 | 75 | 72 | 85 | 58.1 | 0.368 | 12.38 | 21.4 | 2.8 | 27
KJ049 | 4 | 1600 | 80 | 72 | 85 | 58.1 | 0.515 | 17.3 | 29.9 | 2.8 | 27
KJ049 | 4 | 1600 | 85 | 72 | 85 | 58.1 | 0.661 | 22.22 | 38.4 | 2.8 | 27
KJ049 | 4 | 1600 | 90 | 72 | 85 | 58.1 | 0.807 | 27.14 | 46.9 | 2.8 | 27
KJ049 | 4 | 1600 | 80 | 77 | 85 | 62 | 0.345 | 12.38 | 21.4 | 2.8 | 27
KJ049 | 4 | 1600 | 85 | 77 | 85 | 62 | 0.508 | 18.23 | 31.5 | 2.8 | 27
KJ049 | 4 | 1600 | 90 | 77 | 85 | 62 | 0.671 | 24.07 | 41.6 | 2.8 | 27
KJ049 | 4 | 1600 | 65 | 57 | 95 | 47.1 | 0.584 | 15.91 | 27.5 | 3.1 | 27
KJ049 | 4 | 1600 | 70 | 57 | 95 | 47.1 | 0.773 | 21.06 | 36.4 | 3.1 | 27
KJ049 | 4 | 1600 | 75 | 57 | 95 | 47.1 | 0.96 | 26.16 | 45.2 | 3.1 | 27
KJ049 | 4 | 1600 | 80 | 57 | 95 | 47.1 | 1 | 27.26 | 47.1 | 3.1 | 27
KJ049 | 4 | 1600 | 85 | 57 | 95 | 47.1 | 1 | 27.26 | 47.1 | 3.1 | 27
KJ049 | 4 | 1600 | 90 | 57 | 95 | 47.1 | 1 | 27.26 | 47.1 | 3.1 | 27
KJ049 | 4 | 1600 | 65 | 62 | 95 | 49.2 | 0.39 | 11.11 | 19.2 | 3.2 | 27
KJ049 | 4 | 1600 | 70 | 62 | 95 | 49.2 | 0.569 | 16.2 | 28 | 3.2 | 27
KJ049 | 4 | 1600 | 75 | 62 | 95 | 49.2 | 0.746 | 21.24 | 36.7 | 3.2 | 27
KJ049 | 4 | 1600 | 80 | 62 | 95 | 49.2 | 0.925 | 26.33 | 45.5 | 3.2 | 27
KJ049 | 4 | 1600 | 85 | 62 | 95 | 49.2 | 1 | 28.47 | 49.2 | 3.2 | 27
KJ049 | 4 | 1600 | 90 | 62 | 95 | 49.2 | 1 | 28.47 | 49.2 | 3.2 | 27
KJ049 | 4 | 1600 | 70 | 67 | 95 | 51.4 | 0.381 | 11.34 | 19.6 | 3.2 | 27
KJ049 | 4 | 1600 | 75 | 67 | 95 | 51.4 | 0.549 | 16.32 | 28.2 | 3.2 | 27
KJ049 | 4 | 1600 | 80 | 67 | 95 | 51.4 | 0.718 | 21.35 | 36.9 | 3.2 | 27
KJ049 | 4 | 1600 | 85 | 67 | 95 | 51.4 | 0.844 | 25.12 | 43.4 | 3.2 | 27
KJ049 | 4 | 1600 | 90 | 67 | 95 | 51.4 | 0.973 | 28.94 | 50 | 3.2 | 27
KJ049 | 4 | 1600 | 75 | 72 | 95 | 54.8 | 0.359 | 11.4 | 19.7 | 3.2 | 27
KJ049 | 4 | 1600 | 80 | 72 | 95 | 54.8 | 0.516 | 16.38 | 28.3 | 3.2 | 27
KJ049 | 4 | 1600 | 85 | 72 | 95 | 54.8 | 0.672 | 21.3 | 36.8 | 3.2 | 27
KJ049 | 4 | 1600 | 90 | 72 | 95 | 54.8 | 0.828 | 26.27 | 45.4 | 3.2 | 27
KJ049 | 4 | 1600 | 80 | 77 | 95 | 58.1 | 0.339 | 11.4 | 19.7 | 3.2 | 27
KJ049 | 4 | 1600 | 85 | 77 | 95 | 58.1 | 0.52 | 17.48 | 30.2 | 3.2 | 27
KJ049 | 4 | 1600 | 90 | 77 | 95 | 58.1 | 0.702 | 23.61 | 40.8 | 3.2 | 27
KJ049 | 4 | 1600 | 65 | 57 | 105 | 45.2 | 0.564 | 14.76 | 25.5 | 3.7 | 27
KJ049 | 4 | 1600 | 70 | 57 | 105 | 45.2 | 0.768 | 20.08 | 34.7 | 3.7 | 27
KJ049 | 4 | 1600 | 75 | 57 | 105 | 45.2 | 0.969 | 25.35 | 43.8 | 3.7 | 27
KJ049 | 4 | 1600 | 80 | 57 | 105 | 45.2 | 1 | 26.16 | 45.2 | 3.7 | 27
KJ049 | 4 | 1600 | 85 | 57 | 105 | 45.2 | 1 | 26.16 | 45.2 | 3.7 | 27
KJ049 | 4 | 1600 | 90 | 57 | 105 | 45.2 | 1 | 26.16 | 45.2 | 3.7 | 27
KJ049 | 4 | 1600 | 65 | 62 | 105 | 46.7 | 0.368 | 9.95 | 17.2 | 3.7 | 27
KJ049 | 4 | 1600 | 70 | 62 | 105 | 46.7 | 0.559 | 15.1 | 26.1 | 3.7 | 27
KJ049 | 4 | 1600 | 75 | 62 | 105 | 46.7 | 0.752 | 20.31 | 35.1 | 3.7 | 27
KJ049 | 4 | 1600 | 80 | 62 | 105 | 46.7 | 0.944 | 25.52 | 44.1 | 3.7 | 27
KJ049 | 4 | 1600 | 85 | 62 | 105 | 46.7 | 1 | 27.03 | 46.7 | 3.7 | 27
KJ049 | 4 | 1600 | 90 | 62 | 105 | 46.7 | 1 | 27.03 | 46.7 | 3.7 | 27
KJ049 | 4 | 1600 | 70 | 67 | 105 | 48.2 | 0.365 | 10.19 | 17.6 | 3.7 | 27
KJ049 | 4 | 1600 | 75 | 67 | 105 | 48.2 | 0.548 | 15.28 | 26.4 | 3.7 | 27
KJ049 | 4 | 1600 | 80 | 67 | 105 | 48.2 | 0.728 | 20.31 | 35.1 | 3.7 | 27
KJ049 | 4 | 1600 | 85 | 67 | 105 | 48.2 | 0.859 | 23.96 | 41.4 | 3.7 | 27
KJ049 | 4 | 1600 | 90 | 67 | 105 | 48.2 | 0.988 | 27.55 | 47.6 | 3.7 | 27
KJ049 | 4 | 1600 | 75 | 72 | 105 | 51 | 0.345 | 10.19 | 17.6 | 3.7 | 27
KJ049 | 4 | 1600 | 80 | 72 | 105 | 51 | 0.514 | 15.16 | 26.2 | 3.7 | 27
KJ049 | 4 | 1600 | 85 | 72 | 105 | 51 | 0.682 | 20.14 | 34.8 | 3.7 | 27
KJ049 | 4 | 1600 | 90 | 72 | 105 | 51 | 0.851 | 25.12 | 43.4 | 3.7 | 27
KJ049 | 4 | 1600 | 80 | 77 | 105 | 53.7 | 0.322 | 10.01 | 17.3 | 3.7 | 27
KJ049 | 4 | 1600 | 85 | 77 | 105 | 53.7 | 0.527 | 16.38 | 28.3 | 3.7 | 27
KJ049 | 4 | 1600 | 90 | 77 | 105 | 53.7 | 0.732 | 22.74 | 39.3 | 3.7 | 27
KJ049 | 4 | 1600 | 65 | 57 | 115 | 43.2 | 0.546 | 13.66 | 23.6 | 4.2 | 28
KJ049 | 4 | 1600 | 70 | 57 | 115 | 43.2 | 0.764 | 19.1 | 33 | 4.2 | 28
KJ049 | 4 | 1600 | 75 | 57 | 115 | 43.2 | 0.981 | 24.54 | 42.4 | 4.2 | 28
KJ049 | 4 | 1600 | 80 | 57 | 115 | 43.2 | 1 | 25 | 43.2 | 4.2 | 28
KJ049 | 4 | 1600 | 85 | 57 | 115 | 43.2 | 1 | 25 | 43.2 | 4.2 | 28
KJ049 | 4 | 1600 | 90 | 57 | 115 | 43.2 | 1 | 25 | 43.2 | 4.2 | 28
KJ049 | 4 | 1600 | 65 | 62 | 115 | 44.1 | 0.342 | 8.74 | 15.1 | 4.2 | 28
KJ049 | 4 | 1600 | 70 | 62 | 115 | 44.1 | 0.551 | 14.06 | 24.3 | 4.2 | 28
KJ049 | 4 | 1600 | 75 | 62 | 115 | 44.1 | 0.76 | 19.39 | 33.5 | 4.2 | 28
KJ049 | 4 | 1600 | 80 | 62 | 115 | 44.1 | 0.966 | 24.65 | 42.6 | 4.2 | 28
KJ049 | 4 | 1600 | 85 | 62 | 115 | 44.1 | 1 | 25.52 | 44.1 | 4.2 | 28
KJ049 | 4 | 1600 | 90 | 62 | 115 | 44.1 | 1 | 25.52 | 44.1 | 4.2 | 28
KJ049 | 4 | 1600 | 70 | 67 | 115 | 45 | 0.347 | 9.03 | 15.6 | 4.2 | 28
KJ049 | 4 | 1600 | 75 | 67 | 115 | 45 | 0.544 | 14.18 | 24.5 | 4.2 | 28
KJ049 | 4 | 1600 | 80 | 67 | 115 | 45 | 0.742 | 19.33 | 33.4 | 4.2 | 28
KJ049 | 4 | 1600 | 85 | 67 | 115 | 45 | 0.873 | 22.74 | 39.3 | 4.2 | 28
KJ049 | 4 | 1600 | 90 | 67 | 115 | 45 | 1 | 26.04 | 45 | 4.2 | 28
KJ049 | 4 | 1600 | 75 | 72 | 115 | 47.2 | 0.328 | 8.97 | 15.5 | 4.2 | 28
KJ049 | 4 | 1600 | 80 | 72 | 115 | 47.2 | 0.513 | 14 | 24.2 | 4.2 | 28
KJ049 | 4 | 1600 | 85 | 72 | 115 | 47.2 | 0.695 | 18.98 | 32.8 | 4.2 | 28
KJ049 | 4 | 1600 | 90 | 72 | 115 | 47.2 | 0.879 | 24.02 | 41.5 | 4.2 | 28
KJ049 | 4 | 1600 | 80 | 77 | 115 | 49.3 | 0.304 | 8.68 | 15 | 4.3 | 28
KJ049 | 4 | 1600 | 85 | 77 | 115 | 49.3 | 0.535 | 15.28 | 26.4 | 4.3 | 28
KJ049 | 4 | 1600 | 90 | 77 | 115 | 49.3 | 0.767 | 21.88 | 37.8 | 4.3 | 28
KJ049 | 4 | 1600 | 65 | 57 | 125 | 41.3 | 0.523 | 12.5 | 21.6 | 4.7 | 28
KJ049 | 4 | 1600 | 70 | 57 | 125 | 41.3 | 0.758 | 18.11 | 31.3 | 4.7 | 28
KJ049 | 4 | 1600 | 75 | 57 | 125 | 41.3 | 0.993 | 23.73 | 41 | 4.7 | 28
KJ049 | 4 | 1600 | 80 | 57 | 125 | 41.3 | 1 | 23.9 | 41.3 | 4.7 | 28
KJ049 | 4 | 1600 | 85 | 57 | 125 | 41.3 | 1 | 23.9 | 41.3 | 4.7 | 28
KJ049 | 4 | 1600 | 90 | 57 | 125 | 41.3 | 1 | 23.9 | 41.3 | 4.7 | 28
KJ049 | 4 | 1600 | 65 | 62 | 125 | 41.5 | 0.313 | 7.52 | 13 | 4.7 | 28
KJ049 | 4 | 1600 | 70 | 62 | 125 | 41.5 | 0.54 | 12.96 | 22.4 | 4.7 | 28
KJ049 | 4 | 1600 | 75 | 62 | 125 | 41.5 | 0.766 | 18.4 | 31.8 | 4.7 | 28
KJ049 | 4 | 1600 | 80 | 62 | 125 | 41.5 | 0.993 | 23.84 | 41.2 | 4.7 | 28
KJ049 | 4 | 1600 | 85 | 62 | 125 | 41.5 | 1 | 24.02 | 41.5 | 4.7 | 28
KJ049 | 4 | 1600 | 90 | 62 | 125 | 41.5 | 1 | 24.02 | 41.5 | 4.7 | 28
KJ049 | 4 | 1600 | 70 | 67 | 125 | 41.8 | 0.325 | 7.87 | 13.6 | 4.7 | 28
KJ049 | 4 | 1600 | 75 | 67 | 125 | 41.8 | 0.541 | 13.08 | 22.6 | 4.7 | 28
KJ049 | 4 | 1600 | 80 | 67 | 125 | 41.8 | 0.758 | 18.34 | 31.7 | 4.7 | 28
KJ049 | 4 | 1600 | 85 | 67 | 125 | 41.8 | 0.892 | 21.59 | 37.3 | 4.7 | 28
KJ049 | 4 | 1600 | 90 | 67 | 125 | 41.8 | 1 | 24.19 | 41.8 | 4.7 | 28
KJ049 | 4 | 1600 | 75 | 72 | 125 | 43.4 | 0.309 | 7.75 | 13.4 | 4.8 | 28
KJ049 | 4 | 1600 | 80 | 72 | 125 | 43.4 | 0.509 | 12.79 | 22.1 | 4.8 | 28
KJ049 | 4 | 1600 | 85 | 72 | 125 | 43.4 | 0.712 | 17.88 | 30.9 | 4.8 | 28
KJ049 | 4 | 1600 | 90 | 72 | 125 | 43.4 | 0.912 | 22.92 | 39.6 | 4.8 | 28
KJ049 | 4 | 1600 | 80 | 77 | 125 | 44.9 | 0.281 | 7.29 | 12.6 | 4.8 | 28
KJ049 | 4 | 1600 | 85 | 77 | 125 | 44.9 | 0.543 | 14.12 | 24.4 | 4.8 | 28
KJ049 | 4 | 1600 | 90 | 77 | 125 | 44.9 | 0.808 | 21.01 | 36.3 | 4.8 | 28
KJ049 | 4 | 1800 | 65 | 57 | 75 | 56.1 | 0.578 | 16.67 | 32.4 | 2.5 | 27
KJ049 | 4 | 1800 | 70 | 57 | 75 | 56.1 | 0.752 | 21.71 | 42.2 | 2.5 | 27
KJ049 | 4 | 1800 | 75 | 57 | 75 | 56.1 | 0.927 | 26.75 | 52 | 2.5 | 27
KJ049 | 4 | 1800 | 80 | 57 | 75 | 56.1 | 1 | 28.86 | 56.1 | 2.5 | 27
KJ049 | 4 | 1800 | 85 | 57 | 75 | 56.1 | 1 | 28.86 | 56.1 | 2.5 | 27
KJ049 | 4 | 1800 | 90 | 57 | 75 | 56.1 | 1 | 28.86 | 56.1 | 2.5 | 27
KJ049 | 4 | 1800 | 65 | 62 | 75 | 57.4 | 0.404 | 11.93 | 23.2 | 2.5 | 27
KJ049 | 4 | 1800 | 70 | 62 | 75 | 57.4 | 0.573 | 16.92 | 32.9 | 2.5 | 27
KJ049 | 4 | 1800 | 75 | 62 | 75 | 57.4 | 0.74 | 21.86 | 42.5 | 2.5 | 27
KJ049 | 4 | 1800 | 80 | 62 | 75 | 57.4 | 0.913 | 26.95 | 52.4 | 2.5 | 27
KJ049 | 4 | 1800 | 85 | 62 | 75 | 57.4 | 0.974 | 28.76 | 55.9 | 2.5 | 27
KJ049 | 4 | 1800 | 90 | 62 | 75 | 57.4 | 1 | 29.53 | 57.4 | 2.5 | 27
KJ049 | 4 | 1800 | 70 | 67 | 75 | 58.8 | 0.401 | 12.14 | 23.6 | 2.5 | 27
KJ049 | 4 | 1800 | 75 | 67 | 75 | 58.8 | 0.566 | 17.13 | 33.3 | 2.5 | 27
KJ049 | 4 | 1800 | 80 | 67 | 75 | 58.8 | 0.73 | 22.07 | 42.9 | 2.5 | 27
KJ049 | 4 | 1800 | 85 | 67 | 75 | 58.8 | 0.859 | 25.98 | 50.5 | 2.5 | 27
KJ049 | 4 | 1800 | 90 | 67 | 75 | 58.8 | 0.988 | 29.89 | 58.1 | 2.5 | 27
KJ049 | 4 | 1800 | 75 | 72 | 75 | 62.7 | 0.381 | 12.29 | 23.9 | 2.5 | 27
KJ049 | 4 | 1800 | 80 | 72 | 75 | 62.7 | 0.533 | 17.18 | 33.4 | 2.5 | 27
KJ049 | 4 | 1800 | 85 | 72 | 75 | 62.7 | 0.684 | 22.07 | 42.9 | 2.5 | 27
KJ049 | 4 | 1800 | 90 | 72 | 75 | 62.7 | 0.836 | 26.95 | 52.4 | 2.5 | 27
KJ049 | 4 | 1800 | 65 | 57 | 85 | 53.6 | 0.575 | 15.84 | 30.8 | 2.8 | 27
KJ049 | 4 | 1800 | 70 | 57 | 85 | 53.6 | 0.759 | 20.94 | 40.7 | 2.8 | 27
KJ049 | 4 | 1800 | 75 | 57 | 85 | 53.6 | 0.942 | 25.98 | 50.5 | 2.8 | 27
KJ049 | 4 | 1800 | 80 | 57 | 85 | 53.6 | 1 | 27.57 | 53.6 | 2.8 | 27
KJ049 | 4 | 1800 | 85 | 57 | 85 | 53.6 | 1 | 27.57 | 53.6 | 2.8 | 27
KJ049 | 4 | 1800 | 90 | 57 | 85 | 53.6 | 1 | 27.57 | 53.6 | 2.8 | 27
KJ049 | 4 | 1800 | 65 | 62 | 85 | 54.9 | 0.392 | 11.06 | 21.5 | 2.8 | 27
KJ049 | 4 | 1800 | 70 | 62 | 85 | 54.9 | 0.57 | 16.1 | 31.3 | 2.8 | 27
KJ049 | 4 | 1800 | 75 | 62 | 85 | 54.9 | 0.747 | 21.09 | 41 | 2.8 | 27
KJ049 | 4 | 1800 | 80 | 62 | 85 | 54.9 | 0.927 | 26.18 | 50.9 | 2.8 | 27
KJ049 | 4 | 1800 | 85 | 62 | 85 | 54.9 | 0.984 | 27.78 | 54 | 2.8 | 27
KJ049 | 4 | 1800 | 90 | 62 | 85 | 54.9 | 1 | 28.24 | 54.9 | 2.8 | 27
KJ049 | 4 | 1800 | 70 | 67 | 85 | 56.2 | 0.39 | 11.27 | 21.9 | 2.8 | 27
KJ049 | 4 | 1800 | 75 | 67 | 85 | 56.2 | 0.562 | 16.26 | 31.6 | 2.8 | 27
KJ049 | 4 | 1800 | 80 | 67 | 85 | 56.2 | 0.735 | 21.24 | 41.3 | 2.8 | 27
KJ049 | 4 | 1800 | 85 | 67 | 85 | 56.2 | 0.861 | 24.9 | 48.4 | 2.8 | 27
KJ049 | 4 | 1800 | 90 | 67 | 85 | 56.2 | 0.989 | 28.6 | 55.6 | 2.8 | 27
KJ049 | 4 | 1800 | 75 | 72 | 85 | 59.5 | 0.373 | 11.42 | 22.2 | 2.8 | 27
KJ049 | 4 | 1800 | 80 | 72 | 85 | 59.5 | 0.533 | 16.31 | 31.7 | 2.8 | 27
KJ049 | 4 | 1800 | 85 | 72 | 85 | 59.5 | 0.694 | 21.24 | 41.3 | 2.8 | 27
KJ049 | 4 | 1800 | 90 | 72 | 85 | 59.5 | 0.855 | 26.18 | 50.9 | 2.8 | 27
KJ049 | 4 | 1800 | 65 | 57 | 95 | 51.1 | 0.571 | 15.02 | 29.2 | 3.2 | 27
KJ049 | 4 | 1800 | 70 | 57 | 95 | 51.1 | 0.765 | 20.11 | 39.1 | 3.2 | 27
KJ049 | 4 | 1800 | 75 | 57 | 95 | 51.1 | 0.959 | 25.21 | 49 | 3.2 | 27
KJ049 | 4 | 1800 | 80 | 57 | 95 | 51.1 | 1 | 26.29 | 51.1 | 3.2 | 27
KJ049 | 4 | 1800 | 85 | 57 | 95 | 51.1 | 1 | 26.29 | 51.1 | 3.2 | 27
KJ049 | 4 | 1800 | 90 | 57 | 95 | 51.1 | 1 | 26.29 | 51.1 | 3.2 | 27
KJ049 | 4 | 1800 | 65 | 62 | 95 | 52.4 | 0.378 | 10.19 | 19.8 | 3.2 | 27
KJ049 | 4 | 1800 | 70 | 62 | 95 | 52.4 | 0.567 | 15.28 | 29.7 | 3.2 | 27
KJ049 | 4 | 1800 | 75 | 62 | 95 | 52.4 | 0.754 | 20.32 | 39.5 | 3.2 | 27
KJ049 | 4 | 1800 | 80 | 62 | 95 | 52.4 | 0.941 | 25.36 | 49.3 | 3.2 | 27
KJ049 | 4 | 1800 | 85 | 62 | 95 | 52.4 | 0.994 | 26.8 | 52.1 | 3.2 | 27
KJ049 | 4 | 1800 | 90 | 62 | 95 | 52.4 | 1 | 26.95 | 52.4 | 3.2 | 27
KJ049 | 4 | 1800 | 70 | 67 | 95 | 53.7 | 0.376 | 10.39 | 20.2 | 3.2 | 27
KJ049 | 4 | 1800 | 75 | 67 | 95 | 53.7 | 0.559 | 15.43 | 30 | 3.2 | 27
KJ049 | 4 | 1800 | 80 | 67 | 95 | 53.7 | 0.739 | 20.42 | 39.7 | 3.2 | 27
KJ049 | 4 | 1800 | 85 | 67 | 95 | 53.7 | 0.862 | 23.82 | 46.3 | 3.2 | 27
KJ049 | 4 | 1800 | 90 | 67 | 95 | 53.7 | 0.987 | 27.26 | 53 | 3.2 | 27
KJ049 | 4 | 1800 | 75 | 72 | 95 | 56.4 | 0.362 | 10.49 | 20.4 | 3.2 | 27
KJ049 | 4 | 1800 | 80 | 72 | 95 | 56.4 | 0.534 | 15.48 | 30.1 | 3.2 | 27
KJ049 | 4 | 1800 | 85 | 72 | 95 | 56.4 | 0.704 | 20.42 | 39.7 | 3.2 | 27
KJ049 | 4 | 1800 | 90 | 72 | 95 | 56.4 | 0.874 | 25.36 | 49.3 | 3.2 | 27
KJ049 | 4 | 1800 | 65 | 57 | 105 | 48.6 | 0.562 | 14.04 | 27.3 | 3.7 | 27
KJ049 | 4 | 1800 | 70 | 57 | 105 | 48.6 | 0.776 | 19.39 | 37.7 | 3.7 | 27
KJ049 | 4 | 1800 | 75 | 57 | 105 | 48.6 | 0.988 | 24.69 | 48 | 3.7 | 27
KJ049 | 4 | 1800 | 80 | 57 | 105 | 48.6 | 1 | 25 | 48.6 | 3.7 | 27
KJ049 | 4 | 1800 | 85 | 57 | 105 | 48.6 | 1 | 25 | 48.6 | 3.7 | 27
KJ049 | 4 | 1800 | 90 | 57 | 105 | 48.6 | 1 | 25 | 48.6 | 3.7 | 27
KJ049 | 4 | 1800 | 65 | 62 | 105 | 49.5 | 0.358 | 9.1 | 17.7 | 3.7 | 27
KJ049 | 4 | 1800 | 70 | 62 | 105 | 49.5 | 0.564 | 14.35 | 27.9 | 3.7 | 27
KJ049 | 4 | 1800 | 75 | 62 | 105 | 49.5 | 0.768 | 19.55 | 38 | 3.7 | 27
KJ049 | 4 | 1800 | 80 | 62 | 105 | 49.5 | 0.974 | 24.79 | 48.2 | 3.7 | 27
KJ049 | 4 | 1800 | 85 | 62 | 105 | 49.5 | 1 | 25.46 | 49.5 | 3.7 | 27
KJ049 | 4 | 1800 | 90 | 62 | 105 | 49.5 | 1 | 25.46 | 49.5 | 3.7 | 27
KJ049 | 4 | 1800 | 70 | 67 | 105 | 50.5 | 0.358 | 9.31 | 18.1 | 3.7 | 27
KJ049 | 4 | 1800 | 75 | 67 | 105 | 50.5 | 0.554 | 14.4 | 28 | 3.7 | 27
KJ049 | 4 | 1800 | 80 | 67 | 105 | 50.5 | 0.752 | 19.55 | 38 | 3.7 | 27
KJ049 | 4 | 1800 | 85 | 67 | 105 | 50.5 | 0.875 | 22.74 | 44.2 | 3.7 | 27
KJ049 | 4 | 1800 | 90 | 67 | 105 | 50.5 | 0.998 | 25.93 | 50.4 | 3.7 | 27
KJ049 | 4 | 1800 | 75 | 72 | 105 | 52.5 | 0.343 | 9.26 | 18 | 3.7 | 27
KJ049 | 4 | 1800 | 80 | 72 | 105 | 52.5 | 0.53 | 14.3 | 27.8 | 3.7 | 27
KJ049 | 4 | 1800 | 85 | 72 | 105 | 52.5 | 0.714 | 19.29 | 37.5 | 3.7 | 27
KJ049 | 4 | 1800 | 90 | 72 | 105 | 52.5 | 0.901 | 24.33 | 47.3 | 3.7 | 27
KJ049 | 4 | 1800 | 65 | 57 | 115 | 46.1 | 0.553 | 13.12 | 25.5 | 4.2 | 28
KJ049 | 4 | 1800 | 70 | 57 | 115 | 46.1 | 0.785 | 18.62 | 36.2 | 4.2 | 28
KJ049 | 4 | 1800 | 75 | 57 | 115 | 46.1 | 1 | 23.71 | 46.1 | 4.2 | 28
KJ049 | 4 | 1800 | 80 | 57 | 115 | 46.1 | 1 | 23.71 | 46.1 | 4.2 | 28
KJ049 | 4 | 1800 | 85 | 57 | 115 | 46.1 | 1 | 23.71 | 46.1 | 4.2 | 28
KJ049 | 4 | 1800 | 90 | 57 | 115 | 46.1 | 1 | 23.71 | 46.1 | 4.2 | 28
KJ049 | 4 | 1800 | 65 | 62 | 115 | 46.6 | 0.335 | 8.02 | 15.6 | 4.2 | 28
KJ049 | 4 | 1800 | 70 | 62 | 115 | 46.6 | 0.56 | 13.43 | 26.1 | 4.2 | 28
KJ049 | 4 | 1800 | 75 | 62 | 115 | 46.6 | 0.783 | 18.78 | 36.5 | 4.2 | 28
KJ049 | 4 | 1800 | 80 | 62 | 115 | 46.6 | 1 | 23.97 | 46.6 | 4.2 | 28
KJ049 | 4 | 1800 | 85 | 62 | 115 | 46.6 | 1 | 23.97 | 46.6 | 4.2 | 28
KJ049 | 4 | 1800 | 90 | 62 | 115 | 46.6 | 1 | 23.97 | 46.6 | 4.2 | 28
KJ049 | 4 | 1800 | 70 | 67 | 115 | 47.2 | 0.337 | 8.18 | 15.9 | 4.2 | 28
KJ049 | 4 | 1800 | 75 | 67 | 115 | 47.2 | 0.553 | 13.43 | 26.1 | 4.2 | 28
KJ049 | 4 | 1800 | 80 | 67 | 115 | 47.2 | 0.767 | 18.62 | 36.2 | 4.2 | 28
KJ049 | 4 | 1800 | 85 | 67 | 115 | 47.2 | 0.89 | 21.6 | 42 | 4.2 | 28
KJ049 | 4 | 1800 | 90 | 67 | 115 | 47.2 | 1 | 24.28 | 47.2 | 4.2 | 28
KJ049 | 4 | 1800 | 75 | 72 | 115 | 48.7 | 0.322 | 8.08 | 15.7 | 4.2 | 28
KJ049 | 4 | 1800 | 80 | 72 | 115 | 48.7 | 0.524 | 13.12 | 25.5 | 4.2 | 28
KJ049 | 4 | 1800 | 85 | 72 | 115 | 48.7 | 0.727 | 18.21 | 35.4 | 4.2 | 28
KJ049 | 4 | 1800 | 90 | 72 | 115 | 48.7 | 0.928 | 23.25 | 45.2 | 4.2 | 28
KJ049 | 4 | 1800 | 65 | 57 | 125 | 43.6 | 0.541 | 12.14 | 23.6 | 4.7 | 28
KJ049 | 4 | 1800 | 70 | 57 | 125 | 43.6 | 0.798 | 17.9 | 34.8 | 4.7 | 28
KJ049 | 4 | 1800 | 75 | 57 | 125 | 43.6 | 1 | 22.43 | 43.6 | 4.7 | 28
KJ049 | 4 | 1800 | 80 | 57 | 125 | 43.6 | 1 | 22.43 | 43.6 | 4.7 | 28
KJ049 | 4 | 1800 | 85 | 57 | 125 | 43.6 | 1 | 22.43 | 43.6 | 4.7 | 28
KJ049 | 4 | 1800 | 90 | 57 | 125 | 43.6 | 1 | 22.43 | 43.6 | 4.7 | 28
KJ049 | 4 | 1800 | 65 | 62 | 125 | 43.7 | 0.309 | 6.94 | 13.5 | 4.7 | 28
KJ049 | 4 | 1800 | 70 | 62 | 125 | 43.7 | 0.556 | 12.5 | 24.3 | 4.7 | 28
KJ049 | 4 | 1800 | 75 | 62 | 125 | 43.7 | 0.801 | 18 | 35 | 4.7 | 28
KJ049 | 4 | 1800 | 80 | 62 | 125 | 43.7 | 1 | 22.48 | 43.7 | 4.7 | 28
KJ049 | 4 | 1800 | 85 | 62 | 125 | 43.7 | 1 | 22.48 | 43.7 | 4.7 | 28
KJ049 | 4 | 1800 | 90 | 62 | 125 | 43.7 | 1 | 22.48 | 43.7 | 4.7 | 28
KJ049 | 4 | 1800 | 70 | 67 | 125 | 43.9 | 0.314 | 7.1 | 13.8 | 4.7 | 28
KJ049 | 4 | 1800 | 75 | 67 | 125 | 43.9 | 0.551 | 12.45 | 24.2 | 4.7 | 28
KJ049 | 4 | 1800 | 80 | 67 | 125 | 43.9 | 0.786 | 17.75 | 34.5 | 4.7 | 28
KJ049 | 4 | 1800 | 85 | 67 | 125 | 43.9 | 0.907 | 20.47 | 39.8 | 4.7 | 28
KJ049 | 4 | 1800 | 90 | 67 | 125 | 43.9 | 1 | 22.58 | 43.9 | 4.7 | 28
KJ049 | 4 | 1800 | 75 | 72 | 125 | 44.9 | 0.296 | 6.84 | 13.3 | 4.8 | 28
KJ049 | 4 | 1800 | 80 | 72 | 125 | 44.9 | 0.517 | 11.93 | 23.2 | 4.8 | 28
KJ049 | 4 | 1800 | 85 | 72 | 125 | 44.9 | 0.739 | 17.08 | 33.2 | 4.8 | 28
KJ049 | 4 | 1800 | 90 | 72 | 125 | 44.9 | 0.962 | 22.22 | 43.2 | 4.8 | 28
KJ049 | 4 | 2000 | 65 | 57 | 75 | 59.6 | 0.572 | 15.79 | 34.1 | 2.5 | 27
KJ049 | 4 | 2000 | 70 | 57 | 75 | 59.6 | 0.755 | 20.83 | 45 | 2.5 | 27
KJ049 | 4 | 2000 | 75 | 57 | 75 | 59.6 | 0.936 | 25.83 | 55.8 | 2.5 | 27
KJ049 | 4 | 2000 | 80 | 57 | 75 | 59.6 | 1 | 27.59 | 59.6 | 2.5 | 27
KJ049 | 4 | 2000 | 85 | 57 | 75 | 59.6 | 1 | 27.59 | 59.6 | 2.5 | 27
KJ049 | 4 | 2000 | 90 | 57 | 75 | 59.6 | 1 | 27.59 | 59.6 | 2.5 | 27
KJ049 | 4 | 2000 | 65 | 62 | 75 | 60 | 0.398 | 11.06 | 23.9 | 2.5 | 27
KJ049 | 4 | 2000 | 70 | 62 | 75 | 60 | 0.578 | 16.06 | 34.7 | 2.5 | 27
KJ049 | 4 | 2000 | 75 | 62 | 75 | 60 | 0.757 | 21.02 | 45.4 | 2.5 | 27
KJ049 | 4 | 2000 | 80 | 62 | 75 | 60 | 0.937 | 26.02 | 56.2 | 2.5 | 27
KJ049 | 4 | 2000 | 85 | 62 | 75 | 60 | 0.983 | 27.31 | 59 | 2.5 | 27
KJ049 | 4 | 2000 | 90 | 62 | 75 | 60 | 1 | 27.78 | 60 | 2.5 | 27
KJ049 | 4 | 2000 | 70 | 67 | 75 | 60.5 | 0.403 | 11.3 | 24.4 | 2.5 | 27
KJ049 | 4 | 2000 | 75 | 67 | 75 | 60.5 | 0.579 | 16.2 | 35 | 2.5 | 27
KJ049 | 4 | 2000 | 80 | 67 | 75 | 60.5 | 0.755 | 21.16 | 45.7 | 2.5 | 27
KJ049 | 4 | 2000 | 85 | 67 | 75 | 60.5 | 0.888 | 24.86 | 53.7 | 2.5 | 27
KJ049 | 4 | 2000 | 90 | 67 | 75 | 60.5 | 1 | 28.01 | 60.5 | 2.5 | 27
KJ049 | 4 | 2000 | 75 | 72 | 75 | 64 | 0.384 | 11.39 | 24.6 | 2.5 | 27
KJ049 | 4 | 2000 | 80 | 72 | 75 | 64 | 0.55 | 16.3 | 35.2 | 2.5 | 27
KJ049 | 4 | 2000 | 85 | 72 | 75 | 64 | 0.716 | 21.2 | 45.8 | 2.5 | 27
KJ049 | 4 | 2000 | 90 | 72 | 75 | 64 | 0.881 | 26.11 | 56.4 | 2.5 | 27
KJ049 | 4 | 2000 | 65 | 57 | 85 | 57.3 | 0.567 | 15.05 | 32.5 | 2.8 | 27
KJ049 | 4 | 2000 | 70 | 57 | 85 | 57.3 | 0.757 | 20.09 | 43.4 | 2.8 | 27
KJ049 | 4 | 2000 | 75 | 57 | 85 | 57.3 | 0.948 | 25.14 | 54.3 | 2.8 | 27
KJ049 | 4 | 2000 | 80 | 57 | 85 | 57.3 | 1 | 26.53 | 57.3 | 2.8 | 27
KJ049 | 4 | 2000 | 85 | 57 | 85 | 57.3 | 1 | 26.53 | 57.3 | 2.8 | 27
KJ049 | 4 | 2000 | 90 | 57 | 85 | 57.3 | 1 | 26.53 | 57.3 | 2.8 | 27
KJ049 | 4 | 2000 | 65 | 62 | 85 | 57.8 | 0.384 | 10.28 | 22.2 | 2.8 | 27
KJ049 | 4 | 2000 | 70 | 62 | 85 | 57.8 | 0.571 | 15.28 | 33 | 2.8 | 27
KJ049 | 4 | 2000 | 75 | 62 | 85 | 57.8 | 0.76 | 20.32 | 43.9 | 2.8 | 27
KJ049 | 4 | 2000 | 80 | 62 | 85 | 57.8 | 0.946 | 25.32 | 54.7 | 2.8 | 27
KJ049 | 4 | 2000 | 85 | 62 | 85 | 57.8 | 0.984 | 26.34 | 56.9 | 2.8 | 27
KJ049 | 4 | 2000 | 90 | 62 | 85 | 57.8 | 1 | 26.76 | 57.8 | 2.8 | 27
KJ049 | 4 | 2000 | 70 | 67 | 85 | 58.3 | 0.388 | 10.46 | 22.6 | 2.8 | 27
KJ049 | 4 | 2000 | 75 | 67 | 85 | 58.3 | 0.573 | 15.46 | 33.4 | 2.8 | 27
KJ049 | 4 | 2000 | 80 | 67 | 85 | 58.3 | 0.756 | 20.42 | 44.1 | 2.8 | 27
KJ049 | 4 | 2000 | 85 | 67 | 85 | 58.3 | 0.883 | 23.84 | 51.5 | 2.8 | 27
KJ049 | 4 | 2000 | 90 | 67 | 85 | 58.3 | 1 | 26.99 | 58.3 | 2.8 | 27
KJ049 | 4 | 2000 | 75 | 72 | 85 | 61 | 0.375 | 10.6 | 22.9 | 2.8 | 27
KJ049 | 4 | 2000 | 80 | 72 | 85 | 61 | 0.549 | 15.51 | 33.5 | 2.8 | 27
KJ049 | 4 | 2000 | 85 | 72 | 85 | 61 | 0.725 | 20.46 | 44.2 | 2.8 | 27
KJ049 | 4 | 2000 | 90 | 72 | 85 | 61 | 0.898 | 25.37 | 54.8 | 2.8 | 27
KJ049 | 4 | 2000 | 65 | 57 | 95 | 55 | 0.56 | 14.26 | 30.8 | 3.2 | 27
KJ049 | 4 | 2000 | 70 | 57 | 95 | 55 | 0.76 | 19.35 | 41.8 | 3.2 | 27
KJ049 | 4 | 2000 | 75 | 57 | 95 | 55 | 0.962 | 24.49 | 52.9 | 3.2 | 27
KJ049 | 4 | 2000 | 80 | 57 | 95 | 55 | 1 | 25.46 | 55 | 3.2 | 27
KJ049 | 4 | 2000 | 85 | 57 | 95 | 55 | 1 | 25.46 | 55 | 3.2 | 27
KJ049 | 4 | 2000 | 90 | 57 | 95 | 55 | 1 | 25.46 | 55 | 3.2 | 27
KJ049 | 4 | 2000 | 70 | 67 | 95 | 56.1 | 0.373 | 9.68 | 20.9 | 3.2 | 27
KJ049 | 4 | 2000 | 75 | 67 | 95 | 56.1 | 0.565 | 14.68 | 31.7 | 3.2 | 27
KJ049 | 4 | 2000 | 80 | 67 | 95 | 56.1 | 0.758 | 19.68 | 42.5 | 3.2 | 27
KJ049 | 4 | 2000 | 85 | 67 | 95 | 56.1 | 0.879 | 22.82 | 49.3 | 3.2 | 27
KJ049 | 4 | 2000 | 90 | 67 | 95 | 56.1 | 0.998 | 25.93 | 56 | 3.2 | 27
KJ049 | 4 | 2000 | 75 | 72 | 95 | 58 | 0.364 | 9.77 | 21.1 | 3.2 | 27
KJ049 | 4 | 2000 | 80 | 72 | 95 | 58 | 0.548 | 14.72 | 31.8 | 3.2 | 27
KJ049 | 4 | 2000 | 85 | 72 | 95 | 58 | 0.733 | 19.68 | 42.5 | 3.2 | 27
KJ049 | 4 | 2000 | 90 | 72 | 95 | 58 | 0.917 | 24.63 | 53.2 | 3.2 | 27
KJ049 | 4 | 2000 | 65 | 57 | 105 | 52 | 0.56 | 13.47 | 29.1 | 3.7 | 27
KJ049 | 4 | 2000 | 70 | 57 | 105 | 52 | 0.783 | 18.84 | 40.7 | 3.7 | 27
KJ049 | 4 | 2000 | 75 | 57 | 105 | 52 | 1 | 24.07 | 52 | 3.7 | 27
KJ049 | 4 | 2000 | 80 | 57 | 105 | 52 | 1 | 24.07 | 52 | 3.7 | 27
KJ049 | 4 | 2000 | 85 | 57 | 105 | 52 | 1 | 24.07 | 52 | 3.7 | 27
KJ049 | 4 | 2000 | 90 | 57 | 105 | 52 | 1 | 24.07 | 52 | 3.7 | 27
KJ049 | 4 | 2000 | 70 | 67 | 105 | 52.7 | 0.353 | 8.61 | 18.6 | 3.7 | 27
KJ049 | 4 | 2000 | 75 | 67 | 105 | 52.7 | 0.564 | 13.75 | 29.7 | 3.7 | 27
KJ049 | 4 | 2000 | 80 | 67 | 105 | 52.7 | 0.774 | 18.89 | 40.8 | 3.7 | 27
KJ049 | 4 | 2000 | 85 | 67 | 105 | 52.7 | 0.892 | 21.76 | 47 | 3.7 | 27
KJ049 | 4 | 2000 | 90 | 67 | 105 | 52.7 | 1 | 24.4 | 52.7 | 3.7 | 27
KJ049 | 4 | 2000 | 75 | 72 | 105 | 54.1 | 0.342 | 8.56 | 18.5 | 3.7 | 27
KJ049 | 4 | 2000 | 80 | 72 | 105 | 54.1 | 0.542 | 13.56 | 29.3 | 3.7 | 27
KJ049 | 4 | 2000 | 85 | 72 | 105 | 54.1 | 0.743 | 18.61 | 40.2 | 3.7 | 27
KJ049 | 4 | 2000 | 90 | 72 | 105 | 54.1 | 0.945 | 23.66 | 51.1 | 3.7 | 27
KJ049 | 4 | 2000 | 65 | 57 | 115 | 48.9 | 0.56 | 12.69 | 27.4 | 4.2 | 28
KJ049 | 4 | 2000 | 70 | 57 | 115 | 48.9 | 0.808 | 18.29 | 39.5 | 4.2 | 28
KJ049 | 4 | 2000 | 75 | 57 | 115 | 48.9 | 1 | 22.64 | 48.9 | 4.2 | 28
KJ049 | 4 | 2000 | 80 | 57 | 115 | 48.9 | 1 | 22.64 | 48.9 | 4.2 | 28
KJ049 | 4 | 2000 | 85 | 57 | 115 | 48.9 | 1 | 22.64 | 48.9 | 4.2 | 28
KJ049 | 4 | 2000 | 90 | 57 | 115 | 48.9 | 1 | 22.64 | 48.9 | 4.2 | 28
KJ049 | 4 | 2000 | 65 | 62 | 115 | 49.1 | 0.33 | 7.5 | 16.2 | 4.2 | 28
KJ049 | 4 | 2000 | 70 | 62 | 115 | 49.1 | 0.568 | 12.92 | 27.9 | 4.2 | 28
KJ049 | 4 | 2000 | 75 | 62 | 115 | 49.1 | 0.807 | 18.33 | 39.6 | 4.2 | 28
KJ049 | 4 | 2000 | 80 | 62 | 115 | 49.1 | 1 | 22.73 | 49.1 | 4.2 | 28
KJ049 | 4 | 2000 | 85 | 62 | 115 | 49.1 | 1 | 22.73 | 49.1 | 4.2 | 28
KJ049 | 4 | 2000 | 90 | 62 | 115 | 49.1 | 1 | 22.73 | 49.1 | 4.2 | 28
KJ049 | 4 | 2000 | 70 | 67 | 115 | 49.3 | 0.331 | 7.55 | 16.3 | 4.2 | 28
KJ049 | 4 | 2000 | 75 | 67 | 115 | 49.3 | 0.562 | 12.82 | 27.7 | 4.2 | 28
KJ049 | 4 | 2000 | 80 | 67 | 115 | 49.3 | 0.793 | 18.1 | 39.1 | 4.2 | 28
KJ049 | 4 | 2000 | 85 | 67 | 115 | 49.3 | 0.907 | 20.69 | 44.7 | 4.2 | 28
KJ049 | 4 | 2000 | 90 | 67 | 115 | 49.3 | 1 | 22.82 | 49.3 | 4.2 | 28
KJ049 | 4 | 2000 | 75 | 72 | 115 | 50.3 | 0.314 | 7.31 | 15.8 | 4.2 | 28
KJ049 | 4 | 2000 | 80 | 72 | 115 | 50.3 | 0.533 | 12.41 | 26.8 | 4.2 | 28
KJ049 | 4 | 2000 | 85 | 72 | 115 | 50.3 | 0.753 | 17.55 | 37.9 | 4.2 | 28
KJ049 | 4 | 2000 | 90 | 72 | 115 | 50.3 | 0.972 | 22.64 | 48.9 | 4.2 | 28
KJ049 | 4 | 2000 | 65 | 57 | 125 | 45.9 | 0.56 | 11.9 | 25.7 | 4.7 | 28
KJ049 | 4 | 2000 | 70 | 57 | 125 | 45.9 | 0.834 | 17.73 | 38.3 | 4.7 | 28
KJ049 | 4 | 2000 | 75 | 57 | 125 | 45.9 | 1 | 21.25 | 45.9 | 4.7 | 28
KJ049 | 4 | 2000 | 80 | 57 | 125 | 45.9 | 1 | 21.25 | 45.9 | 4.7 | 28
KJ049 | 4 | 2000 | 85 | 57 | 125 | 45.9 | 1 | 21.25 | 45.9 | 4.7 | 28
KJ049 | 4 | 2000 | 90 | 57 | 125 | 45.9 | 1 | 21.25 | 45.9 | 4.7 | 28
KJ049 | 4 | 2000 | 65 | 62 | 125 | 45.9 | 0.305 | 6.48 | 14 | 4.7 | 28
KJ049 | 4 | 2000 | 70 | 62 | 125 | 45.9 | 0.569 | 12.08 | 26.1 | 4.7 | 28
KJ049 | 4 | 2000 | 75 | 62 | 125 | 45.9 | 0.834 | 17.73 | 38.3 | 4.7 | 28
KJ049 | 4 | 2000 | 80 | 62 | 125 | 45.9 | 1 | 21.25 | 45.9 | 4.7 | 28
KJ049 | 4 | 2000 | 85 | 62 | 125 | 45.9 | 1 | 21.25 | 45.9 | 4.7 | 28
KJ049 | 4 | 2000 | 90 | 62 | 125 | 45.9 | 1 | 21.25 | 45.9 | 4.7 | 28
KJ049 | 4 | 2000 | 70 | 67 | 125 | 46 | 0.304 | 6.48 | 14 | 4.8 | 28
KJ049 | 4 | 2000 | 75 | 67 | 125 | 46 | 0.559 | 11.9 | 25.7 | 4.8 | 28
KJ049 | 4 | 2000 | 80 | 67 | 125 | 46 | 0.813 | 17.31 | 37.4 | 4.8 | 28
KJ049 | 4 | 2000 | 85 | 67 | 125 | 46 | 0.92 | 19.58 | 42.3 | 4.8 | 28
KJ049 | 4 | 2000 | 90 | 67 | 125 | 46 | 1 | 21.3 | 46 | 4.8 | 28
KJ049 | 4 | 2000 | 75 | 72 | 125 | 46.4 | 0.282 | 6.06 | 13.1 | 4.8 | 28
KJ049 | 4 | 2000 | 80 | 72 | 125 | 46.4 | 0.524 | 11.25 | 24.3 | 4.8 | 28
KJ049 | 4 | 2000 | 85 | 72 | 125 | 46.4 | 0.767 | 16.48 | 35.6 | 4.8 | 28
KJ049 | 4 | 2000 | 90 | 72 | 125 | 46.4 | 1 | 21.48 | 46.4 | 4.8 | 28
KJ061 | 5 | 1250 | 65 | 62 | 75 | 60.1 | 0.434 | 19.33 | 26.1 | 3.1 | 29
KJ061 | 5 | 1250 | 70 | 62 | 75 | 60.1 | 0.554 | 24.67 | 33.3 | 3.1 | 29
KJ061 | 5 | 1250 | 75 | 62 | 75 | 60.1 | 0.654 | 29.11 | 39.3 | 3.1 | 29
KJ061 | 5 | 1250 | 80 | 62 | 75 | 60.1 | 0.795 | 35.41 | 47.8 | 3.1 | 29
KJ061 | 5 | 1250 | 85 | 62 | 75 | 60.1 | 0.917 | 40.81 | 55.1 | 3.1 | 29
KJ061 | 5 | 1250 | 90 | 62 | 75 | 60.1 | 1 | 44.52 | 60.1 | 3.1 | 29
KJ061 | 5 | 1250 | 70 | 67 | 75 | 65.4 | 0.399 | 19.33 | 26.1 | 3.1 | 29
KJ061 | 5 | 1250 | 75 | 67 | 75 | 65.4 | 0.506 | 24.52 | 33.1 | 3.1 | 29
KJ061 | 5 | 1250 | 80 | 67 | 75 | 65.4 | 0.616 | 29.85 | 40.3 | 3.1 | 29
KJ061 | 5 | 1250 | 85 | 67 | 75 | 65.4 | 0.732 | 35.48 | 47.9 | 3.1 | 29
KJ061 | 5 | 1250 | 90 | 67 | 75 | 65.4 | 0.85 | 41.19 | 55.6 | 3.1 | 29
KJ061 | 5 | 1250 | 75 | 72 | 75 | 72.5 | 0.357 | 19.19 | 25.9 | 3.2 | 29
KJ061 | 5 | 1250 | 80 | 72 | 75 | 72.5 | 0.452 | 24.3 | 32.8 | 3.2 | 29
KJ061 | 5 | 1250 | 85 | 72 | 75 | 72.5 | 0.549 | 29.48 | 39.8 | 3.2 | 29
KJ061 | 5 | 1250 | 90 | 72 | 75 | 72.5 | 0.644 | 34.59 | 46.7 | 3.2 | 29
KJ061 | 5 | 1250 | 80 | 77 | 75 | 79.5 | 0.318 | 18.74 | 25.3 | 3.2 | 29
KJ061 | 5 | 1250 | 85 | 77 | 75 | 79.5 | 0.397 | 23.41 | 31.6 | 3.2 | 29
KJ061 | 5 | 1250 | 90 | 77 | 75 | 79.5 | 0.475 | 28 | 37.8 | 3.2 | 29
KJ061 | 5 | 1250 | 65 | 62 | 85 | 58.4 | 0.421 | 18.22 | 24.6 | 3.5 | 29
KJ061 | 5 | 1250 | 70 | 62 | 85 | 58.4 | 0.541 | 23.41 | 31.6 | 3.5 | 29
KJ061 | 5 | 1250 | 75 | 62 | 85 | 58.4 | 0.649 | 28.07 | 37.9 | 3.5 | 29
KJ061 | 5 | 1250 | 80 | 62 | 85 | 58.4 | 0.781 | 33.78 | 45.6 | 3.5 | 29
KJ061 | 5 | 1250 | 85 | 62 | 85 | 58.4 | 0.902 | 39.04 | 52.7 | 3.5 | 29
KJ061 | 5 | 1250 | 90 | 62 | 85 | 58.4 | 1 | 43.26 | 58.4 | 3.5 | 29
KJ061 | 5 | 1250 | 70 | 67 | 85 | 62.1 | 0.398 | 18.3 | 24.7 | 3.6 | 29
KJ061 | 5 | 1250 | 75 | 67 | 85 | 62.1 | 0.509 | 23.41 | 31.6 | 3.6 | 29
KJ061 | 5 | 1250 | 80 | 67 | 85 | 62.1 | 0.622 | 28.59 | 38.6 | 3.6 | 29
KJ061 | 5 | 1250 | 85 | 67 | 85 | 62.1 | 0.75 | 34.52 | 46.6 | 3.6 | 29
KJ061 | 5 | 1250 | 90 | 67 | 85 | 62.1 | 0.878 | 40.37 | 54.5 | 3.6 | 29
KJ061 | 5 | 1250 | 75 | 72 | 85 | 69.2 | 0.358 | 18.37 | 24.8 | 3.6 | 29
KJ061 | 5 | 1250 | 80 | 72 | 85 | 69.2 | 0.458 | 23.48 | 31.7 | 3.6 | 29
KJ061 | 5 | 1250 | 85 | 72 | 85 | 69.2 | 0.558 | 28.59 | 38.6 | 3.6 | 29
KJ061 | 5 | 1250 | 90 | 72 | 85 | 69.2 | 0.658 | 33.7 | 45.5 | 3.6 | 29
KJ061 | 5 | 1250 | 80 | 77 | 85 | 76.4 | 0.325 | 18.37 | 24.8 | 3.6 | 29
KJ061 | 5 | 1250 | 85 | 77 | 85 | 76.4 | 0.402 | 22.74 | 30.7 | 3.6 | 29
KJ061 | 5 | 1250 | 90 | 77 | 85 | 76.4 | 0.479 | 27.11 | 36.6 | 3.6 | 29
KJ061 | 5 | 1250 | 65 | 62 | 95 | 56.7 | 0.407 | 17.11 | 23.1 | 3.9 | 29
KJ061 | 5 | 1250 | 70 | 62 | 95 | 56.7 | 0.526 | 22.07 | 29.8 | 3.9 | 29
KJ061 | 5 | 1250 | 75 | 62 | 95 | 56.7 | 0.646 | 27.11 | 36.6 | 3.9 | 29
KJ061 | 5 | 1250 | 80 | 62 | 95 | 56.7 | 0.764 | 32.07 | 43.3 | 3.9 | 29
KJ061 | 5 | 1250 | 85 | 62 | 95 | 56.7 | 0.887 | 37.26 | 50.3 | 3.9 | 29
KJ061 | 5 | 1250 | 90 | 62 | 95 | 56.7 | 1 | 42 | 56.7 | 3.9 | 29
KJ061 | 5 | 1250 | 70 | 67 | 95 | 58.8 | 0.396 | 17.26 | 23.3 | 4 | 29
KJ061 | 5 | 1250 | 75 | 67 | 95 | 58.8 | 0.512 | 22.3 | 30.1 | 4 | 29
KJ061 | 5 | 1250 | 80 | 67 | 95 | 58.8 | 0.628 | 27.33 | 36.9 | 4 | 29
KJ061 | 5 | 1250 | 85 | 67 | 95 | 58.8 | 0.769 | 33.48 | 45.2 | 4 | 29
KJ061 | 5 | 1250 | 90 | 67 | 95 | 58.8 | 0.908 | 39.56 | 53.4 | 4 | 29
KJ061 | 5 | 1250 | 75 | 72 | 95 | 66 | 0.359 | 17.56 | 23.7 | 4 | 29
KJ061 | 5 | 1250 | 80 | 72 | 95 | 66 | 0.464 | 22.67 | 30.6 | 4 | 29
KJ061 | 5 | 1250 | 85 | 72 | 95 | 66 | 0.568 | 27.78 | 37.5 | 4 | 29
KJ061 | 5 | 1250 | 90 | 72 | 95 | 66 | 0.671 | 32.81 | 44.3 | 4 | 29
KJ061 | 5 | 1250 | 80 | 77 | 95 | 73.2 | 0.331 | 17.93 | 24.2 | 4 | 29
KJ061 | 5 | 1250 | 85 | 77 | 95 | 73.2 | 0.406 | 22 | 29.7 | 4 | 29
KJ061 | 5 | 1250 | 90 | 77 | 95 | 73.2 | 0.482 | 26.15 | 35.3 | 4 | 29
KJ061 | 5 | 1250 | 65 | 62 | 105 | 54.1 | 0.39 | 15.63 | 21.1 | 4.5 | 29
KJ061 | 5 | 1250 | 70 | 62 | 105 | 54.1 | 0.516 | 20.67 | 27.9 | 4.5 | 29
KJ061 | 5 | 1250 | 75 | 62 | 105 | 54.1 | 0.643 | 25.78 | 34.8 | 4.5 | 29
KJ061 | 5 | 1250 | 80 | 62 | 105 | 54.1 | 0.769 | 30.81 | 41.6 | 4.5 | 29
KJ061 | 5 | 1250 | 85 | 62 | 105 | 54.1 | 0.887 | 35.56 | 48 | 4.5 | 29
KJ061 | 5 | 1250 | 90 | 62 | 105 | 54.1 | 1 | 40.07 | 54.1 | 4.5 | 29
KJ061 | 5 | 1250 | 70 | 67 | 105 | 53.9 | 0.399 | 15.93 | 21.5 | 4.6 | 29
KJ061 | 5 | 1250 | 75 | 67 | 105 | 53.9 | 0.525 | 20.96 | 28.3 | 4.6 | 29
KJ061 | 5 | 1250 | 80 | 67 | 105 | 53.9 | 0.653 | 26.07 | 35.2 | 4.6 | 29
KJ061 | 5 | 1250 | 85 | 67 | 105 | 53.9 | 0.807 | 32.22 | 43.5 | 4.6 | 29
KJ061 | 5 | 1250 | 90 | 67 | 105 | 53.9 | 0.961 | 38.37 | 51.8 | 4.6 | 29
KJ061 | 5 | 1250 | 75 | 72 | 105 | 61.8 | 0.354 | 16.22 | 21.9 | 4.6 | 29
KJ061 | 5 | 1250 | 80 | 72 | 105 | 61.8 | 0.464 | 21.26 | 28.7 | 4.6 | 29
KJ061 | 5 | 1250 | 85 | 72 | 105 | 61.8 | 0.574 | 26.3 | 35.5 | 4.6 | 29
KJ061 | 5 | 1250 | 90 | 72 | 105 | 61.8 | 0.684 | 31.33 | 42.3 | 4.6 | 29
KJ061 | 5 | 1250 | 80 | 77 | 105 | 69.8 | 0.318 | 16.44 | 22.2 | 4.6 | 29
KJ061 | 5 | 1250 | 85 | 77 | 105 | 69.8 | 0.395 | 20.44 | 27.6 | 4.6 | 29
KJ061 | 5 | 1250 | 90 | 77 | 105 | 69.8 | 0.471 | 24.37 | 32.9 | 4.6 | 29
KJ061 | 5 | 1250 | 65 | 62 | 115 | 48.8 | 0.389 | 14.07 | 19 | 5.2 | 30
KJ061 | 5 | 1250 | 70 | 62 | 115 | 48.8 | 0.533 | 19.26 | 26 | 5.2 | 30
KJ061 | 5 | 1250 | 75 | 62 | 115 | 48.8 | 0.676 | 24.44 | 33 | 5.2 | 30
KJ061 | 5 | 1250 | 80 | 62 | 115 | 48.8 | 0.82 | 29.63 | 40 | 5.2 | 30
KJ061 | 5 | 1250 | 85 | 62 | 115 | 48.8 | 0.936 | 33.85 | 45.7 | 5.2 | 30
KJ061 | 5 | 1250 | 90 | 62 | 115 | 48.8 | 1 | 36.15 | 48.8 | 5.2 | 30
KJ061 | 5 | 1250 | 70 | 67 | 115 | 48.9 | 0.401 | 14.52 | 19.6 | 5.2 | 30
KJ061 | 5 | 1250 | 75 | 67 | 115 | 48.9 | 0.542 | 19.63 | 26.5 | 5.2 | 30
KJ061 | 5 | 1250 | 80 | 67 | 115 | 48.9 | 0.683 | 24.74 | 33.4 | 5.2 | 30
KJ061 | 5 | 1250 | 85 | 67 | 115 | 48.9 | 0.855 | 30.96 | 41.8 | 5.2 | 30
KJ061 | 5 | 1250 | 90 | 67 | 115 | 48.9 | 1 | 36.22 | 48.9 | 5.2 | 30
KJ061 | 5 | 1250 | 75 | 72 | 115 | 57.6 | 0.347 | 14.81 | 20 | 5.2 | 30
KJ061 | 5 | 1250 | 80 | 72 | 115 | 57.6 | 0.465 | 19.85 | 26.8 | 5.2 | 30
KJ061 | 5 | 1250 | 85 | 72 | 115 | 57.6 | 0.583 | 24.89 | 33.6 | 5.2 | 30
KJ061 | 5 | 1250 | 90 | 72 | 115 | 57.6 | 0.701 | 29.93 | 40.4 | 5.2 | 30
KJ061 | 5 | 1250 | 80 | 77 | 115 | 66.3 | 0.305 | 14.96 | 20.2 | 5.2 | 30
KJ061 | 5 | 1250 | 85 | 77 | 115 | 66.3 | 0.383 | 18.81 | 25.4 | 5.2 | 30
KJ061 | 5 | 1250 | 90 | 77 | 115 | 66.3 | 0.46 | 22.59 | 30.5 | 5.2 | 30
KJ061 | 5 | 1250 | 65 | 62 | 125 | 49 | 0.347 | 12.59 | 17 | 5.8 | 30
KJ061 | 5 | 1250 | 70 | 62 | 125 | 49 | 0.492 | 17.85 | 24.1 | 5.8 | 30
KJ061 | 5 | 1250 | 75 | 62 | 125 | 49 | 0.637 | 23.11 | 31.2 | 5.8 | 30
KJ061 | 5 | 1250 | 80 | 62 | 125 | 49 | 0.782 | 28.37 | 38.3 | 5.8 | 30
KJ061 | 5 | 1250 | 85 | 62 | 125 | 49 | 0.886 | 32.15 | 43.4 | 5.8 | 30
KJ061 | 5 | 1250 | 90 | 62 | 125 | 49 | 0.99 | 35.93 | 48.5 | 5.8 | 30
KJ061 | 5 | 1250 | 70 | 67 | 125 | 49.3 | 0.359 | 13.11 | 17.7 | 5.8 | 30
KJ061 | 5 | 1250 | 75 | 67 | 125 | 49.3 | 0.501 | 18.3 | 24.7 | 5.8 | 30
KJ061 | 5 | 1250 | 80 | 67 | 125 | 49.3 | 0.641 | 23.41 | 31.6 | 5.8 | 30
KJ061 | 5 | 1250 | 85 | 67 | 125 | 49.3 | 0.813 | 29.7 | 40.1 | 5.8 | 30
KJ061 | 5 | 1250 | 90 | 67 | 125 | 49.3 | 0.986 | 36 | 48.6 | 5.8 | 30
KJ061 | 5 | 1250 | 75 | 72 | 125 | 53.4 | 0.339 | 13.41 | 18.1 | 5.8 | 30
KJ061 | 5 | 1250 | 80 | 72 | 125 | 53.4 | 0.466 | 18.44 | 24.9 | 5.8 | 30
KJ061 | 5 | 1250 | 85 | 72 | 125 | 53.4 | 0.592 | 23.41 | 31.6 | 5.8 | 30
KJ061 | 5 | 1250 | 90 | 72 | 125 | 53.4 | 0.719 | 28.44 | 38.4 | 5.8 | 30
KJ061 | 5 | 1250 | 80 | 77 | 125 | 62.9 | 0.289 | 13.48 | 18.2 | 5.9 | 30
KJ061 | 5 | 1250 | 85 | 77 | 125 | 62.9 | 0.369 | 17.19 | 23.2 | 5.9 | 30
KJ061 | 5 | 1250 | 90 | 77 | 125 | 62.9 | 0.447 | 20.81 | 28.1 | 5.9 | 30
KJ061 | 5 | 1500 | 65 | 57 | 75 | 59.7 | 0.588 | 21.67 | 35.1 | 3.1 | 29
KJ061 | 5 | 1500 | 70 | 57 | 75 | 59.7 | 0.735 | 27.1 | 43.9 | 3.1 | 29
KJ061 | 5 | 1500 | 75 | 57 | 75 | 59.7 | 0.881 | 32.47 | 52.6 | 3.1 | 29
KJ061 | 5 | 1500 | 80 | 57 | 75 | 59.7 | 1 | 36.85 | 59.7 | 3.1 | 29
KJ061 | 5 | 1500 | 85 | 57 | 75 | 59.7 | 1 | 36.85 | 59.7 | 3.1 | 29
KJ061 | 5 | 1500 | 90 | 57 | 75 | 59.7 | 1 | 36.85 | 59.7 | 3.1 | 29
KJ061 | 5 | 1500 | 65 | 62 | 75 | 63.9 | 0.418 | 16.48 | 26.7 | 3.1 | 29
KJ061 | 5 | 1500 | 70 | 62 | 75 | 63.9 | 0.552 | 21.79 | 35.3 | 3.1 | 29
KJ061 | 5 | 1500 | 75 | 62 | 75 | 63.9 | 0.671 | 26.48 | 42.9 | 3.1 | 29
KJ061 | 5 | 1500 | 80 | 62 | 75 | 63.9 | 0.822 | 32.41 | 52.5 | 3.1 | 29
KJ061 | 5 | 1500 | 85 | 62 | 75 | 63.9 | 0.923 | 36.42 | 59 | 3.1 | 29
KJ061 | 5 | 1500 | 90 | 62 | 75 | 63.9 | 0.933 | 36.79 | 59.6 | 3.1 | 29
KJ061 | 5 | 1500 | 70 | 67 | 75 | 68.1 | 0.394 | 16.54 | 26.8 | 3.1 | 29
KJ061 | 5 | 1500 | 75 | 67 | 75 | 68.1 | 0.515 | 21.67 | 35.1 | 3.1 | 29
KJ061 | 5 | 1500 | 80 | 67 | 75 | 68.1 | 0.642 | 26.98 | 43.7 | 3.1 | 29
KJ061 | 5 | 1500 | 85 | 67 | 75 | 68.1 | 0.761 | 31.98 | 51.8 | 3.1 | 29
KJ061 | 5 | 1500 | 90 | 67 | 75 | 68.1 | 0.874 | 36.73 | 59.5 | 3.1 | 29
KJ061 | 5 | 1500 | 75 | 72 | 75 | 74.5 | 0.357 | 16.42 | 26.6 | 3.1 | 29
KJ061 | 5 | 1500 | 80 | 72 | 75 | 74.5 | 0.467 | 21.48 | 34.8 | 3.1 | 29
KJ061 | 5 | 1500 | 85 | 72 | 75 | 74.5 | 0.579 | 26.6 | 43.1 | 3.1 | 29
KJ061 | 5 | 1500 | 90 | 72 | 75 | 74.5 | 0.69 | 31.73 | 51.4 | 3.1 | 29
KJ061 | 5 | 1500 | 80 | 77 | 75 | 80.8 | 0.322 | 16.05 | 26 | 3.2 | 29
KJ061 | 5 | 1500 | 85 | 77 | 75 | 80.8 | 0.426 | 21.23 | 34.4 | 3.2 | 29
KJ061 | 5 | 1500 | 90 | 77 | 75 | 80.8 | 0.53 | 26.42 | 42.8 | 3.2 | 29
KJ061 | 5 | 1500 | 65 | 57 | 85 | 58.7 | 0.571 | 20.68 | 33.5 | 3.5 | 29
KJ061 | 5 | 1500 | 70 | 57 | 85 | 58.7 | 0.714 | 25.86 | 41.9 | 3.5 | 29
KJ061 | 5 | 1500 | 75 | 57 | 85 | 58.7 | 0.857 | 31.05 | 50.3 | 3.5 | 29
KJ061 | 5 | 1500 | 80 | 57 | 85 | 58.7 | 0.998 | 36.17 | 58.6 | 3.5 | 29
KJ061 | 5 | 1500 | 85 | 57 | 85 | 58.7 | 1 | 36.23 | 58.7 | 3.5 | 29
KJ061 | 5 | 1500 | 90 | 57 | 85 | 58.7 | 1 | 36.23 | 58.7 | 3.5 | 29
KJ061 | 5 | 1500 | 65 | 62 | 85 | 61.6 | 0.411 | 15.62 | 25.3 | 3.5 | 29
KJ061 | 5 | 1500 | 70 | 62 | 85 | 61.6 | 0.545 | 20.74 | 33.6 | 3.5 | 29
KJ061 | 5 | 1500 | 75 | 62 | 85 | 61.6 | 0.672 | 25.56 | 41.4 | 3.5 | 29
KJ061 | 5 | 1500 | 80 | 62 | 85 | 61.6 | 0.817 | 31.05 | 50.3 | 3.5 | 29
KJ061 | 5 | 1500 | 85 | 62 | 85 | 61.6 | 0.919 | 34.94 | 56.6 | 3.5 | 29
KJ061 | 5 | 1500 | 90 | 62 | 85 | 61.6 | 0.953 | 36.23 | 58.7 | 3.5 | 29
KJ061 | 5 | 1500 | 70 | 67 | 85 | 64.6 | 0.392 | 15.62 | 25.3 | 3.5 | 29
KJ061 | 5 | 1500 | 75 | 67 | 85 | 64.6 | 0.52 | 20.74 | 33.6 | 3.5 | 29
KJ061 | 5 | 1500 | 80 | 67 | 85 | 64.6 | 0.649 | 25.86 | 41.9 | 3.5 | 29
KJ061 | 5 | 1500 | 85 | 67 | 85 | 64.6 | 0.779 | 31.05 | 50.3 | 3.5 | 29
KJ061 | 5 | 1500 | 90 | 67 | 85 | 64.6 | 0.907 | 36.17 | 58.6 | 3.5 | 29
KJ061 | 5 | 1500 | 75 | 72 | 85 | 70.9 | 0.357 | 15.62 | 25.3 | 3.6 | 29
KJ061 | 5 | 1500 | 80 | 72 | 85 | 70.9 | 0.474 | 20.74 | 33.6 | 3.6 | 29
KJ061 | 5 | 1500 | 85 | 72 | 85 | 70.9 | 0.59 | 25.8 | 41.8 | 3.6 | 29
KJ061 | 5 | 1500 | 90 | 72 | 85 | 70.9 | 0.707 | 30.93 | 50.1 | 3.6 | 29
KJ061 | 5 | 1500 | 80 | 77 | 85 | 77.3 | 0.326 | 15.56 | 25.2 | 3.6 | 29
KJ061 | 5 | 1500 | 85 | 77 | 85 | 77.3 | 0.432 | 20.62 | 33.4 | 3.6 | 29
KJ061 | 5 | 1500 | 90 | 77 | 85 | 77.3 | 0.537 | 25.62 | 41.5 | 3.6 | 29
KJ061 | 5 | 1500 | 65 | 57 | 95 | 57.8 | 0.55 | 19.63 | 31.8 | 3.9 | 29
KJ061 | 5 | 1500 | 70 | 57 | 95 | 57.8 | 0.69 | 24.63 | 39.9 | 3.9 | 29
KJ061 | 5 | 1500 | 75 | 57 | 95 | 57.8 | 0.829 | 29.57 | 47.9 | 3.9 | 29
KJ061 | 5 | 1500 | 80 | 57 | 95 | 57.8 | 0.967 | 34.51 | 55.9 | 3.9 | 29
KJ061 | 5 | 1500 | 85 | 57 | 95 | 57.8 | 1 | 35.68 | 57.8 | 3.9 | 29
KJ061 | 5 | 1500 | 90 | 57 | 95 | 57.8 | 1 | 35.68 | 57.8 | 3.9 | 29
KJ061 | 5 | 1500 | 65 | 62 | 95 | 59.4 | 0.401 | 14.69 | 23.8 | 3.9 | 29
KJ061 | 5 | 1500 | 70 | 62 | 95 | 59.4 | 0.537 | 19.69 | 31.9 | 3.9 | 29
KJ061 | 5 | 1500 | 75 | 62 | 95 | 59.4 | 0.673 | 24.69 | 40 | 3.9 | 29
KJ061 | 5 | 1500 | 80 | 62 | 95 | 59.4 | 0.81 | 29.69 | 48.1 | 3.9 | 29
KJ061 | 5 | 1500 | 85 | 62 | 95 | 59.4 | 0.911 | 33.4 | 54.1 | 3.9 | 29
KJ061 | 5 | 1500 | 90 | 62 | 95 | 59.4 | 0.97 | 35.56 | 57.6 | 3.9 | 29
KJ061 | 5 | 1500 | 70 | 67 | 95 | 61 | 0.392 | 14.75 | 23.9 | 4 | 29
KJ061 | 5 | 1500 | 75 | 67 | 95 | 61 | 0.525 | 19.75 | 32 | 4 | 29
KJ061 | 5 | 1500 | 80 | 67 | 95 | 61 | 0.659 | 24.81 | 40.2 | 4 | 29
KJ061 | 5 | 1500 | 85 | 67 | 95 | 61 | 0.798 | 30.06 | 48.7 | 4 | 29
KJ061 | 5 | 1500 | 90 | 67 | 95 | 61 | 0.939 | 35.37 | 57.3 | 4 | 29
KJ061 | 5 | 1500 | 75 | 72 | 95 | 67.3 | 0.358 | 14.88 | 24.1 | 4 | 29
KJ061 | 5 | 1500 | 80 | 72 | 95 | 67.3 | 0.48 | 19.94 | 32.3 | 4 | 29
KJ061 | 5 | 1500 | 85 | 72 | 95 | 67.3 | 0.602 | 25 | 40.5 | 4 | 29
KJ061 | 5 | 1500 | 90 | 72 | 95 | 67.3 | 0.725 | 30.12 | 48.8 | 4 | 29
KJ061 | 5 | 1500 | 80 | 77 | 95 | 73.7 | 0.331 | 15.06 | 24.4 | 4 | 29
KJ061 | 5 | 1500 | 85 | 77 | 95 | 73.7 | 0.438 | 19.94 | 32.3 | 4 | 29
KJ061 | 5 | 1500 | 90 | 77 | 95 | 73.7 | 0.545 | 24.81 | 40.2 | 4 | 29
KJ061 | 5 | 1500 | 65 | 57 | 105 | 56.8 | 0.521 | 18.27 | 29.6 | 4.5 | 29
KJ061 | 5 | 1500 | 70 | 57 | 105 | 56.8 | 0.665 | 23.33 | 37.8 | 4.5 | 29
KJ061 | 5 | 1500 | 75 | 57 | 105 | 56.8 | 0.81 | 28.4 | 46 | 4.5 | 29
KJ061 | 5 | 1500 | 80 | 57 | 105 | 56.8 | 0.956 | 33.52 | 54.3 | 4.5 | 29
KJ061 | 5 | 1500 | 85 | 57 | 105 | 56.8 | 0.996 | 34.94 | 56.6 | 4.5 | 29
KJ061 | 5 | 1500 | 90 | 57 | 105 | 56.8 | 1 | 35.06 | 56.8 | 4.5 | 29
KJ061 | 5 | 1500 | 65 | 62 | 105 | 56.9 | 0.38 | 13.33 | 21.6 | 4.5 | 29
KJ061 | 5 | 1500 | 70 | 62 | 105 | 56.9 | 0.524 | 18.4 | 29.8 | 4.5 | 29
KJ061 | 5 | 1500 | 75 | 62 | 105 | 56.9 | 0.67 | 23.52 | 38.1 | 4.5 | 29
KJ061 | 5 | 1500 | 80 | 62 | 105 | 56.9 | 0.814 | 28.58 | 46.3 | 4.5 | 29
KJ061 | 5 | 1500 | 85 | 62 | 105 | 56.9 | 0.909 | 31.91 | 51.7 | 4.5 | 29
KJ061 | 5 | 1500 | 90 | 62 | 105 | 56.9 | 1 | 35.12 | 56.9 | 4.5 | 29
KJ061 | 5 | 1500 | 70 | 67 | 105 | 57 | 0.384 | 13.52 | 21.9 | 4.6 | 29
KJ061 | 5 | 1500 | 75 | 67 | 105 | 57 | 0.528 | 18.58 | 30.1 | 4.6 | 29
KJ061 | 5 | 1500 | 80 | 67 | 105 | 57 | 0.672 | 23.64 | 38.3 | 4.6 | 29
KJ061 | 5 | 1500 | 85 | 67 | 105 | 57 | 0.819 | 28.83 | 46.7 | 4.6 | 29
KJ061 | 5 | 1500 | 90 | 67 | 105 | 57 | 0.967 | 34.01 | 55.1 | 4.6 | 29
KJ061 | 5 | 1500 | 75 | 72 | 105 | 63.1 | 0.35 | 13.64 | 22.1 | 4.6 | 29
KJ061 | 5 | 1500 | 80 | 72 | 105 | 63.1 | 0.48 | 18.7 | 30.3 | 4.6 | 29
KJ061 | 5 | 1500 | 85 | 72 | 105 | 63.1 | 0.61 | 23.77 | 38.5 | 4.6 | 29
KJ061 | 5 | 1500 | 90 | 72 | 105 | 63.1 | 0.74 | 28.83 | 46.7 | 4.6 | 29
KJ061 | 5 | 1500 | 80 | 77 | 105 | 69.9 | 0.319 | 13.77 | 22.3 | 4.6 | 29
KJ061 | 5 | 1500 | 85 | 77 | 105 | 69.9 | 0.433 | 18.7 | 30.3 | 4.6 | 29
KJ061 | 5 | 1500 | 90 | 77 | 105 | 69.9 | 0.546 | 23.58 | 38.2 | 4.6 | 29
KJ061 | 5 | 1500 | 65 | 57 | 115 | 55.8 | 0.489 | 16.85 | 27.3 | 5.1 | 30
KJ061 | 5 | 1500 | 70 | 57 | 115 | 55.8 | 0.64 | 22.04 | 35.7 | 5.1 | 30
KJ061 | 5 | 1500 | 75 | 57 | 115 | 55.8 | 0.792 | 27.28 | 44.2 | 5.1 | 30
KJ061 | 5 | 1500 | 80 | 57 | 115 | 55.8 | 0.943 | 32.47 | 52.6 | 5.1 | 30
KJ061 | 5 | 1500 | 85 | 57 | 115 | 55.8 | 0.964 | 33.21 | 53.8 | 5.1 | 30
KJ061 | 5 | 1500 | 90 | 57 | 115 | 55.8 | 0.984 | 33.89 | 54.9 | 5.1 | 30
KJ061 | 5 | 1500 | 65 | 62 | 115 | 55.9 | 0.349 | 12.04 | 19.5 | 5.2 | 30
KJ061 | 5 | 1500 | 70 | 62 | 115 | 55.9 | 0.497 | 17.16 | 27.8 | 5.2 | 30
KJ061 | 5 | 1500 | 75 | 62 | 115 | 55.9 | 0.648 | 22.35 | 36.2 | 5.2 | 30
KJ061 | 5 | 1500 | 80 | 62 | 115 | 55.9 | 0.796 | 27.47 | 44.5 | 5.2 | 30
KJ061 | 5 | 1500 | 85 | 62 | 115 | 55.9 | 0.88 | 30.37 | 49.2 | 5.2 | 30
KJ061 | 5 | 1500 | 90 | 62 | 115 | 55.9 | 0.964 | 33.27 | 53.9 | 5.2 | 30
KJ061 | 5 | 1500 | 70 | 67 | 115 | 56 | 0.355 | 12.28 | 19.9 | 5.2 | 30
KJ061 | 5 | 1500 | 75 | 67 | 115 | 56 | 0.504 | 17.41 | 28.2 | 5.2 | 30
KJ061 | 5 | 1500 | 80 | 67 | 115 | 56 | 0.65 | 22.47 | 36.4 | 5.2 | 30
KJ061 | 5 | 1500 | 85 | 67 | 115 | 56 | 0.798 | 27.59 | 44.7 | 5.2 | 30
KJ061 | 5 | 1500 | 90 | 67 | 115 | 56 | 0.946 | 32.72 | 53 | 5.2 | 30
KJ061 | 5 | 1500 | 75 | 72 | 115 | 58.8 | 0.344 | 12.47 | 20.2 | 5.2 | 30
KJ061 | 5 | 1500 | 80 | 72 | 115 | 58.8 | 0.481 | 17.47 | 28.3 | 5.2 | 30
KJ061 | 5 | 1500 | 85 | 72 | 115 | 58.8 | 0.621 | 22.53 | 36.5 | 5.2 | 30
KJ061 | 5 | 1500 | 90 | 72 | 115 | 58.8 | 0.759 | 27.53 | 44.6 | 5.2 | 30
KJ061 | 5 | 1500 | 80 | 77 | 115 | 66.1 | 0.306 | 12.47 | 20.2 | 5.2 | 30
KJ061 | 5 | 1500 | 85 | 77 | 115 | 66.1 | 0.427 | 17.41 | 28.2 | 5.2 | 30
KJ061 | 5 | 1500 | 90 | 77 | 115 | 66.1 | 0.549 | 22.41 | 36.3 | 5.2 | 30
KJ061 | 5 | 1500 | 65 | 57 | 125 | 54.8 | 0.456 | 15.43 | 25 | 5.8 | 30
KJ061 | 5 | 1500 | 70 | 57 | 125 | 54.8 | 0.613 | 20.74 | 33.6 | 5.8 | 30
KJ061 | 5 | 1500 | 75 | 57 | 125 | 54.8 | 0.772 | 26.11 | 42.3 | 5.8 | 30
KJ061 | 5 | 1500 | 80 | 57 | 125 | 54.8 | 0.925 | 31.3 | 50.7 | 5.8 | 30
KJ061 | 5 | 1500 | 85 | 57 | 125 | 54.8 | 0.925 | 31.3 | 50.7 | 5.8 | 30
KJ061 | 5 | 1500 | 90 | 57 | 125 | 54.8 | 0.925 | 31.3 | 50.7 | 5.8 | 30
KJ061 | 5 | 1500 | 65 | 62 | 125 | 54.8 | 0.316 | 10.68 | 17.3 | 5.8 | 30
KJ061 | 5 | 1500 | 70 | 62 | 125 | 54.8 | 0.471 | 15.93 | 25.8 | 5.8 | 30
KJ061 | 5 | 1500 | 75 | 62 | 125 | 54.8 | 0.626 | 21.17 | 34.3 | 5.8 | 30
KJ061 | 5 | 1500 | 80 | 62 | 125 | 54.8 | 0.781 | 26.42 | 42.8 | 5.8 | 30
KJ061 | 5 | 1500 | 85 | 62 | 125 | 54.8 | 0.854 | 28.89 | 46.8 | 5.8 | 30
KJ061 | 5 | 1500 | 90 | 62 | 125 | 54.8 | 0.927 | 31.36 | 50.8 | 5.8 | 30
KJ061 | 5 | 1500 | 70 | 67 | 125 | 54.9 | 0.326 | 11.05 | 17.9 | 5.8 | 30
KJ061 | 5 | 1500 | 75 | 67 | 125 | 54.9 | 0.477 | 16.17 | 26.2 | 5.8 | 30
KJ061 | 5 | 1500 | 80 | 67 | 125 | 54.9 | 0.628 | 21.3 | 34.5 | 5.8 | 30
KJ061 | 5 | 1500 | 85 | 67 | 125 | 54.9 | 0.778 | 26.36 | 42.7 | 5.8 | 30
KJ061 | 5 | 1500 | 90 | 67 | 125 | 54.9 | 0.925 | 31.36 | 50.8 | 5.8 | 30
KJ061 | 5 | 1500 | 75 | 72 | 125 | 54.6 | 0.333 | 11.23 | 18.2 | 5.8 | 30
KJ061 | 5 | 1500 | 80 | 72 | 125 | 54.6 | 0.482 | 16.23 | 26.3 | 5.8 | 30
KJ061 | 5 | 1500 | 85 | 72 | 125 | 54.6 | 0.63 | 21.23 | 34.4 | 5.8 | 30
KJ061 | 5 | 1500 | 90 | 72 | 125 | 54.6 | 0.778 | 26.23 | 42.5 | 5.8 | 30
KJ061 | 5 | 1500 | 80 | 77 | 125 | 62.3 | 0.291 | 11.17 | 18.1 | 5.9 | 30
KJ061 | 5 | 1500 | 85 | 77 | 125 | 62.3 | 0.421 | 16.17 | 26.2 | 5.9 | 30
KJ061 | 5 | 1500 | 90 | 77 | 125 | 62.3 | 0.551 | 21.17 | 34.3 | 5.9 | 30
KJ061 | 5 | 1750 | 65 | 57 | 75 | 64.6 | 0.573 | 19.58 | 37 | 3.1 | 29
KJ061 | 5 | 1750 | 70 | 57 | 75 | 64.6 | 0.729 | 24.92 | 47.1 | 3.1 | 29
KJ061 | 5 | 1750 | 75 | 57 | 75 | 64.6 | 0.885 | 30.26 | 57.2 | 3.1 | 29
KJ061 | 5 | 1750 | 80 | 57 | 75 | 64.6 | 1 | 34.18 | 64.6 | 3.1 | 29
KJ061 | 5 | 1750 | 85 | 57 | 75 | 64.6 | 1 | 34.18 | 64.6 | 3.1 | 29
KJ061 | 5 | 1750 | 90 | 57 | 75 | 64.6 | 1 | 34.18 | 64.6 | 3.1 | 29
KJ061 | 5 | 1750 | 65 | 62 | 75 | 67.7 | 0.405 | 14.5 | 27.4 | 3.1 | 29
KJ061 | 5 | 1750 | 70 | 62 | 75 | 67.7 | 0.551 | 19.74 | 37.3 | 3.1 | 29
KJ061 | 5 | 1750 | 75 | 62 | 75 | 67.7 | 0.687 | 24.6 | 46.5 | 3.1 | 29
KJ061 | 5 | 1750 | 80 | 62 | 75 | 67.7 | 0.845 | 30.26 | 57.2 | 3.1 | 29
KJ061 | 5 | 1750 | 85 | 62 | 75 | 67.7 | 0.929 | 33.28 | 62.9 | 3.1 | 29
KJ061 | 5 | 1750 | 90 | 62 | 75 | 67.7 | 0.953 | 34.13 | 64.5 | 3.1 | 29
KJ061 | 5 | 1750 | 70 | 67 | 75 | 70.8 | 0.388 | 14.55 | 27.5 | 3.1 | 29
KJ061 | 5 | 1750 | 75 | 67 | 75 | 70.8 | 0.525 | 19.68 | 37.2 | 3.1 | 29
KJ061 | 5 | 1750 | 80 | 67 | 75 | 70.8 | 0.664 | 24.87 | 47 | 3.1 | 29
KJ061 | 5 | 1750 | 85 | 67 | 75 | 70.8 | 0.787 | 29.47 | 55.7 | 3.1 | 29
KJ061 | 5 | 1750 | 90 | 67 | 75 | 70.8 | 0.91 | 34.07 | 64.4 | 3.1 | 29
KJ061 | 5 | 1750 | 75 | 72 | 75 | 76.5 | 0.357 | 14.44 | 27.3 | 3.1 | 29
KJ061 | 5 | 1750 | 80 | 72 | 75 | 76.5 | 0.482 | 19.52 | 36.9 | 3.1 | 29
KJ061 | 5 | 1750 | 85 | 72 | 75 | 76.5 | 0.608 | 24.6 | 46.5 | 3.1 | 29
KJ061 | 5 | 1750 | 90 | 72 | 75 | 76.5 | 0.733 | 29.68 | 56.1 | 3.1 | 29
KJ061 | 5 | 1750 | 80 | 77 | 75 | 82.2 | 0.325 | 14.13 | 26.7 | 3.2 | 29
KJ061 | 5 | 1750 | 85 | 77 | 75 | 82.2 | 0.453 | 19.68 | 37.2 | 3.2 | 29
KJ061 | 5 | 1750 | 90 | 77 | 75 | 82.2 | 0.58 | 25.24 | 47.7 | 3.2 | 29
KJ061 | 5 | 1750 | 65 | 57 | 85 | 62.8 | 0.565 | 18.78 | 35.5 | 3.5 | 29
KJ061 | 5 | 1750 | 70 | 57 | 85 | 62.8 | 0.721 | 23.97 | 45.3 | 3.5 | 29
KJ061 | 5 | 1750 | 75 | 57 | 85 | 62.8 | 0.876 | 29.1 | 55 | 3.5 | 29
KJ061 | 5 | 1750 | 80 | 57 | 85 | 62.8 | 1 | 33.23 | 62.8 | 3.5 | 29
KJ061 | 5 | 1750 | 85 | 57 | 85 | 62.8 | 1 | 33.23 | 62.8 | 3.5 | 29
KJ061 | 5 | 1750 | 90 | 57 | 85 | 62.8 | 1 | 33.23 | 62.8 | 3.5 | 29
KJ061 | 5 | 1750 | 65 | 62 | 85 | 64.9 | 0.399 | 13.7 | 25.9 | 3.5 | 29
KJ061 | 5 | 1750 | 70 | 62 | 85 | 64.9 | 0.549 | 18.84 | 35.6 | 3.5 | 29
KJ061 | 5 | 1750 | 75 | 62 | 85 | 64.9 | 0.692 | 23.76 | 44.9 | 3.5 | 29
KJ061 | 5 | 1750 | 80 | 62 | 85 | 64.9 | 0.847 | 29.1 | 55 | 3.5 | 29
KJ061 | 5 | 1750 | 85 | 62 | 85 | 64.9 | 0.931 | 31.96 | 60.4 | 3.5 | 29
KJ061 | 5 | 1750 | 90 | 62 | 85 | 64.9 | 0.968 | 33.23 | 62.8 | 3.5 | 29
KJ061 | 5 | 1750 | 70 | 67 | 85 | 67 | 0.387 | 13.7 | 25.9 | 3.5 | 29
KJ061 | 5 | 1750 | 75 | 67 | 85 | 67 | 0.53 | 18.78 | 35.5 | 3.5 | 29
KJ061 | 5 | 1750 | 80 | 67 | 85 | 67 | 0.675 | 23.92 | 45.2 | 3.5 | 29
KJ061 | 5 | 1750 | 85 | 67 | 85 | 67 | 0.806 | 28.57 | 54 | 3.5 | 29
KJ061 | 5 | 1750 | 90 | 67 | 85 | 67 | 0.937 | 33.23 | 62.8 | 3.5 | 29
KJ061 | 5 | 1750 | 75 | 72 | 85 | 72.6 | 0.357 | 13.7 | 25.9 | 3.5 | 29
KJ061 | 5 | 1750 | 80 | 72 | 85 | 72.6 | 0.489 | 18.78 | 35.5 | 3.5 | 29
KJ061 | 5 | 1750 | 85 | 72 | 85 | 72.6 | 0.62 | 23.81 | 45 | 3.5 | 29
KJ061 | 5 | 1750 | 90 | 72 | 85 | 72.6 | 0.752 | 28.89 | 54.6 | 3.5 | 29
KJ061 | 5 | 1750 | 80 | 77 | 85 | 78.2 | 0.329 | 13.6 | 25.7 | 3.6 | 29
KJ061 | 5 | 1750 | 85 | 77 | 85 | 78.2 | 0.462 | 19.1 | 36.1 | 3.6 | 29
KJ061 | 5 | 1750 | 90 | 77 | 85 | 78.2 | 0.593 | 24.55 | 46.4 | 3.6 | 29
KJ061 | 5 | 1750 | 65 | 57 | 95 | 61 | 0.557 | 17.99 | 34 | 3.9 | 29
KJ061 | 5 | 1750 | 70 | 57 | 95 | 61 | 0.711 | 22.96 | 43.4 | 3.9 | 29
KJ061 | 5 | 1750 | 75 | 57 | 95 | 61 | 0.866 | 27.94 | 52.8 | 3.9 | 29
KJ061 | 5 | 1750 | 80 | 57 | 95 | 61 | 1 | 32.28 | 61 | 3.9 | 29
KJ061 | 5 | 1750 | 85 | 57 | 95 | 61 | 1 | 32.28 | 61 | 3.9 | 29
KJ061 | 5 | 1750 | 90 | 57 | 95 | 61 | 1 | 32.28 | 61 | 3.9 | 29
KJ061 | 5 | 1750 | 65 | 62 | 95 | 62.1 | 0.393 | 12.91 | 24.4 | 3.9 | 29
KJ061 | 5 | 1750 | 70 | 62 | 95 | 62.1 | 0.546 | 17.94 | 33.9 | 3.9 | 29
KJ061 | 5 | 1750 | 75 | 62 | 95 | 62.1 | 0.699 | 22.96 | 43.4 | 3.9 | 29
KJ061 | 5 | 1750 | 80 | 62 | 95 | 62.1 | 0.85 | 27.94 | 52.8 | 3.9 | 29
KJ061 | 5 | 1750 | 85 | 62 | 95 | 62.1 | 0.934 | 30.69 | 58 | 3.9 | 29
KJ061 | 5 | 1750 | 90 | 62 | 95 | 62.1 | 0.982 | 32.28 | 61 | 3.9 | 29
KJ061 | 5 | 1750 | 70 | 67 | 95 | 63.2 | 0.386 | 12.91 | 24.4 | 4 | 29
KJ061 | 5 | 1750 | 75 | 67 | 95 | 63.2 | 0.536 | 17.94 | 33.9 | 4 | 29
KJ061 | 5 | 1750 | 80 | 67 | 95 | 63.2 | 0.687 | 22.96 | 43.4 | 4 | 29
KJ061 | 5 | 1750 | 85 | 67 | 95 | 63.2 | 0.828 | 27.67 | 52.3 | 4 | 29
KJ061 | 5 | 1750 | 90 | 67 | 95 | 63.2 | 0.965 | 32.28 | 61 | 4 | 29
KJ061 | 5 | 1750 | 75 | 72 | 95 | 68.7 | 0.357 | 12.96 | 24.5 | 4 | 29
KJ061 | 5 | 1750 | 80 | 72 | 95 | 68.7 | 0.496 | 18.04 | 34.1 | 4 | 29
KJ061 | 5 | 1750 | 85 | 72 | 95 | 68.7 | 0.635 | 23.07 | 43.6 | 4 | 29
KJ061 | 5 | 1750 | 90 | 72 | 95 | 68.7 | 0.774 | 28.15 | 53.2 | 4 | 29
KJ061 | 5 | 1750 | 80 | 77 | 95 | 74.2 | 0.333 | 13.07 | 24.7 | 3.9 | 29
KJ061 | 5 | 1750 | 85 | 77 | 95 | 74.2 | 0.47 | 18.47 | 34.9 | 3.9 | 29
KJ061 | 5 | 1750 | 90 | 77 | 95 | 74.2 | 0.609 | 23.92 | 45.2 | 3.9 | 29
KJ061 | 5 | 1750 | 65 | 57 | 105 | 59.2 | 0.534 | 16.72 | 31.6 | 4.5 | 29
KJ061 | 5 | 1750 | 70 | 57 | 105 | 59.2 | 0.696 | 21.8 | 41.2 | 4.5 | 29
KJ061 | 5 | 1750 | 75 | 57 | 105 | 59.2 | 0.858 | 26.88 | 50.8 | 4.5 | 29
KJ061 | 5 | 1750 | 80 | 57 | 105 | 59.2 | 1 | 31.32 | 59.2 | 4.5 | 29
KJ061 | 5 | 1750 | 85 | 57 | 105 | 59.2 | 1 | 31.32 | 59.2 | 4.5 | 29
KJ061 | 5 | 1750 | 90 | 57 | 105 | 59.2 | 1 | 31.32 | 59.2 | 4.5 | 29
KJ061 | 5 | 1750 | 65 | 62 | 105 | 59.3 | 0.374 | 11.75 | 22.2 | 4.5 | 29
KJ061 | 5 | 1750 | 70 | 62 | 105 | 59.3 | 0.536 | 16.83 | 31.8 | 4.5 | 29
KJ061 | 5 | 1750 | 75 | 62 | 105 | 59.3 | 0.698 | 21.9 | 41.4 | 4.5 | 29
KJ061 | 5 | 1750 | 80 | 62 | 105 | 59.3 | 0.86 | 26.98 | 51 | 4.5 | 29
KJ061 | 5 | 1750 | 85 | 62 | 105 | 59.3 | 0.934 | 29.31 | 55.4 | 4.5 | 29
KJ061 | 5 | 1750 | 90 | 62 | 105 | 59.3 | 1 | 31.38 | 59.3 | 4.5 | 29
KJ061 | 5 | 1750 | 70 | 67 | 105 | 59.4 | 0.375 | 11.8 | 22.3 | 4.6 | 29
KJ061 | 5 | 1750 | 75 | 67 | 105 | 59.4 | 0.537 | 16.88 | 31.9 | 4.6 | 29
KJ061 | 5 | 1750 | 80 | 67 | 105 | 59.4 | 0.697 | 21.9 | 41.4 | 4.6 | 29
KJ061 | 5 | 1750 | 85 | 67 | 105 | 59.4 | 0.84 | 26.4 | 49.9 | 4.6 | 29
KJ061 | 5 | 1750 | 90 | 67 | 105 | 59.4 | 0.983 | 30.9 | 58.4 | 4.6 | 29
KJ061 | 5 | 1750 | 75 | 72 | 105 | 64.4 | 0.348 | 11.85 | 22.4 | 4.6 | 29
KJ061 | 5 | 1750 | 80 | 72 | 105 | 64.4 | 0.495 | 16.88 | 31.9 | 4.6 | 29
KJ061 | 5 | 1750 | 85 | 72 | 105 | 64.4 | 0.644 | 21.96 | 41.5 | 4.6 | 29
KJ061 | 5 | 1750 | 90 | 72 | 105 | 64.4 | 0.792 | 26.98 | 51 | 4.6 | 29
KJ061 | 5 | 1750 | 80 | 77 | 105 | 70 | 0.32 | 11.85 | 22.4 | 4.6 | 29
KJ061 | 5 | 1750 | 85 | 77 | 105 | 70 | 0.471 | 17.46 | 33 | 4.6 | 29
KJ061 | 5 | 1750 | 90 | 77 | 105 | 70 | 0.623 | 23.07 | 43.6 | 4.6 | 29
KJ061 | 5 | 1750 | 65 | 57 | 115 | 57.4 | 0.509 | 15.45 | 29.2 | 5.1 | 30
KJ061 | 5 | 1750 | 70 | 57 | 115 | 57.4 | 0.679 | 20.63 | 39 | 5.1 | 30
KJ061 | 5 | 1750 | 75 | 57 | 115 | 57.4 | 0.852 | 25.87 | 48.9 | 5.1 | 30
KJ061 | 5 | 1750 | 80 | 57 | 115 | 57.4 | 0.995 | 30.21 | 57.1 | 5.1 | 30
KJ061 | 5 | 1750 | 85 | 57 | 115 | 57.4 | 0.995 | 30.21 | 57.1 | 5.1 | 30
KJ061 | 5 | 1750 | 90 | 57 | 115 | 57.4 | 0.995 | 30.21 | 57.1 | 5.1 | 30
KJ061 | 5 | 1750 | 65 | 62 | 115 | 57.5 | 0.346 | 10.53 | 19.9 | 5.1 | 30
KJ061 | 5 | 1750 | 70 | 62 | 115 | 57.5 | 0.515 | 15.66 | 29.6 | 5.1 | 30
KJ061 | 5 | 1750 | 75 | 62 | 115 | 57.5 | 0.685 | 20.85 | 39.4 | 5.1 | 30
KJ061 | 5 | 1750 | 80 | 62 | 115 | 57.5 | 0.854 | 25.98 | 49.1 | 5.1 | 30
KJ061 | 5 | 1750 | 85 | 62 | 115 | 57.5 | 0.918 | 27.94 | 52.8 | 5.1 | 30
KJ061 | 5 | 1750 | 90 | 62 | 115 | 57.5 | 0.981 | 29.84 | 56.4 | 5.1 | 30
KJ061 | 5 | 1750 | 70 | 67 | 115 | 57.6 | 0.351 | 10.69 | 20.2 | 5.2 | 30
KJ061 | 5 | 1750 | 75 | 67 | 115 | 57.6 | 0.517 | 15.77 | 29.8 | 5.2 | 30
KJ061 | 5 | 1750 | 80 | 67 | 115 | 57.6 | 0.686 | 20.9 | 39.5 | 5.2 | 30
KJ061 | 5 | 1750 | 85 | 67 | 115 | 57.6 | 0.826 | 25.19 | 47.6 | 5.2 | 30
KJ061 | 5 | 1750 | 90 | 67 | 115 | 57.6 | 0.967 | 29.47 | 55.7 | 5.2 | 30
KJ061 | 5 | 1750 | 75 | 72 | 115 | 60.1 | 0.338 | 10.74 | 20.3 | 5.2 | 30
KJ061 | 5 | 1750 | 80 | 72 | 115 | 60.1 | 0.496 | 15.77 | 29.8 | 5.2 | 30
KJ061 | 5 | 1750 | 85 | 72 | 115 | 60.1 | 0.654 | 20.79 | 39.3 | 5.2 | 30
KJ061 | 5 | 1750 | 90 | 72 | 115 | 60.1 | 0.812 | 25.82 | 48.8 | 5.2 | 30
KJ061 | 5 | 1750 | 80 | 77 | 115 | 65.9 | 0.307 | 10.69 | 20.2 | 5.2 | 30
KJ061 | 5 | 1750 | 85 | 77 | 115 | 65.9 | 0.472 | 16.46 | 31.1 | 5.2 | 30
KJ061 | 5 | 1750 | 90 | 77 | 115 | 65.9 | 0.637 | 22.22 | 42 | 5.2 | 30
KJ061 | 5 | 1750 | 65 | 57 | 125 | 55.6 | 0.482 | 14.18 | 26.8 | 5.7 | 30
KJ061 | 5 | 1750 | 70 | 57 | 125 | 55.6 | 0.664 | 19.52 | 36.9 | 5.7 | 30
KJ061 | 5 | 1750 | 75 | 57 | 125 | 55.6 | 0.844 | 24.81 | 46.9 | 5.7 | 30
KJ061 | 5 | 1750 | 80 | 57 | 125 | 55.6 | 0.955 | 28.1 | 53.1 | 5.7 | 30
KJ061 | 5 | 1750 | 85 | 57 | 125 | 55.6 | 0.955 | 28.1 | 53.1 | 5.7 | 30
KJ061 | 5 | 1750 | 90 | 57 | 125 | 55.6 | 0.955 | 28.1 | 53.1 | 5.7 | 30
KJ061 | 5 | 1750 | 65 | 62 | 125 | 55.6 | 0.317 | 9.31 | 17.6 | 5.7 | 30
KJ061 | 5 | 1750 | 70 | 62 | 125 | 55.6 | 0.495 | 14.55 | 27.5 | 5.7 | 30
KJ061 | 5 | 1750 | 75 | 62 | 125 | 55.6 | 0.673 | 19.79 | 37.4 | 5.7 | 30
KJ061 | 5 | 1750 | 80 | 62 | 125 | 55.6 | 0.849 | 24.97 | 47.2 | 5.7 | 30
KJ061 | 5 | 1750 | 85 | 62 | 125 | 55.6 | 0.901 | 26.51 | 50.1 | 5.7 | 30
KJ061 | 5 | 1750 | 90 | 62 | 125 | 55.6 | 0.953 | 28.04 | 53 | 5.7 | 30
KJ061 | 5 | 1750 | 70 | 67 | 125 | 55.7 | 0.325 | 9.58 | 18.1 | 5.8 | 30
KJ061 | 5 | 1750 | 75 | 67 | 125 | 55.7 | 0.499 | 14.71 | 27.8 | 5.8 | 30
KJ061 | 5 | 1750 | 80 | 67 | 125 | 55.7 | 0.673 | 19.84 | 37.5 | 5.8 | 30
KJ061 | 5 | 1750 | 85 | 67 | 125 | 55.7 | 0.811 | 23.92 | 45.2 | 5.8 | 30
KJ061 | 5 | 1750 | 90 | 67 | 125 | 55.7 | 0.952 | 28.04 | 53 | 5.8 | 30
KJ061 | 5 | 1750 | 75 | 72 | 125 | 55.8 | 0.326 | 9.63 | 18.2 | 5.8 | 30
KJ061 | 5 | 1750 | 80 | 72 | 125 | 55.8 | 0.496 | 14.66 | 27.7 | 5.8 | 30
KJ061 | 5 | 1750 | 85 | 72 | 125 | 55.8 | 0.667 | 19.68 | 37.2 | 5.8 | 30
KJ061 | 5 | 1750 | 90 | 72 | 125 | 55.8 | 0.837 | 24.71 | 46.7 | 5.8 | 30
KJ061 | 5 | 1750 | 80 | 77 | 125 | 61.7 | 0.29 | 9.47 | 17.9 | 5.8 | 30
KJ061 | 5 | 1750 | 85 | 77 | 125 | 61.7 | 0.473 | 15.45 | 29.2 | 5.8 | 30
KJ061 | 5 | 1750 | 90 | 77 | 125 | 61.7 | 0.655 | 21.38 | 40.4 | 5.8 | 30
KJ061 | 5 | 2000 | 65 | 57 | 75 | 69.5 | 0.561 | 18.06 | 39 | 3.1 | 29
KJ061 | 5 | 2000 | 70 | 57 | 75 | 69.5 | 0.725 | 23.33 | 50.4 | 3.1 | 29
KJ061 | 5 | 2000 | 75 | 57 | 75 | 69.5 | 0.891 | 28.66 | 61.9 | 3.1 | 29
KJ061 | 5 | 2000 | 80 | 57 | 75 | 69.5 | 1 | 32.18 | 69.5 | 3.1 | 29
KJ061 | 5 | 2000 | 85 | 57 | 75 | 69.5 | 1 | 32.18 | 69.5 | 3.1 | 29
KJ061 | 5 | 2000 | 90 | 57 | 75 | 69.5 | 1 | 32.18 | 69.5 | 3.1 | 29
KJ061 | 5 | 2000 | 65 | 62 | 75 | 71.5 | 0.392 | 12.96 | 28 | 3.1 | 29
KJ061 | 5 | 2000 | 70 | 62 | 75 | 71.5 | 0.55 | 18.19 | 39.3 | 3.1 | 29
KJ061 | 5 | 2000 | 75 | 62 | 75 | 71.5 | 0.701 | 23.19 | 50.1 | 3.1 | 29
KJ061 | 5 | 2000 | 80 | 62 | 75 | 71.5 | 0.866 | 28.66 | 61.9 | 3.1 | 29
KJ061 | 5 | 2000 | 85 | 62 | 75 | 71.5 | 0.933 | 30.88 | 66.7 | 3.1 | 29
KJ061 | 5 | 2000 | 90 | 62 | 75 | 71.5 | 0.971 | 32.13 | 69.4 | 3.1 | 29
KJ061 | 5 | 2000 | 70 | 67 | 75 | 73.4 | 0.384 | 13.06 | 28.2 | 3.1 | 29
KJ061 | 5 | 2000 | 75 | 67 | 75 | 73.4 | 0.534 | 18.15 | 39.2 | 3.1 | 29
KJ061 | 5 | 2000 | 80 | 67 | 75 | 73.4 | 0.687 | 23.33 | 50.4 | 3.1 | 29
KJ061 | 5 | 2000 | 85 | 67 | 75 | 73.4 | 0.812 | 27.59 | 59.6 | 3.1 | 29
KJ061 | 5 | 2000 | 90 | 67 | 75 | 73.4 | 0.939 | 31.9 | 68.9 | 3.1 | 29
KJ061 | 5 | 2000 | 75 | 72 | 75 | 78.5 | 0.355 | 12.92 | 27.9 | 3.1 | 29
KJ061 | 5 | 2000 | 80 | 72 | 75 | 78.5 | 0.496 | 18.01 | 38.9 | 3.1 | 29
KJ061 | 5 | 2000 | 85 | 72 | 75 | 78.5 | 0.634 | 23.06 | 49.8 | 3.1 | 29
KJ061 | 5 | 2000 | 90 | 72 | 75 | 78.5 | 0.773 | 28.1 | 60.7 | 3.1 | 29
KJ061 | 5 | 2000 | 80 | 77 | 75 | 83.5 | 0.328 | 12.69 | 27.4 | 3.1 | 29
KJ061 | 5 | 2000 | 85 | 77 | 75 | 83.5 | 0.479 | 18.52 | 40 | 3.1 | 29
KJ061 | 5 | 2000 | 90 | 77 | 75 | 83.5 | 0.63 | 24.35 | 52.6 | 3.1 | 29
KJ061 | 5 | 2000 | 65 | 57 | 85 | 66.8 | 0.563 | 17.41 | 37.6 | 3.5 | 29
KJ061 | 5 | 2000 | 70 | 57 | 85 | 66.8 | 0.729 | 22.55 | 48.7 | 3.5 | 29
KJ061 | 5 | 2000 | 75 | 57 | 85 | 66.8 | 0.895 | 27.69 | 59.8 | 3.5 | 29
KJ061 | 5 | 2000 | 80 | 57 | 85 | 66.8 | 1 | 30.93 | 66.8 | 3.5 | 29
KJ061 | 5 | 2000 | 85 | 57 | 85 | 66.8 | 1 | 30.93 | 66.8 | 3.5 | 29
KJ061 | 5 | 2000 | 90 | 57 | 85 | 66.8 | 1 | 30.93 | 66.8 | 3.5 | 29
KJ061 | 5 | 2000 | 65 | 62 | 85 | 68.1 | 0.391 | 12.31 | 26.6 | 3.5 | 29
KJ061 | 5 | 2000 | 70 | 62 | 85 | 68.1 | 0.552 | 17.41 | 37.6 | 3.5 | 29
KJ061 | 5 | 2000 | 75 | 62 | 85 | 68.1 | 0.711 | 22.41 | 48.4 | 3.5 | 29
KJ061 | 5 | 2000 | 80 | 62 | 85 | 68.1 | 0.877 | 27.64 | 59.7 | 3.5 | 29
KJ061 | 5 | 2000 | 85 | 62 | 85 | 68.1 | 0.944 | 29.77 | 64.3 | 3.5 | 29
KJ061 | 5 | 2000 | 90 | 62 | 85 | 68.1 | 0.981 | 30.93 | 66.8 | 3.5 | 29
KJ061 | 5 | 2000 | 70 | 67 | 85 | 69.4 | 0.383 | 12.31 | 26.6 | 3.5 | 29
KJ061 | 5 | 2000 | 75 | 67 | 85 | 69.4 | 0.54 | 17.36 | 37.5 | 3.5 | 29
KJ061 | 5 | 2000 | 80 | 67 | 85 | 69.4 | 0.699 | 22.45 | 48.5 | 3.5 | 29
KJ061 | 5 | 2000 | 85 | 67 | 85 | 69.4 | 0.833 | 26.76 | 57.8 | 3.5 | 29
KJ061 | 5 | 2000 | 90 | 67 | 85 | 69.4 | 0.958 | 30.79 | 66.5 | 3.5 | 29
KJ061 | 5 | 2000 | 75 | 72 | 85 | 74.2 | 0.356 | 12.22 | 26.4 | 3.5 | 29
KJ061 | 5 | 2000 | 80 | 72 | 85 | 74.2 | 0.503 | 17.27 | 37.3 | 3.5 | 29
KJ061 | 5 | 2000 | 85 | 72 | 85 | 74.2 | 0.651 | 22.36 | 48.3 | 3.5 | 29
KJ061 | 5 | 2000 | 90 | 72 | 85 | 74.2 | 0.798 | 27.41 | 59.2 | 3.5 | 29
KJ061 | 5 | 2000 | 80 | 77 | 85 | 79.1 | 0.33 | 12.08 | 26.1 | 3.5 | 29
KJ061 | 5 | 2000 | 85 | 77 | 85 | 79.1 | 0.491 | 17.96 | 38.8 | 3.5 | 29
KJ061 | 5 | 2000 | 90 | 77 | 85 | 79.1 | 0.65 | 23.8 | 51.4 | 3.5 | 29
KJ061 | 5 | 2000 | 65 | 57 | 95 | 64.2 | 0.562 | 16.71 | 36.1 | 3.9 | 29
KJ061 | 5 | 2000 | 70 | 57 | 95 | 64.2 | 0.731 | 21.71 | 46.9 | 3.9 | 29
KJ061 | 5 | 2000 | 75 | 57 | 95 | 64.2 | 0.899 | 26.71 | 57.7 | 3.9 | 29
KJ061 | 5 | 2000 | 80 | 57 | 95 | 64.2 | 1 | 29.72 | 64.2 | 3.9 | 29
KJ061 | 5 | 2000 | 85 | 57 | 95 | 64.2 | 1 | 29.72 | 64.2 | 3.9 | 29
KJ061 | 5 | 2000 | 90 | 57 | 95 | 64.2 | 1 | 29.72 | 64.2 | 3.9 | 29
KJ061 | 5 | 2000 | 65 | 62 | 95 | 64.8 | 0.387 | 11.62 | 25.1 | 3.9 | 29
KJ061 | 5 | 2000 | 70 | 62 | 95 | 64.8 | 0.554 | 16.62 | 35.9 | 3.9 | 29
KJ061 | 5 | 2000 | 75 | 62 | 95 | 64.8 | 0.721 | 21.62 | 46.7 | 3.9 | 29
KJ061 | 5 | 2000 | 80 | 62 | 95 | 64.8 | 0.889 | 26.67 | 57.6 | 3.9 | 29
KJ061 | 5 | 2000 | 85 | 62 | 95 | 64.8 | 0.955 | 28.66 | 61.9 | 3.9 | 29
KJ061 | 5 | 2000 | 90 | 62 | 95 | 64.8 | 0.989 | 29.68 | 64.1 | 3.9 | 29
KJ061 | 5 | 2000 | 70 | 67 | 95 | 65.3 | 0.381 | 11.53 | 24.9 | 4 | 29
KJ061 | 5 | 2000 | 75 | 67 | 95 | 65.3 | 0.548 | 16.57 | 35.8 | 4 | 29
KJ061 | 5 | 2000 | 80 | 67 | 95 | 65.3 | 0.715 | 21.62 | 46.7 | 4 | 29
KJ061 | 5 | 2000 | 85 | 67 | 95 | 65.3 | 0.856 | 25.88 | 55.9 | 4 | 29
KJ061 | 5 | 2000 | 90 | 67 | 95 | 65.3 | 0.98 | 29.63 | 64 | 4 | 29
KJ061 | 5 | 2000 | 75 | 72 | 95 | 70 | 0.356 | 11.53 | 24.9 | 4 | 29
KJ061 | 5 | 2000 | 80 | 72 | 95 | 70 | 0.511 | 16.57 | 35.8 | 4 | 29
KJ061 | 5 | 2000 | 85 | 72 | 95 | 70 | 0.667 | 21.62 | 46.7 | 4 | 29
KJ061 | 5 | 2000 | 90 | 72 | 95 | 70 | 0.823 | 26.67 | 57.6 | 4 | 29
KJ061 | 5 | 2000 | 80 | 77 | 95 | 74.7 | 0.333 | 11.53 | 24.9 | 3.9 | 29
KJ061 | 5 | 2000 | 85 | 77 | 95 | 74.7 | 0.502 | 17.36 | 37.5 | 3.9 | 29
KJ061 | 5 | 2000 | 90 | 77 | 95 | 74.7 | 0.672 | 23.24 | 50.2 | 3.9 | 29
KJ061 | 5 | 2000 | 65 | 57 | 105 | 61.6 | 0.545 | 15.56 | 33.6 | 4.5 | 29
KJ061 | 5 | 2000 | 70 | 57 | 105 | 61.6 | 0.724 | 20.65 | 44.6 | 4.5 | 29
KJ061 | 5 | 2000 | 75 | 57 | 105 | 61.6 | 0.903 | 25.74 | 55.6 | 4.5 | 29
KJ061 | 5 | 2000 | 80 | 57 | 105 | 61.6 | 1 | 28.52 | 61.6 | 4.5 | 29
KJ061 | 5 | 2000 | 85 | 57 | 105 | 61.6 | 1 | 28.52 | 61.6 | 4.5 | 29
KJ061 | 5 | 2000 | 90 | 57 | 105 | 61.6 | 1 | 28.52 | 61.6 | 4.5 | 29
KJ061 | 5 | 2000 | 65 | 62 | 105 | 61.6 | 0.369 | 10.51 | 22.7 | 4.5 | 29
KJ061 | 5 | 2000 | 70 | 62 | 105 | 61.6 | 0.547 | 15.6 | 33.7 | 4.5 | 29
KJ061 | 5 | 2000 | 75 | 62 | 105 | 61.6 | 0.724 | 20.65 | 44.6 | 4.5 | 29
KJ061 | 5 | 2000 | 80 | 62 | 105 | 61.6 | 0.903 | 25.74 | 55.6 | 4.5 | 29
KJ061 | 5 | 2000 | 85 | 62 | 105 | 61.6 | 0.959 | 27.36 | 59.1 | 4.5 | 29
KJ061 | 5 | 2000 | 90 | 62 | 105 | 61.6 | 1 | 28.52 | 61.6 | 4.5 | 29
KJ061 | 5 | 2000 | 70 | 67 | 105 | 61.7 | 0.368 | 10.51 | 22.7 | 4.5 | 29
KJ061 | 5 | 2000 | 75 | 67 | 105 | 61.7 | 0.546 | 15.6 | 33.7 | 4.5 | 29
KJ061 | 5 | 2000 | 80 | 67 | 105 | 61.7 | 0.723 | 20.65 | 44.6 | 4.5 | 29
KJ061 | 5 | 2000 | 85 | 67 | 105 | 61.7 | 0.862 | 24.63 | 53.2 | 4.5 | 29
KJ061 | 5 | 2000 | 90 | 67 | 105 | 61.7 | 1 | 28.56 | 61.7 | 4.5 | 29
KJ061 | 5 | 2000 | 75 | 72 | 105 | 65.6 | 0.346 | 10.51 | 22.7 | 4.5 | 29
KJ061 | 5 | 2000 | 80 | 72 | 105 | 65.6 | 0.512 | 15.56 | 33.6 | 4.5 | 29
KJ061 | 5 | 2000 | 85 | 72 | 105 | 65.6 | 0.678 | 20.6 | 44.5 | 4.5 | 29
KJ061 | 5 | 2000 | 90 | 72 | 105 | 65.6 | 0.845 | 25.65 | 55.4 | 4.5 | 29
KJ061 | 5 | 2000 | 80 | 77 | 105 | 70.1 | 0.321 | 10.42 | 22.5 | 4.6 | 29
KJ061 | 5 | 2000 | 85 | 77 | 105 | 70.1 | 0.509 | 16.53 | 35.7 | 4.6 | 29
KJ061 | 5 | 2000 | 90 | 77 | 105 | 70.1 | 0.698 | 22.64 | 48.9 | 4.6 | 29
KJ061 | 5 | 2000 | 65 | 57 | 115 | 59 | 0.527 | 14.4 | 31.1 | 5.1 | 30
KJ061 | 5 | 2000 | 70 | 57 | 115 | 59 | 0.717 | 19.58 | 42.3 | 5.1 | 30
KJ061 | 5 | 2000 | 75 | 57 | 115 | 59 | 0.908 | 24.81 | 53.6 | 5.1 | 30
KJ061 | 5 | 2000 | 80 | 57 | 115 | 59 | 1 | 27.31 | 59 | 5.1 | 30
KJ061 | 5 | 2000 | 85 | 57 | 115 | 59 | 1 | 27.31 | 59 | 5.1 | 30
KJ061 | 5 | 2000 | 90 | 57 | 115 | 59 | 1 | 27.31 | 59 | 5.1 | 30
KJ061 | 5 | 2000 | 65 | 62 | 115 | 59 | 0.344 | 9.4 | 20.3 | 5.1 | 30
KJ061 | 5 | 2000 | 70 | 62 | 115 | 59 | 0.532 | 14.54 | 31.4 | 5.1 | 30
KJ061 | 5 | 2000 | 75 | 62 | 115 | 59 | 0.72 | 19.68 | 42.5 | 5.1 | 30
KJ061 | 5 | 2000 | 80 | 62 | 115 | 59 | 0.91 | 24.86 | 53.7 | 5.1 | 30
KJ061 | 5 | 2000 | 85 | 62 | 115 | 59 | 0.954 | 26.06 | 56.3 | 5.1 | 30
KJ061 | 5 | 2000 | 90 | 62 | 115 | 59 | 0.998 | 27.27 | 58.9 | 5.1 | 30
KJ061 | 5 | 2000 | 70 | 67 | 115 | 59 | 0.347 | 9.49 | 20.5 | 5.1 | 30
KJ061 | 5 | 2000 | 75 | 67 | 115 | 59 | 0.534 | 14.58 | 31.5 | 5.1 | 30
KJ061 | 5 | 2000 | 80 | 67 | 115 | 59 | 0.72 | 19.68 | 42.5 | 5.1 | 30
KJ061 | 5 | 2000 | 85 | 67 | 115 | 59 | 0.856 | 23.38 | 50.5 | 5.1 | 30
KJ061 | 5 | 2000 | 90 | 67 | 115 | 59 | 0.99 | 27.04 | 58.4 | 5.1 | 30
KJ061 | 5 | 2000 | 75 | 72 | 115 | 61.3 | 0.334 | 9.49 | 20.5 | 5.1 | 30
KJ061 | 5 | 2000 | 80 | 72 | 115 | 61.3 | 0.511 | 14.49 | 31.3 | 5.1 | 30
KJ061 | 5 | 2000 | 85 | 72 | 115 | 61.3 | 0.688 | 19.54 | 42.2 | 5.1 | 30
KJ061 | 5 | 2000 | 90 | 72 | 115 | 61.3 | 0.866 | 24.58 | 53.1 | 5.1 | 30
KJ061 | 5 | 2000 | 80 | 77 | 115 | 65.6 | 0.308 | 9.35 | 20.2 | 5.2 | 30
KJ061 | 5 | 2000 | 85 | 77 | 115 | 65.6 | 0.517 | 15.69 | 33.9 | 5.2 | 30
KJ061 | 5 | 2000 | 90 | 77 | 115 | 65.6 | 0.727 | 22.08 | 47.7 | 5.2 | 30
KJ061 | 5 | 2000 | 65 | 57 | 125 | 56.4 | 0.507 | 13.24 | 28.6 | 5.7 | 30
KJ061 | 5 | 2000 | 70 | 57 | 125 | 56.4 | 0.711 | 18.56 | 40.1 | 5.7 | 30
KJ061 | 5 | 2000 | 75 | 57 | 125 | 56.4 | 0.915 | 23.89 | 51.6 | 5.7 | 30
KJ061 | 5 | 2000 | 80 | 57 | 125 | 56.4 | 0.982 | 25.65 | 55.4 | 5.7 | 30
KJ061 | 5 | 2000 | 85 | 57 | 125 | 56.4 | 0.982 | 25.65 | 55.4 | 5.7 | 30
KJ061 | 5 | 2000 | 90 | 57 | 125 | 56.4 | 0.982 | 25.65 | 55.4 | 5.7 | 30
KJ061 | 5 | 2000 | 65 | 62 | 125 | 56.5 | 0.317 | 8.29 | 17.9 | 5.7 | 30
KJ061 | 5 | 2000 | 70 | 62 | 125 | 56.5 | 0.517 | 13.52 | 29.2 | 5.7 | 30
KJ061 | 5 | 2000 | 75 | 62 | 125 | 56.5 | 0.715 | 18.7 | 40.4 | 5.7 | 30
KJ061 | 5 | 2000 | 80 | 62 | 125 | 56.5 | 0.915 | 23.94 | 51.7 | 5.7 | 30
KJ061 | 5 | 2000 | 85 | 62 | 125 | 56.5 | 0.947 | 24.77 | 53.5 | 5.7 | 30
KJ061 | 5 | 2000 | 90 | 62 | 125 | 56.5 | 0.977 | 25.56 | 55.2 | 5.7 | 30
KJ061 | 5 | 2000 | 70 | 67 | 125 | 56.6 | 0.323 | 8.47 | 18.3 | 5.7 | 30
KJ061 | 5 | 2000 | 75 | 67 | 125 | 56.6 | 0.518 | 13.56 | 29.3 | 5.7 | 30
KJ061 | 5 | 2000 | 80 | 67 | 125 | 56.6 | 0.714 | 18.7 | 40.4 | 5.7 | 30
KJ061 | 5 | 2000 | 85 | 67 | 125 | 56.6 | 0.845 | 22.13 | 47.8 | 5.7 | 30
KJ061 | 5 | 2000 | 90 | 67 | 125 | 56.6 | 0.973 | 25.51 | 55.1 | 5.7 | 30
KJ061 | 5 | 2000 | 75 | 72 | 125 | 56.9 | 0.32 | 8.43 | 18.2 | 5.7 | 30
KJ061 | 5 | 2000 | 80 | 72 | 125 | 56.9 | 0.511 | 13.47 | 29.1 | 5.7 | 30
KJ061 | 5 | 2000 | 85 | 72 | 125 | 56.9 | 0.703 | 18.52 | 40 | 5.7 | 30
KJ061 | 5 | 2000 | 90 | 72 | 125 | 56.9 | 0.893 | 23.52 | 50.8 | 5.7 | 30
KJ061 | 5 | 2000 | 80 | 77 | 125 | 61.1 | 0.291 | 8.24 | 17.8 | 5.8 | 30
KJ061 | 5 | 2000 | 85 | 77 | 125 | 61.1 | 0.525 | 14.86 | 32.1 | 5.8 | 30
KJ061 | 5 | 2000 | 90 | 77 | 125 | 61.1 | 0.761 | 21.53 | 46.5 | 5.8 | 30
KJ061 | 5 | 2250 | 65 | 57 | 75 | 74.4 | 0.55 | 16.83 | 40.9 | 3.1 | 29
KJ061 | 5 | 2250 | 70 | 57 | 75 | 74.4 | 0.722 | 22.1 | 53.7 | 3.1 | 29
KJ061 | 5 | 2250 | 75 | 57 | 75 | 74.4 | 0.895 | 27.41 | 66.6 | 3.1 | 29
KJ061 | 5 | 2250 | 80 | 57 | 75 | 74.4 | 0.989 | 30.29 | 73.6 | 3.1 | 29
KJ061 | 5 | 2250 | 85 | 57 | 75 | 74.4 | 0.989 | 30.29 | 73.6 | 3.1 | 29
KJ061 | 5 | 2250 | 90 | 57 | 75 | 74.4 | 0.989 | 30.29 | 73.6 | 3.1 | 29
KJ061 | 5 | 2250 | 65 | 62 | 75 | 75.2 | 0.38 | 11.77 | 28.6 | 3.1 | 29
KJ061 | 5 | 2250 | 70 | 62 | 75 | 75.2 | 0.549 | 17 | 41.3 | 3.1 | 29
KJ061 | 5 | 2250 | 75 | 62 | 75 | 75.2 | 0.714 | 22.1 | 53.7 | 3.1 | 29
KJ061 | 5 | 2250 | 80 | 62 | 75 | 75.2 | 0.886 | 27.41 | 66.6 | 3.1 | 29
KJ061 | 5 | 2250 | 85 | 62 | 75 | 75.2 | 0.939 | 29.05 | 70.6 | 3.1 | 29
KJ061 | 5 | 2250 | 90 | 62 | 75 | 75.2 | 0.977 | 30.25 | 73.5 | 3.1 | 29
KJ061 | 5 | 2250 | 70 | 67 | 75 | 76.1 | 0.378 | 11.85 | 28.8 | 3.1 | 29
KJ061 | 5 | 2250 | 75 | 67 | 75 | 76.1 | 0.541 | 16.95 | 41.2 | 3.1 | 29
KJ061 | 5 | 2250 | 80 | 67 | 75 | 76.1 | 0.706 | 22.1 | 53.7 | 3.1 | 29
KJ061 | 5 | 2250 | 85 | 67 | 75 | 76.1 | 0.834 | 26.13 | 63.5 | 3.1 | 29
KJ061 | 5 | 2250 | 90 | 67 | 75 | 76.1 | 0.963 | 30.16 | 73.3 | 3.1 | 29
KJ061 | 5 | 2250 | 75 | 72 | 75 | 80.4 | 0.356 | 11.77 | 28.6 | 3.1 | 29
KJ061 | 5 | 2250 | 80 | 72 | 75 | 80.4 | 0.509 | 16.83 | 40.9 | 3.1 | 29
KJ061 | 5 | 2250 | 85 | 72 | 75 | 80.4 | 0.66 | 21.85 | 53.1 | 3.1 | 29
KJ061 | 5 | 2250 | 90 | 72 | 75 | 80.4 | 0.813 | 26.91 | 65.4 | 3.1 | 29
KJ061 | 5 | 2250 | 65 | 57 | 85 | 70.9 | 0.559 | 16.3 | 39.6 | 3.5 | 29
KJ061 | 5 | 2250 | 70 | 57 | 85 | 70.9 | 0.735 | 21.44 | 52.1 | 3.5 | 29
KJ061 | 5 | 2250 | 75 | 57 | 85 | 70.9 | 0.911 | 26.58 | 64.6 | 3.5 | 29
KJ061 | 5 | 2250 | 80 | 57 | 85 | 70.9 | 1 | 29.18 | 70.9 | 3.5 | 29
KJ061 | 5 | 2250 | 85 | 57 | 85 | 70.9 | 1 | 29.18 | 70.9 | 3.5 | 29
KJ061 | 5 | 2250 | 90 | 57 | 85 | 70.9 | 1 | 29.18 | 70.9 | 3.5 | 29
KJ061 | 5 | 2250 | 65 | 62 | 85 | 71.4 | 0.381 | 11.19 | 27.2 | 3.5 | 29
KJ061 | 5 | 2250 | 70 | 62 | 85 | 71.4 | 0.555 | 16.3 | 39.6 | 3.5 | 29
KJ061 | 5 | 2250 | 75 | 62 | 85 | 71.4 | 0.727 | 21.36 | 51.9 | 3.5 | 29
KJ061 | 5 | 2250 | 80 | 62 | 85 | 71.4 | 0.902 | 26.5 | 64.4 | 3.5 | 29
KJ061 | 5 | 2250 | 85 | 62 | 85 | 71.4 | 0.955 | 28.07 | 68.2 | 3.5 | 29
KJ061 | 5 | 2250 | 90 | 62 | 85 | 71.4 | 0.992 | 29.14 | 70.8 | 3.5 | 29
KJ061 | 5 | 2250 | 70 | 67 | 85 | 71.8 | 0.379 | 11.19 | 27.2 | 3.5 | 29
KJ061 | 5 | 2250 | 75 | 67 | 85 | 71.8 | 0.55 | 16.26 | 39.5 | 3.5 | 29
KJ061 | 5 | 2250 | 80 | 67 | 85 | 71.8 | 0.721 | 21.32 | 51.8 | 3.5 | 29
KJ061 | 5 | 2250 | 85 | 67 | 85 | 71.8 | 0.857 | 25.31 | 61.5 | 3.5 | 29
KJ061 | 5 | 2250 | 90 | 67 | 85 | 71.8 | 0.985 | 29.09 | 70.7 | 3.5 | 29
KJ061 | 5 | 2250 | 75 | 72 | 85 | 75.9 | 0.356 | 11.11 | 27 | 3.5 | 29
KJ061 | 5 | 2250 | 80 | 72 | 85 | 75.9 | 0.516 | 16.13 | 39.2 | 3.5 | 29
KJ061 | 5 | 2250 | 85 | 72 | 85 | 75.9 | 0.679 | 21.19 | 51.5 | 3.5 | 29
KJ061 | 5 | 2250 | 90 | 72 | 85 | 75.9 | 0.839 | 26.21 | 63.7 | 3.5 | 29
KJ061 | 5 | 2250 | 65 | 57 | 95 | 67.4 | 0.568 | 15.76 | 38.3 | 3.9 | 29
KJ061 | 5 | 2250 | 70 | 57 | 95 | 67.4 | 0.748 | 20.74 | 50.4 | 3.9 | 29
KJ061 | 5 | 2250 | 75 | 57 | 95 | 67.4 | 0.929 | 25.76 | 62.6 | 3.9 | 29
KJ061 | 5 | 2250 | 80 | 57 | 95 | 67.4 | 1 | 27.74 | 67.4 | 3.9 | 29
KJ061 | 5 | 2250 | 85 | 57 | 95 | 67.4 | 1 | 27.74 | 67.4 | 3.9 | 29
KJ061 | 5 | 2250 | 90 | 57 | 95 | 67.4 | 1 | 27.74 | 67.4 | 3.9 | 29
KJ061 | 5 | 2250 | 65 | 62 | 95 | 67.5 | 0.382 | 10.62 | 25.8 | 3.9 | 29
KJ061 | 5 | 2250 | 70 | 62 | 95 | 67.5 | 0.563 | 15.64 | 38 | 3.9 | 29
KJ061 | 5 | 2250 | 75 | 62 | 95 | 67.5 | 0.742 | 20.62 | 50.1 | 3.9 | 29
KJ061 | 5 | 2250 | 80 | 62 | 95 | 67.5 | 0.923 | 25.64 | 62.3 | 3.9 | 29
KJ061 | 5 | 2250 | 85 | 62 | 95 | 67.5 | 0.975 | 27.08 | 65.8 | 3.9 | 29
KJ061 | 5 | 2250 | 90 | 62 | 95 | 67.5 | 1 | 27.78 | 67.5 | 3.9 | 29
KJ061 | 5 | 2250 | 70 | 67 | 95 | 67.5 | 0.378 | 10.49 | 25.5 | 3.9 | 29
KJ061 | 5 | 2250 | 75 | 67 | 95 | 67.5 | 0.559 | 15.51 | 37.7 | 3.9 | 29
KJ061 | 5 | 2250 | 80 | 67 | 95 | 67.5 | 0.739 | 20.53 | 49.9 | 3.9 | 29
KJ061 | 5 | 2250 | 85 | 67 | 95 | 67.5 | 0.881 | 24.49 | 59.5 | 3.9 | 29
KJ061 | 5 | 2250 | 90 | 67 | 95 | 67.5 | 1 | 27.78 | 67.5 | 3.9 | 29
KJ061 | 5 | 2250 | 75 | 72 | 95 | 71.3 | 0.355 | 10.41 | 25.3 | 3.9 | 29
KJ061 | 5 | 2250 | 80 | 72 | 95 | 71.3 | 0.526 | 15.43 | 37.5 | 3.9 | 29
KJ061 | 5 | 2250 | 85 | 72 | 95 | 71.3 | 0.698 | 20.49 | 49.8 | 3.9 | 29
KJ061 | 5 | 2250 | 90 | 72 | 95 | 71.3 | 0.871 | 25.56 | 62.1 | 3.9 | 29
KJ061 | 5 | 2250 | 65 | 57 | 105 | 64 | 0.558 | 14.69 | 35.7 | 4.5 | 29
KJ061 | 5 | 2250 | 70 | 57 | 105 | 64 | 0.75 | 19.75 | 48 | 4.5 | 29
KJ061 | 5 | 2250 | 75 | 57 | 105 | 64 | 0.944 | 24.86 | 60.4 | 4.5 | 29
KJ061 | 5 | 2250 | 80 | 57 | 105 | 64 | 1 | 26.34 | 64 | 4.5 | 29
KJ061 | 5 | 2250 | 85 | 57 | 105 | 64 | 1 | 26.34 | 64 | 4.5 | 29
KJ061 | 5 | 2250 | 90 | 57 | 105 | 64 | 1 | 26.34 | 64 | 4.5 | 29
KJ061 | 5 | 2250 | 65 | 62 | 105 | 64.1 | 0.362 | 9.55 | 23.2 | 4.5 | 29
KJ061 | 5 | 2250 | 70 | 62 | 105 | 64.1 | 0.555 | 14.65 | 35.6 | 4.5 | 29
KJ061 | 5 | 2250 | 75 | 62 | 105 | 64.1 | 0.747 | 19.71 | 47.9 | 4.5 | 29
KJ061 | 5 | 2250 | 80 | 62 | 105 | 64.1 | 0.941 | 24.81 | 60.3 | 4.5 | 29
KJ061 | 5 | 2250 | 85 | 62 | 105 | 64.1 | 0.98 | 25.84 | 62.8 | 4.5 | 29
KJ061 | 5 | 2250 | 90 | 62 | 105 | 64.1 | 1 | 26.38 | 64.1 | 4.5 | 29
KJ061 | 5 | 2250 | 70 | 67 | 105 | 64.3 | 0.359 | 9.51 | 23.1 | 4.5 | 29
KJ061 | 5 | 2250 | 75 | 67 | 105 | 64.3 | 0.551 | 14.57 | 35.4 | 4.5 | 29
KJ061 | 5 | 2250 | 80 | 67 | 105 | 64.3 | 0.742 | 19.63 | 47.7 | 4.5 | 29
KJ061 | 5 | 2250 | 85 | 67 | 105 | 64.3 | 0.877 | 23.21 | 56.4 | 4.5 | 29
KJ061 | 5 | 2250 | 90 | 67 | 105 | 64.3 | 1 | 26.46 | 64.3 | 4.5 | 29
KJ061 | 5 | 2250 | 75 | 72 | 105 | 66.9 | 0.342 | 9.42 | 22.9 | 4.5 | 29
KJ061 | 5 | 2250 | 80 | 72 | 105 | 66.9 | 0.526 | 14.49 | 35.2 | 4.5 | 29
KJ061 | 5 | 2250 | 85 | 72 | 105 | 66.9 | 0.709 | 19.51 | 47.4 | 4.5 | 29
KJ061 | 5 | 2250 | 90 | 72 | 105 | 66.9 | 0.892 | 24.57 | 59.7 | 4.5 | 29
KJ061 | 5 | 2250 | 65 | 57 | 115 | 60.6 | 0.545 | 13.58 | 33 | 5.1 | 30
KJ061 | 5 | 2250 | 70 | 57 | 115 | 60.6 | 0.754 | 18.81 | 45.7 | 5.1 | 30
KJ061 | 5 | 2250 | 75 | 57 | 115 | 60.6 | 0.962 | 23.99 | 58.3 | 5.1 | 30
KJ061 | 5 | 2250 | 80 | 57 | 115 | 60.6 | 1 | 24.94 | 60.6 | 5.1 | 30
KJ061 | 5 | 2250 | 85 | 57 | 115 | 60.6 | 1 | 24.94 | 60.6 | 5.1 | 30
KJ061 | 5 | 2250 | 90 | 57 | 115 | 60.6 | 1 | 24.94 | 60.6 | 5.1 | 30
KJ061 | 5 | 2250 | 65 | 62 | 115 | 60.6 | 0.342 | 8.52 | 20.7 | 5.1 | 30
KJ061 | 5 | 2250 | 70 | 62 | 115 | 60.6 | 0.548 | 13.66 | 33.2 | 5.1 | 30
KJ061 | 5 | 2250 | 75 | 62 | 115 | 60.6 | 0.754 | 18.81 | 45.7 | 5.1 | 30
KJ061 | 5 | 2250 | 80 | 62 | 115 | 60.6 | 0.96 | 23.95 | 58.2 | 5.1 | 30
KJ061 | 5 | 2250 | 85 | 62 | 115 | 60.6 | 0.987 | 24.61 | 59.8 | 5.1 | 30
KJ061 | 5 | 2250 | 90 | 62 | 115 | 60.6 | 1 | 24.94 | 60.6 | 5.1 | 30
KJ061 | 5 | 2250 | 70 | 67 | 115 | 60.7 | 0.343 | 8.56 | 20.8 | 5.1 | 30
KJ061 | 5 | 2250 | 75 | 67 | 115 | 60.7 | 0.547 | 13.66 | 33.2 | 5.1 | 30
KJ061 | 5 | 2250 | 80 | 67 | 115 | 60.7 | 0.75 | 18.72 | 45.5 | 5.1 | 30
KJ061 | 5 | 2250 | 85 | 67 | 115 | 60.7 | 0.88 | 21.98 | 53.4 | 5.1 | 30
KJ061 | 5 | 2250 | 90 | 67 | 115 | 60.7 | 1 | 24.98 | 60.7 | 5.1 | 30
KJ061 | 5 | 2250 | 75 | 72 | 115 | 62.5 | 0.33 | 8.48 | 20.6 | 5.1 | 30
KJ061 | 5 | 2250 | 80 | 72 | 115 | 62.5 | 0.525 | 13.5 | 32.8 | 5.1 | 30
KJ061 | 5 | 2250 | 85 | 72 | 115 | 62.5 | 0.722 | 18.56 | 45.1 | 5.1 | 30
KJ061 | 5 | 2250 | 90 | 72 | 115 | 62.5 | 0.917 | 23.58 | 57.3 | 5.1 | 30
KJ061 | 5 | 2250 | 65 | 57 | 125 | 57.1 | 0.532 | 12.51 | 30.4 | 5.7 | 30
KJ061 | 5 | 2250 | 70 | 57 | 125 | 57.1 | 0.758 | 17.82 | 43.3 | 5.7 | 30
KJ061 | 5 | 2250 | 75 | 57 | 125 | 57.1 | 0.984 | 23.13 | 56.2 | 5.7 | 30
KJ061 | 5 | 2250 | 80 | 57 | 125 | 57.1 | 1 | 23.5 | 57.1 | 5.7 | 30
KJ061 | 5 | 2250 | 85 | 57 | 125 | 57.1 | 1 | 23.5 | 57.1 | 5.7 | 30
KJ061 | 5 | 2250 | 90 | 57 | 125 | 57.1 | 1 | 23.5 | 57.1 | 5.7 | 30
KJ061 | 5 | 2250 | 65 | 62 | 125 | 57.1 | 0.319 | 7.49 | 18.2 | 5.7 | 30
KJ061 | 5 | 2250 | 70 | 62 | 125 | 57.1 | 0.541 | 12.72 | 30.9 | 5.7 | 30
KJ061 | 5 | 2250 | 75 | 62 | 125 | 57.1 | 0.762 | 17.9 | 43.5 | 5.7 | 30
KJ061 | 5 | 2250 | 80 | 62 | 125 | 57.1 | 0.984 | 23.13 | 56.2 | 5.7 | 30
KJ061 | 5 | 2250 | 85 | 62 | 125 | 57.1 | 0.995 | 23.37 | 56.8 | 5.7 | 30
KJ061 | 5 | 2250 | 90 | 62 | 125 | 57.1 | 1 | 23.5 | 57.1 | 5.7 | 30
KJ061 | 5 | 2250 | 70 | 67 | 125 | 57.2 | 0.323 | 7.61 | 18.5 | 5.7 | 30
KJ061 | 5 | 2250 | 75 | 67 | 125 | 57.2 | 0.54 | 12.72 | 30.9 | 5.7 | 30
KJ061 | 5 | 2250 | 80 | 67 | 125 | 57.2 | 0.759 | 17.86 | 43.4 | 5.7 | 30
KJ061 | 5 | 2250 | 85 | 67 | 125 | 57.2 | 0.879 | 20.7 | 50.3 | 5.7 | 30
KJ061 | 5 | 2250 | 90 | 67 | 125 | 57.2 | 1 | 23.54 | 57.2 | 5.7 | 30
KJ061 | 5 | 2250 | 75 | 72 | 125 | 58.1 | 0.315 | 7.53 | 18.3 | 5.7 | 30
KJ061 | 5 | 2250 | 80 | 72 | 125 | 58.1 | 0.525 | 12.55 | 30.5 | 5.7 | 30
KJ061 | 5 | 2250 | 85 | 72 | 125 | 58.1 | 0.735 | 17.57 | 42.7 | 5.7 | 30
KJ061 | 5 | 2250 | 90 | 72 | 125 | 58.1 | 0.947 | 22.63 | 55 | 5.7 | 30
KJ061 | 5 | 2500 | 65 | 57 | 75 | 78.6 | 0.545 | 15.85 | 42.8 | 3.1 | 29
KJ061 | 5 | 2500 | 70 | 57 | 75 | 78.6 | 0.725 | 21.11 | 57 | 3.1 | 29
KJ061 | 5 | 2500 | 75 | 57 | 75 | 78.6 | 0.906 | 26.37 | 71.2 | 3.1 | 29
KJ061 | 5 | 2500 | 80 | 57 | 75 | 78.6 | 0.99 | 28.81 | 77.8 | 3.1 | 29
KJ061 | 5 | 2500 | 85 | 57 | 75 | 78.6 | 0.99 | 28.81 | 77.8 | 3.1 | 29
KJ061 | 5 | 2500 | 90 | 57 | 75 | 78.6 | 0.99 | 28.81 | 77.8 | 3.1 | 29
KJ061 | 5 | 2500 | 65 | 62 | 75 | 78.7 | 0.372 | 10.85 | 29.3 | 3.1 | 29
KJ061 | 5 | 2500 | 70 | 62 | 75 | 78.7 | 0.55 | 16.04 | 43.3 | 3.1 | 29
KJ061 | 5 | 2500 | 75 | 62 | 75 | 78.7 | 0.727 | 21.19 | 57.2 | 3.1 | 29
KJ061 | 5 | 2500 | 80 | 62 | 75 | 78.7 | 0.905 | 26.37 | 71.2 | 3.1 | 29
KJ061 | 5 | 2500 | 85 | 62 | 75 | 78.7 | 0.947 | 27.59 | 74.5 | 3.1 | 29
KJ061 | 5 | 2500 | 90 | 62 | 75 | 78.7 | 0.989 | 28.81 | 77.8 | 3.1 | 29
KJ061 | 5 | 2500 | 70 | 67 | 75 | 78.8 | 0.374 | 10.93 | 29.5 | 3.1 | 29
KJ061 | 5 | 2500 | 75 | 67 | 75 | 78.8 | 0.549 | 16.04 | 43.3 | 3.1 | 29
KJ061 | 5 | 2500 | 80 | 67 | 75 | 78.8 | 0.725 | 21.15 | 57.1 | 3.1 | 29
KJ061 | 5 | 2500 | 85 | 67 | 75 | 78.8 | 0.855 | 24.96 | 67.4 | 3.1 | 29
KJ061 | 5 | 2500 | 90 | 67 | 75 | 78.8 | 0.986 | 28.78 | 77.7 | 3.1 | 29
KJ061 | 5 | 2500 | 75 | 72 | 75 | 82.4 | 0.356 | 10.85 | 29.3 | 3.1 | 29
KJ061 | 5 | 2500 | 80 | 72 | 75 | 82.4 | 0.521 | 15.89 | 42.9 | 3.1 | 29
KJ061 | 5 | 2500 | 85 | 72 | 75 | 82.4 | 0.686 | 20.93 | 56.5 | 3.1 | 29
KJ061 | 5 | 2500 | 90 | 72 | 75 | 82.4 | 0.851 | 25.96 | 70.1 | 3.1 | 29
KJ061 | 5 | 2500 | 65 | 57 | 85 | 74 | 0.562 | 15.41 | 41.6 | 3.5 | 29
KJ061 | 5 | 2500 | 70 | 57 | 85 | 74 | 0.75 | 20.56 | 55.5 | 3.5 | 29
KJ061 | 5 | 2500 | 75 | 57 | 85 | 74 | 0.936 | 25.67 | 69.3 | 3.5 | 29
KJ061 | 5 | 2500 | 80 | 57 | 85 | 74 | 1 | 27.41 | 74 | 3.5 | 29
KJ061 | 5 | 2500 | 85 | 57 | 85 | 74 | 1 | 27.41 | 74 | 3.5 | 29
KJ061 | 5 | 2500 | 90 | 57 | 85 | 74 | 1 | 27.41 | 74 | 3.5 | 29
KJ061 | 5 | 2500 | 65 | 62 | 85 | 74.1 | 0.377 | 10.33 | 27.9 | 3.5 | 29
KJ061 | 5 | 2500 | 70 | 62 | 85 | 74.1 | 0.561 | 15.41 | 41.6 | 3.5 | 29
KJ061 | 5 | 2500 | 75 | 62 | 85 | 74.1 | 0.748 | 20.52 | 55.4 | 3.5 | 29
KJ061 | 5 | 2500 | 80 | 62 | 85 | 74.1 | 0.934 | 25.63 | 69.2 | 3.5 | 29
KJ061 | 5 | 2500 | 85 | 62 | 85 | 74.1 | 0.973 | 26.7 | 72.1 | 3.5 | 29
KJ061 | 5 | 2500 | 90 | 62 | 85 | 74.1 | 0.999 | 27.41 | 74 | 3.5 | 29
KJ061 | 5 | 2500 | 70 | 67 | 85 | 74.2 | 0.375 | 10.3 | 27.8 | 3.5 | 29
KJ061 | 5 | 2500 | 75 | 67 | 85 | 74.2 | 0.558 | 15.33 | 41.4 | 3.5 | 29
KJ061 | 5 | 2500 | 80 | 67 | 85 | 74.2 | 0.743 | 20.41 | 55.1 | 3.5 | 29
KJ061 | 5 | 2500 | 85 | 67 | 85 | 74.2 | 0.879 | 24.15 | 65.2 | 3.5 | 29
KJ061 | 5 | 2500 | 90 | 67 | 85 | 74.2 | 0.997 | 27.41 | 74 | 3.5 | 29
KJ061 | 5 | 2500 | 75 | 72 | 85 | 77.6 | 0.354 | 10.19 | 27.5 | 3.5 | 29
KJ061 | 5 | 2500 | 80 | 72 | 85 | 77.6 | 0.53 | 15.22 | 41.1 | 3.5 | 29
KJ061 | 5 | 2500 | 85 | 72 | 85 | 77.6 | 0.705 | 20.26 | 54.7 | 3.5 | 29
KJ061 | 5 | 2500 | 90 | 72 | 85 | 77.6 | 0.88 | 25.3 | 68.3 | 3.5 | 29
KJ061 | 5 | 2500 | 65 | 57 | 95 | 70.6 | 0.572 | 14.96 | 40.4 | 4 | 29
KJ061 | 5 | 2500 | 70 | 57 | 95 | 70.6 | 0.763 | 19.96 | 53.9 | 4 | 29
KJ061 | 5 | 2500 | 75 | 57 | 95 | 70.6 | 0.956 | 25 | 67.5 | 4 | 29
KJ061 | 5 | 2500 | 80 | 57 | 95 | 70.6 | 1 | 26.15 | 70.6 | 4 | 29
KJ061 | 5 | 2500 | 85 | 57 | 95 | 70.6 | 1 | 26.15 | 70.6 | 4 | 29
KJ061 | 5 | 2500 | 90 | 57 | 95 | 70.6 | 1 | 26.15 | 70.6 | 4 | 29
KJ061 | 5 | 2500 | 65 | 62 | 95 | 70.6 | 0.374 | 9.78 | 26.4 | 4 | 29
KJ061 | 5 | 2500 | 70 | 62 | 95 | 70.6 | 0.567 | 14.81 | 40 | 4 | 29
KJ061 | 5 | 2500 | 75 | 62 | 95 | 70.6 | 0.758 | 19.81 | 53.5 | 4 | 29
KJ061 | 5 | 2500 | 80 | 62 | 95 | 70.6 | 0.95 | 24.85 | 67.1 | 4 | 29
KJ061 | 5 | 2500 | 85 | 62 | 95 | 70.6 | 0.987 | 25.81 | 69.7 | 4 | 29
KJ061 | 5 | 2500 | 90 | 62 | 95 | 70.6 | 1 | 26.15 | 70.6 | 4 | 29
KJ061 | 5 | 2500 | 70 | 67 | 95 | 70.7 | 0.368 | 9.63 | 26 | 3.9 | 29
KJ061 | 5 | 2500 | 75 | 67 | 95 | 70.7 | 0.56 | 14.67 | 39.6 | 3.9 | 29
KJ061 | 5 | 2500 | 80 | 67 | 95 | 70.7 | 0.752 | 19.7 | 53.2 | 3.9 | 29
KJ061 | 5 | 2500 | 85 | 67 | 95 | 70.7 | 0.891 | 23.33 | 63 | 3.9 | 29
KJ061 | 5 | 2500 | 90 | 67 | 95 | 70.7 | 1 | 26.19 | 70.7 | 3.9 | 29
KJ061 | 5 | 2500 | 75 | 72 | 95 | 72.7 | 0.354 | 9.52 | 25.7 | 3.9 | 29
KJ061 | 5 | 2500 | 80 | 72 | 95 | 72.7 | 0.541 | 14.56 | 39.3 | 3.9 | 29
KJ061 | 5 | 2500 | 85 | 72 | 95 | 72.7 | 0.728 | 19.59 | 52.9 | 3.9 | 29
KJ061 | 5 | 2500 | 90 | 72 | 95 | 72.7 | 0.915 | 24.63 | 66.5 | 3.9 | 29
KJ061 | 5 | 2500 | 65 | 57 | 105 | 66.4 | 0.568 | 13.96 | 37.7 | 4.5 | 29
KJ061 | 5 | 2500 | 70 | 57 | 105 | 66.4 | 0.776 | 19.07 | 51.5 | 4.5 | 29
KJ061 | 5 | 2500 | 75 | 57 | 105 | 66.4 | 0.982 | 24.15 | 65.2 | 4.5 | 29
KJ061 | 5 | 2500 | 80 | 57 | 105 | 66.4 | 1 | 24.59 | 66.4 | 4.5 | 29
KJ061 | 5 | 2500 | 85 | 57 | 105 | 66.4 | 1 | 24.59 | 66.4 | 4.5 | 29
KJ061 | 5 | 2500 | 90 | 57 | 105 | 66.4 | 1 | 24.59 | 66.4 | 4.5 | 29
KJ061 | 5 | 2500 | 65 | 62 | 105 | 66.4 | 0.358 | 8.81 | 23.8 | 4.5 | 29
KJ061 | 5 | 2500 | 70 | 62 | 105 | 66.4 | 0.565 | 13.89 | 37.5 | 4.5 | 29
KJ061 | 5 | 2500 | 75 | 62 | 105 | 66.4 | 0.771 | 18.96 | 51.2 | 4.5 | 29
KJ061 | 5 | 2500 | 80 | 62 | 105 | 66.4 | 0.977 | 24.04 | 64.9 | 4.5 | 29
KJ061 | 5 | 2500 | 85 | 62 | 105 | 66.4 | 1 | 24.59 | 66.4 | 4.5 | 29
KJ061 | 5 | 2500 | 90 | 62 | 105 | 66.4 | 1 | 24.59 | 66.4 | 4.5 | 29
KJ061 | 5 | 2500 | 70 | 67 | 105 | 66.5 | 0.355 | 8.74 | 23.6 | 4.5 | 29
KJ061 | 5 | 2500 | 75 | 67 | 105 | 66.5 | 0.559 | 13.78 | 37.2 | 4.5 | 29
KJ061 | 5 | 2500 | 80 | 67 | 105 | 66.5 | 0.765 | 18.85 | 50.9 | 4.5 | 29
KJ061 | 5 | 2500 | 85 | 67 | 105 | 66.5 | 0.896 | 22.07 | 59.6 | 4.5 | 29
KJ061 | 5 | 2500 | 90 | 67 | 105 | 66.5 | 1 | 24.63 | 66.5 | 4.5 | 29
KJ061 | 5 | 2500 | 75 | 72 | 105 | 68.2 | 0.34 | 8.59 | 23.2 | 4.5 | 29
KJ061 | 5 | 2500 | 80 | 72 | 105 | 68.2 | 0.54 | 13.63 | 36.8 | 4.5 | 29
KJ061 | 5 | 2500 | 85 | 72 | 105 | 68.2 | 0.739 | 18.67 | 50.4 | 4.5 | 29
KJ061 | 5 | 2500 | 90 | 72 | 105 | 68.2 | 0.938 | 23.7 | 64 | 4.5 | 29
KJ061 | 5 | 2500 | 65 | 57 | 115 | 62.2 | 0.561 | 12.93 | 34.9 | 5.1 | 30
KJ061 | 5 | 2500 | 70 | 57 | 115 | 62.2 | 0.788 | 18.15 | 49 | 5.1 | 30
KJ061 | 5 | 2500 | 75 | 57 | 115 | 62.2 | 1 | 23.04 | 62.2 | 5.1 | 30
KJ061 | 5 | 2500 | 80 | 57 | 115 | 62.2 | 1 | 23.04 | 62.2 | 5.1 | 30
KJ061 | 5 | 2500 | 85 | 57 | 115 | 62.2 | 1 | 23.04 | 62.2 | 5.1 | 30
KJ061 | 5 | 2500 | 90 | 57 | 115 | 62.2 | 1 | 23.04 | 62.2 | 5.1 | 30
KJ061 | 5 | 2500 | 65 | 62 | 115 | 62.2 | 0.339 | 7.81 | 21.1 | 5.1 | 30
KJ061 | 5 | 2500 | 70 | 62 | 115 | 62.2 | 0.563 | 12.96 | 35 | 5.1 | 30
KJ061 | 5 | 2500 | 75 | 62 | 115 | 62.2 | 0.786 | 18.11 | 48.9 | 5.1 | 30
KJ061 | 5 | 2500 | 80 | 62 | 115 | 62.2 | 1 | 23.04 | 62.2 | 5.1 | 30
KJ061 | 5 | 2500 | 85 | 62 | 115 | 62.2 | 1 | 23.04 | 62.2 | 5.1 | 30
KJ061 | 5 | 2500 | 90 | 62 | 115 | 62.2 | 1 | 23.04 | 62.2 | 5.1 | 30
KJ061 | 5 | 2500 | 70 | 67 | 115 | 62.3 | 0.339 | 7.81 | 21.1 | 5.1 | 30
KJ061 | 5 | 2500 | 75 | 67 | 115 | 62.3 | 0.559 | 12.89 | 34.8 | 5.1 | 30
KJ061 | 5 | 2500 | 80 | 67 | 115 | 62.3 | 0.78 | 18 | 48.6 | 5.1 | 30
KJ061 | 5 | 2500 | 85 | 67 | 115 | 62.3 | 0.904 | 20.85 | 56.3 | 5.1 | 30
KJ061 | 5 | 2500 | 90 | 67 | 115 | 62.3 | 1 | 23.07 | 62.3 | 5.1 | 30
KJ061 | 5 | 2500 | 75 | 72 | 115 | 63.7 | 0.327 | 7.7 | 20.8 | 5.1 | 30
KJ061 | 5 | 2500 | 80 | 72 | 115 | 63.7 | 0.54 | 12.74 | 34.4 | 5.1 | 30
KJ061 | 5 | 2500 | 85 | 72 | 115 | 63.7 | 0.754 | 17.78 | 48 | 5.1 | 30
KJ061 | 5 | 2500 | 90 | 72 | 115 | 63.7 | 0.967 | 22.81 | 61.6 | 5.1 | 30
KJ061 | 5 | 2500 | 65 | 57 | 125 | 57.9 | 0.556 | 11.93 | 32.2 | 5.7 | 30
KJ061 | 5 | 2500 | 70 | 57 | 125 | 57.9 | 0.803 | 17.22 | 46.5 | 5.7 | 30
KJ061 | 5 | 2500 | 75 | 57 | 125 | 57.9 | 1 | 21.44 | 57.9 | 5.7 | 30
KJ061 | 5 | 2500 | 80 | 57 | 125 | 57.9 | 1 | 21.44 | 57.9 | 5.7 | 30
KJ061 | 5 | 2500 | 85 | 57 | 125 | 57.9 | 1 | 21.44 | 57.9 | 5.7 | 30
KJ061 | 5 | 2500 | 90 | 57 | 125 | 57.9 | 1 | 21.44 | 57.9 | 5.7 | 30
KJ061 | 5 | 2500 | 65 | 62 | 125 | 58.3 | 0.317 | 6.85 | 18.5 | 5.7 | 30
KJ061 | 5 | 2500 | 70 | 62 | 125 | 58.3 | 0.559 | 12.07 | 32.6 | 5.7 | 30
KJ061 | 5 | 2500 | 75 | 62 | 125 | 58.3 | 0.799 | 17.26 | 46.6 | 5.7 | 30
KJ061 | 5 | 2500 | 80 | 62 | 125 | 58.3 | 0.991 | 21.41 | 57.8 | 5.7 | 30
KJ061 | 5 | 2500 | 85 | 62 | 125 | 58.3 | 0.991 | 21.41 | 57.8 | 5.7 | 30
KJ061 | 5 | 2500 | 90 | 62 | 125 | 58.3 | 0.991 | 21.41 | 57.8 | 5.7 | 30
KJ061 | 5 | 2500 | 70 | 67 | 125 | 58.6 | 0.317 | 6.89 | 18.6 | 5.7 | 30
KJ061 | 5 | 2500 | 75 | 67 | 125 | 58.6 | 0.555 | 12.04 | 32.5 | 5.7 | 30
KJ061 | 5 | 2500 | 80 | 67 | 125 | 58.6 | 0.79 | 17.15 | 46.3 | 5.7 | 30
KJ061 | 5 | 2500 | 85 | 67 | 125 | 58.6 | 0.903 | 19.59 | 52.9 | 5.7 | 30
KJ061 | 5 | 2500 | 90 | 67 | 125 | 58.6 | 0.985 | 21.37 | 57.7 | 5.7 | 30
KJ061 | 5 | 2500 | 75 | 72 | 125 | 59.3 | 0.309 | 6.78 | 18.3 | 5.7 | 30
KJ061 | 5 | 2500 | 80 | 72 | 125 | 59.3 | 0.538 | 11.81 | 31.9 | 5.7 | 30
KJ061 | 5 | 2500 | 85 | 72 | 125 | 59.3 | 0.767 | 16.85 | 45.5 | 5.7 | 30
KJ061 | 5 | 2500 | 90 | 72 | 125 | 59.3 | 0.997 | 21.89 | 59.1 | 5.7 | 30
KJ078 | 6.5 | 1625 | 65 | 62 | 75 | 72.2 | 0.442 | 18.18 | 31.9 | 4.6 | 31
KJ078 | 6.5 | 1625 | 70 | 62 | 75 | 72.2 | 0.564 | 23.19 | 40.7 | 4.6 | 31
KJ078 | 6.5 | 1625 | 75 | 62 | 75 | 72.2 | 0.662 | 27.24 | 47.8 | 4.6 | 31
KJ078 | 6.5 | 1625 | 80 | 62 | 75 | 72.2 | 0.809 | 33.28 | 58.4 | 4.6 | 31
KJ078 | 6.5 | 1625 | 85 | 62 | 75 | 72.2 | 0.91 | 37.44 | 65.7 | 4.6 | 31
KJ078 | 6.5 | 1625 | 90 | 62 | 75 | 72.2 | 1 | 41.14 | 72.2 | 4.6 | 31
KJ078 | 6.5 | 1625 | 70 | 67 | 75 | 82.3 | 0.42 | 19.72 | 34.6 | 4.5 | 31
KJ078 | 6.5 | 1625 | 75 | 67 | 75 | 82.3 | 0.513 | 24.05 | 42.2 | 4.5 | 31
KJ078 | 6.5 | 1625 | 80 | 67 | 75 | 82.3 | 0.617 | 28.95 | 50.8 | 4.5 | 31
KJ078 | 6.5 | 1625 | 85 | 67 | 75 | 82.3 | 0.707 | 33.16 | 58.2 | 4.5 | 31
KJ078 | 6.5 | 1625 | 90 | 67 | 75 | 82.3 | 0.796 | 37.32 | 65.5 | 4.5 | 31
KJ078 | 6.5 | 1625 | 75 | 72 | 75 | 91.8 | 0.391 | 20.46 | 35.9 | 4.4 | 31
KJ078 | 6.5 | 1625 | 80 | 72 | 75 | 91.8 | 0.471 | 24.62 | 43.2 | 4.4 | 31
KJ078 | 6.5 | 1625 | 85 | 72 | 75 | 91.8 | 0.551 | 28.83 | 50.6 | 4.4 | 31
KJ078 | 6.5 | 1625 | 90 | 72 | 75 | 91.8 | 0.631 | 32.99 | 57.9 | 4.4 | 31
KJ078 | 6.5 | 1625 | 80 | 77 | 75 | 101.4 | 0.351 | 20.28 | 35.6 | 4.3 | 31
KJ078 | 6.5 | 1625 | 85 | 77 | 75 | 101.4 | 0.424 | 24.5 | 43 | 4.3 | 31
KJ078 | 6.5 | 1625 | 90 | 77 | 75 | 101.4 | 0.496 | 28.66 | 50.3 | 4.3 | 31
KJ078 | 6.5 | 1625 | 65 | 62 | 85 | 69.1 | 0.433 | 17.04 | 29.9 | 5.2 | 31
KJ078 | 6.5 | 1625 | 70 | 62 | 85 | 69.1 | 0.556 | 21.88 | 38.4 | 5.2 | 31
KJ078 | 6.5 | 1625 | 75 | 62 | 85 | 69.1 | 0.667 | 26.27 | 46.1 | 5.2 | 31
KJ078 | 6.5 | 1625 | 80 | 62 | 85 | 69.1 | 0.802 | 31.57 | 55.4 | 5.2 | 31
KJ078 | 6.5 | 1625 | 85 | 62 | 85 | 69.1 | 0.915 | 36.01 | 63.2 | 5.2 | 31
KJ078 | 6.5 | 1625 | 90 | 62 | 85 | 69.1 | 1 | 39.37 | 69.1 | 5.2 | 31
KJ078 | 6.5 | 1625 | 70 | 67 | 85 | 77.3 | 0.405 | 17.83 | 31.3 | 5.2 | 31
KJ078 | 6.5 | 1625 | 75 | 67 | 85 | 77.3 | 0.508 | 22.39 | 39.3 | 5.2 | 31
KJ078 | 6.5 | 1625 | 80 | 67 | 85 | 77.3 | 0.618 | 27.24 | 47.8 | 5.2 | 31
KJ078 | 6.5 | 1625 | 85 | 67 | 85 | 77.3 | 0.721 | 31.74 | 55.7 | 5.2 | 31
KJ078 | 6.5 | 1625 | 90 | 67 | 85 | 77.3 | 0.823 | 36.24 | 63.6 | 5.2 | 31
KJ078 | 6.5 | 1625 | 75 | 72 | 85 | 86.9 | 0.369 | 18.29 | 32.1 | 5.1 | 31
KJ078 | 6.5 | 1625 | 80 | 72 | 85 | 86.9 | 0.461 | 22.85 | 40.1 | 5.1 | 31
KJ078 | 6.5 | 1625 | 85 | 72 | 85 | 86.9 | 0.554 | 27.41 | 48.1 | 5.1 | 31
KJ078 | 6.5 | 1625 | 90 | 72 | 85 | 86.9 | 0.644 | 31.91 | 56 | 5.1 | 31
KJ078 | 6.5 | 1625 | 80 | 77 | 85 | 96.5 | 0.336 | 18.46 | 32.4 | 5.1 | 31
KJ078 | 6.5 | 1625 | 85 | 77 | 85 | 96.5 | 0.419 | 23.02 | 40.4 | 5.1 | 31
KJ078 | 6.5 | 1625 | 90 | 77 | 85 | 96.5 | 0.503 | 27.64 | 48.5 | 5.1 | 31
KJ078 | 6.5 | 1625 | 65 | 62 | 95 | 66 | 0.424 | 15.95 | 28 | 5.9 | 31
KJ078 | 6.5 | 1625 | 70 | 62 | 95 | 66 | 0.548 | 20.63 | 36.2 | 5.9 | 31
KJ078 | 6.5 | 1625 | 75 | 62 | 95 | 66 | 0.671 | 25.24 | 44.3 | 5.9 | 31
KJ078 | 6.5 | 1625 | 80 | 62 | 95 | 66 | 0.795 | 29.91 | 52.5 | 5.9 | 31
KJ078 | 6.5 | 1625 | 85 | 62 | 95 | 66 | 0.92 | 34.59 | 60.7 | 5.9 | 31
KJ078 | 6.5 | 1625 | 90 | 62 | 95 | 66 | 1 | 37.61 | 66 | 5.9 | 31
KJ078 | 6.5 | 1625 | 70 | 67 | 95 | 72.4 | 0.385 | 15.9 | 27.9 | 5.9 | 31
KJ078 | 6.5 | 1625 | 75 | 67 | 95 | 72.4 | 0.501 | 20.68 | 36.3 | 5.9 | 31
KJ078 | 6.5 | 1625 | 80 | 67 | 95 | 72.4 | 0.617 | 25.47 | 44.7 | 5.9 | 31
KJ078 | 6.5 | 1625 | 85 | 67 | 95 | 72.4 | 0.735 | 30.31 | 53.2 | 5.9 | 31
KJ078 | 6.5 | 1625 | 90 | 67 | 95 | 72.4 | 0.852 | 35.16 | 61.7 | 5.9 | 31
KJ078 | 6.5 | 1625 | 75 | 72 | 95 | 82 | 0.345 | 16.13 | 28.3 | 5.8 | 31
KJ078 | 6.5 | 1625 | 80 | 72 | 95 | 82 | 0.45 | 21.03 | 36.9 | 5.8 | 31
KJ078 | 6.5 | 1625 | 85 | 72 | 95 | 82 | 0.555 | 25.93 | 45.5 | 5.8 | 31
KJ078 | 6.5 | 1625 | 90 | 72 | 95 | 82 | 0.661 | 30.88 | 54.2 | 5.8 | 31
KJ078 | 6.5 | 1625 | 80 | 77 | 95 | 91.7 | 0.317 | 16.58 | 29.1 | 5.8 | 31
KJ078 | 6.5 | 1625 | 85 | 77 | 95 | 91.7 | 0.413 | 21.6 | 37.9 | 5.8 | 31
KJ078 | 6.5 | 1625 | 90 | 77 | 95 | 91.7 | 0.508 | 26.55 | 46.6 | 5.8 | 31
KJ078 | 6.5 | 1625 | 65 | 62 | 105 | 63 | 0.395 | 14.19 | 24.9 | 6.8 | 31
KJ078 | 6.5 | 1625 | 70 | 62 | 105 | 63 | 0.53 | 19.03 | 33.4 | 6.8 | 31
KJ078 | 6.5 | 1625 | 75 | 62 | 105 | 63 | 0.667 | 23.93 | 42 | 6.8 | 31
KJ078 | 6.5 | 1625 | 80 | 62 | 105 | 63 | 0.802 | 28.77 | 50.5 | 6.8 | 31
KJ078 | 6.5 | 1625 | 85 | 62 | 105 | 63 | 0.924 | 33.16 | 58.2 | 6.8 | 31
KJ078 | 6.5 | 1625 | 90 | 62 | 105 | 63 | 1 | 35.9 | 63 | 6.8 | 31
KJ078 | 6.5 | 1625 | 70 | 67 | 105 | 67.1 | 0.377 | 14.42 | 25.3 | 6.8 | 31
KJ078 | 6.5 | 1625 | 75 | 67 | 105 | 67.1 | 0.505 | 19.32 | 33.9 | 6.8 | 31
KJ078 | 6.5 | 1625 | 80 | 67 | 105 | 67.1 | 0.632 | 24.16 | 42.4 | 6.8 | 31
KJ078 | 6.5 | 1625 | 85 | 67 | 105 | 67.1 | 0.763 | 29.17 | 51.2 | 6.8 | 31
KJ078 | 6.5 | 1625 | 90 | 67 | 105 | 67.1 | 0.893 | 34.13 | 59.9 | 6.8 | 31
KJ078 | 6.5 | 1625 | 75 | 72 | 105 | 76.1 | 0.339 | 14.7 | 25.8 | 6.8 | 31
KJ078 | 6.5 | 1625 | 80 | 72 | 105 | 76.1 | 0.452 | 19.6 | 34.4 | 6.8 | 31
KJ078 | 6.5 | 1625 | 85 | 72 | 105 | 76.1 | 0.565 | 24.5 | 43 | 6.8 | 31
KJ078 | 6.5 | 1625 | 90 | 72 | 105 | 76.1 | 0.678 | 29.4 | 51.6 | 6.8 | 31
KJ078 | 6.5 | 1625 | 80 | 77 | 105 | 85.1 | 0.309 | 14.99 | 26.3 | 6.9 | 31
KJ078 | 6.5 | 1625 | 85 | 77 | 105 | 85.1 | 0.409 | 19.83 | 34.8 | 6.9 | 31
KJ078 | 6.5 | 1625 | 90 | 77 | 105 | 85.1 | 0.509 | 24.67 | 43.3 | 6.9 | 31
KJ078 | 6.5 | 1625 | 65 | 62 | 115 | 60 | 0.362 | 12.36 | 21.7 | 7.7 | 32
KJ078 | 6.5 | 1625 | 70 | 62 | 115 | 60 | 0.512 | 17.49 | 30.7 | 7.7 | 32
KJ078 | 6.5 | 1625 | 75 | 62 | 115 | 60 | 0.66 | 22.56 | 39.6 | 7.7 | 32
KJ078 | 6.5 | 1625 | 80 | 62 | 115 | 60 | 0.808 | 27.64 | 48.5 | 7.7 | 32
KJ078 | 6.5 | 1625 | 85 | 62 | 115 | 60 | 0.928 | 31.74 | 55.7 | 7.7 | 32
KJ078 | 6.5 | 1625 | 90 | 62 | 115 | 60 | 1 | 34.19 | 60 | 7.7 | 32
KJ078 | 6.5 | 1625 | 70 | 67 | 115 | 61.8 | 0.367 | 12.93 | 22.7 | 7.7 | 32
KJ078 | 6.5 | 1625 | 75 | 67 | 115 | 61.8 | 0.508 | 17.89 | 31.4 | 7.7 | 32
KJ078 | 6.5 | 1625 | 80 | 67 | 115 | 61.8 | 0.65 | 22.91 | 40.2 | 7.7 | 32
KJ078 | 6.5 | 1625 | 85 | 67 | 115 | 61.8 | 0.796 | 28.03 | 49.2 | 7.7 | 32
KJ078 | 6.5 | 1625 | 90 | 67 | 115 | 61.8 | 0.942 | 33.16 | 58.2 | 7.7 | 32
KJ078 | 6.5 | 1625 | 75 | 72 | 115 | 70.1 | 0.332 | 13.28 | 23.3 | 7.8 | 32
KJ078 | 6.5 | 1625 | 80 | 72 | 115 | 70.1 | 0.455 | 18.18 | 31.9 | 7.8 | 32
KJ078 | 6.5 | 1625 | 85 | 72 | 115 | 70.1 | 0.576 | 23.02 | 40.4 | 7.8 | 32
KJ078 | 6.5 | 1625 | 90 | 72 | 115 | 70.1 | 0.699 | 27.92 | 49 | 7.8 | 32
KJ078 | 6.5 | 1625 | 80 | 77 | 115 | 78.5 | 0.299 | 13.39 | 23.5 | 7.9 | 32
KJ078 | 6.5 | 1625 | 85 | 77 | 115 | 78.5 | 0.404 | 18.06 | 31.7 | 7.9 | 32
KJ078 | 6.5 | 1625 | 90 | 77 | 115 | 78.5 | 0.508 | 22.74 | 39.9 | 7.9 | 32
KJ078 | 6.5 | 1625 | 65 | 62 | 125 | 56.9 | 0.327 | 10.6 | 18.6 | 8.6 | 32
KJ078 | 6.5 | 1625 | 70 | 62 | 125 | 56.9 | 0.49 | 15.9 | 27.9 | 8.6 | 32
KJ078 | 6.5 | 1625 | 75 | 62 | 125 | 56.9 | 0.656 | 21.25 | 37.3 | 8.6 | 32
KJ078 | 6.5 | 1625 | 80 | 62 | 125 | 56.9 | 0.819 | 26.55 | 46.6 | 8.6 | 32
KJ078 | 6.5 | 1625 | 85 | 62 | 125 | 56.9 | 0.933 | 30.26 | 53.1 | 8.6 | 32
KJ078 | 6.5 | 1625 | 90 | 62 | 125 | 56.9 | 1 | 32.42 | 56.9 | 8.6 | 32
KJ078 | 6.5 | 1625 | 70 | 67 | 125 | 56.4 | 0.356 | 11.45 | 20.1 | 8.6 | 32
KJ078 | 6.5 | 1625 | 75 | 67 | 125 | 56.4 | 0.514 | 16.52 | 29 | 8.6 | 32
KJ078 | 6.5 | 1625 | 80 | 67 | 125 | 56.4 | 0.674 | 21.65 | 38 | 8.6 | 32
KJ078 | 6.5 | 1625 | 85 | 67 | 125 | 56.4 | 0.837 | 26.89 | 47.2 | 8.6 | 32
KJ078 | 6.5 | 1625 | 90 | 67 | 125 | 56.4 | 1 | 32.14 | 56.4 | 8.6 | 32
KJ078 | 6.5 | 1625 | 75 | 72 | 125 | 64.2 | 0.324 | 11.85 | 20.8 | 8.8 | 32
KJ078 | 6.5 | 1625 | 80 | 72 | 125 | 64.2 | 0.456 | 16.7 | 29.3 | 8.8 | 32
KJ078 | 6.5 | 1625 | 85 | 72 | 125 | 64.2 | 0.59 | 21.6 | 37.9 | 8.8 | 32
KJ078 | 6.5 | 1625 | 90 | 72 | 125 | 64.2 | 0.724 | 26.5 | 46.5 | 8.8 | 32
KJ078 | 6.5 | 1625 | 80 | 77 | 125 | 72 | 0.287 | 11.79 | 20.7 | 8.9 | 32
KJ078 | 6.5 | 1625 | 85 | 77 | 125 | 72 | 0.397 | 16.3 | 28.6 | 8.9 | 32
KJ078 | 6.5 | 1625 | 90 | 77 | 125 | 72 | 0.507 | 20.8 | 36.5 | 8.9 | 32
KJ078 | 6.5 | 1950 | 65 | 57 | 75 | 69.9 | 0.579 | 19.23 | 40.5 | 4.6 | 31
KJ078 | 6.5 | 1950 | 70 | 57 | 75 | 69.9 | 0.73 | 24.22 | 51 | 4.6 | 31
KJ078 | 6.5 | 1950 | 75 | 57 | 75 | 69.9 | 0.881 | 29.25 | 61.6 | 4.6 | 31
KJ078 | 6.5 | 1950 | 80 | 57 | 75 | 69.9 | 1 | 33.19 | 69.9 | 4.6 | 31
KJ078 | 6.5 | 1950 | 85 | 57 | 75 | 69.9 | 1 | 33.19 | 69.9 | 4.6 | 31
KJ078 | 6.5 | 1950 | 90 | 57 | 75 | 69.9 | 1 | 33.19 | 69.9 | 4.6 | 31
KJ078 | 6.5 | 1950 | 65 | 62 | 75 | 77.4 | 0.429 | 15.76 | 33.2 | 4.5 | 31
KJ078 | 6.5 | 1950 | 70 | 62 | 75 | 77.4 | 0.558 | 20.51 | 43.2 | 4.5 | 31
KJ078 | 6.5 | 1950 | 75 | 62 | 75 | 77.4 | 0.671 | 24.64 | 51.9 | 4.5 | 31
KJ078 | 6.5 | 1950 | 80 | 62 | 75 | 77.4 | 0.818 | 30.06 | 63.3 | 4.5 | 31
KJ078 | 6.5 | 1950 | 85 | 62 | 75 | 77.4 | 0.901 | 33.1 | 69.7 | 4.5 | 31
KJ078 | 6.5 | 1950 | 90 | 62 | 75 | 77.4 | 0.901 | 33.1 | 69.7 | 4.5 | 31
KJ078 | 6.5 | 1950 | 70 | 67 | 75 | 84.9 | 0.417 | 16.81 | 35.4 | 4.4 | 31
KJ078 | 6.5 | 1950 | 75 | 67 | 75 | 84.9 | 0.525 | 21.18 | 44.6 | 4.4 | 31
KJ078 | 6.5 | 1950 | 80 | 67 | 75 | 84.9 | 0.642 | 25.88 | 54.5 | 4.4 | 31
KJ078 | 6.5 | 1950 | 85 | 67 | 75 | 84.9 | 0.744 | 30.01 | 63.2 | 4.4 | 31
KJ078 | 6.5 | 1950 | 90 | 67 | 75 | 84.9 | 0.816 | 32.91 | 69.3 | 4.4 | 31
KJ078 | 6.5 | 1950 | 75 | 72 | 75 | 94.6 | 0.387 | 17.38 | 36.6 | 4.4 | 31
KJ078 | 6.5 | 1950 | 80 | 72 | 75 | 94.6 | 0.483 | 21.7 | 45.7 | 4.4 | 31
KJ078 | 6.5 | 1950 | 85 | 72 | 75 | 94.6 | 0.578 | 25.97 | 54.7 | 4.4 | 31
KJ078 | 6.5 | 1950 | 90 | 72 | 75 | 94.6 | 0.673 | 30.25 | 63.7 | 4.4 | 31
KJ078 | 6.5 | 1950 | 80 | 77 | 75 | 104.2 | 0.353 | 17.47 | 36.8 | 4.3 | 31
KJ078 | 6.5 | 1950 | 85 | 77 | 75 | 104.2 | 0.443 | 21.94 | 46.2 | 4.3 | 31
KJ078 | 6.5 | 1950 | 90 | 77 | 75 | 104.2 | 0.533 | 26.35 | 55.5 | 4.3 | 31
KJ078 | 6.5 | 1950 | 65 | 57 | 85 | 68.1 | 0.58 | 18.76 | 39.5 | 5.2 | 31
KJ078 | 6.5 | 1950 | 70 | 57 | 85 | 68.1 | 0.728 | 23.55 | 49.6 | 5.2 | 31
KJ078 | 6.5 | 1950 | 75 | 57 | 85 | 68.1 | 0.877 | 28.35 | 59.7 | 5.2 | 31
KJ078 | 6.5 | 1950 | 80 | 57 | 85 | 68.1 | 1 | 32.34 | 68.1 | 5.2 | 31
KJ078 | 6.5 | 1950 | 85 | 57 | 85 | 68.1 | 1 | 32.34 | 68.1 | 5.2 | 31
KJ078 | 6.5 | 1950 | 90 | 57 | 85 | 68.1 | 1 | 32.34 | 68.1 | 5.2 | 31
KJ078 | 6.5 | 1950 | 65 | 62 | 85 | 74 | 0.418 | 14.67 | 30.9 | 5.2 | 31
KJ078 | 6.5 | 1950 | 70 | 62 | 85 | 74 | 0.551 | 19.37 | 40.8 | 5.2 | 31
KJ078 | 6.5 | 1950 | 75 | 62 | 85 | 74 | 0.677 | 23.79 | 50.1 | 5.2 | 31
KJ078 | 6.5 | 1950 | 80 | 62 | 85 | 74 | 0.82 | 28.82 | 60.7 | 5.2 | 31
KJ078 | 6.5 | 1950 | 85 | 62 | 85 | 74 | 0.918 | 32.24 | 67.9 | 5.2 | 31
KJ078 | 6.5 | 1950 | 90 | 62 | 85 | 74 | 0.919 | 32.29 | 68 | 5.2 | 31
KJ078 | 6.5 | 1950 | 70 | 67 | 85 | 79.9 | 0.401 | 15.19 | 32 | 5.1 | 31
KJ078 | 6.5 | 1950 | 75 | 67 | 85 | 79.9 | 0.521 | 19.75 | 41.6 | 5.1 | 31
KJ078 | 6.5 | 1950 | 80 | 67 | 85 | 79.9 | 0.646 | 24.5 | 51.6 | 5.1 | 31
KJ078 | 6.5 | 1950 | 85 | 67 | 85 | 79.9 | 0.758 | 28.77 | 60.6 | 5.1 | 31
KJ078 | 6.5 | 1950 | 90 | 67 | 85 | 79.9 | 0.849 | 32.19 | 67.8 | 5.1 | 31
KJ078 | 6.5 | 1950 | 75 | 72 | 85 | 89.1 | 0.368 | 15.57 | 32.8 | 5.1 | 31
KJ078 | 6.5 | 1950 | 80 | 72 | 85 | 89.1 | 0.476 | 20.13 | 42.4 | 5.1 | 31
KJ078 | 6.5 | 1950 | 85 | 72 | 85 | 89.1 | 0.584 | 24.69 | 52 | 5.1 | 31
KJ078 | 6.5 | 1950 | 90 | 72 | 85 | 89.1 | 0.691 | 29.25 | 61.6 | 5.1 | 31
KJ078 | 6.5 | 1950 | 80 | 77 | 85 | 98.3 | 0.339 | 15.81 | 33.3 | 5 | 31
KJ078 | 6.5 | 1950 | 85 | 77 | 85 | 98.3 | 0.44 | 20.56 | 43.3 | 5 | 31
KJ078 | 6.5 | 1950 | 90 | 77 | 85 | 98.3 | 0.543 | 25.36 | 53.4 | 5 | 31
KJ078 | 6.5 | 1950 | 65 | 57 | 95 | 66.2 | 0.582 | 18.28 | 38.5 | 5.8 | 31
KJ078 | 6.5 | 1950 | 70 | 57 | 95 | 66.2 | 0.728 | 22.89 | 48.2 | 5.8 | 31
KJ078 | 6.5 | 1950 | 75 | 57 | 95 | 66.2 | 0.875 | 27.49 | 57.9 | 5.8 | 31
KJ078 | 6.5 | 1950 | 80 | 57 | 95 | 66.2 | 1 | 31.43 | 66.2 | 5.8 | 31
KJ078 | 6.5 | 1950 | 85 | 57 | 95 | 66.2 | 1 | 31.43 | 66.2 | 5.8 | 31
KJ078 | 6.5 | 1950 | 90 | 57 | 95 | 66.2 | 1 | 31.43 | 66.2 | 5.8 | 31
KJ078 | 6.5 | 1950 | 65 | 62 | 95 | 70.5 | 0.406 | 13.58 | 28.6 | 5.8 | 31
KJ078 | 6.5 | 1950 | 70 | 62 | 95 | 70.5 | 0.545 | 18.23 | 38.4 | 5.8 | 31
KJ078 | 6.5 | 1950 | 75 | 62 | 95 | 70.5 | 0.685 | 22.93 | 48.3 | 5.8 | 31
KJ078 | 6.5 | 1950 | 80 | 62 | 95 | 70.5 | 0.824 | 27.59 | 58.1 | 5.8 | 31
KJ078 | 6.5 | 1950 | 85 | 62 | 95 | 70.5 | 0.926 | 31.01 | 65.3 | 5.8 | 31
KJ078 | 6.5 | 1950 | 90 | 62 | 95 | 70.5 | 0.938 | 31.39 | 66.1 | 5.8 | 31
KJ078 | 6.5 | 1950 | 70 | 67 | 95 | 74.9 | 0.383 | 13.63 | 28.7 | 5.8 | 31
KJ078 | 6.5 | 1950 | 75 | 67 | 95 | 74.9 | 0.515 | 18.33 | 38.6 | 5.8 | 31
KJ078 | 6.5 | 1950 | 80 | 67 | 95 | 74.9 | 0.649 | 23.08 | 48.6 | 5.8 | 31
KJ078 | 6.5 | 1950 | 85 | 67 | 95 | 74.9 | 0.774 | 27.54 | 58 | 5.8 | 31
KJ078 | 6.5 | 1950 | 90 | 67 | 95 | 74.9 | 0.868 | 30.86 | 65 | 5.8 | 31
KJ078 | 6.5 | 1950 | 75 | 72 | 95 | 83.6 | 0.347 | 13.77 | 29 | 5.8 | 31
KJ078 | 6.5 | 1950 | 80 | 72 | 95 | 83.6 | 0.468 | 18.57 | 39.1 | 5.8 | 31
KJ078 | 6.5 | 1950 | 85 | 72 | 95 | 83.6 | 0.59 | 23.41 | 49.3 | 5.8 | 31
KJ078 | 6.5 | 1950 | 90 | 72 | 95 | 83.6 | 0.711 | 28.21 | 59.4 | 5.8 | 31
KJ078 | 6.5 | 1950 | 80 | 77 | 95 | 92.4 | 0.321 | 14.1 | 29.7 | 5.8 | 31
KJ078 | 6.5 | 1950 | 85 | 77 | 95 | 92.4 | 0.438 | 19.23 | 40.5 | 5.8 | 31
KJ078 | 6.5 | 1950 | 90 | 77 | 95 | 92.4 | 0.556 | 24.41 | 51.4 | 5.8 | 31
KJ078 | 6.5 | 1950 | 65 | 57 | 105 | 64.2 | 0.547 | 16.67 | 35.1 | 6.7 | 31
KJ078 | 6.5 | 1950 | 70 | 57 | 105 | 64.2 | 0.706 | 21.51 | 45.3 | 6.7 | 31
KJ078 | 6.5 | 1950 | 75 | 57 | 105 | 64.2 | 0.864 | 26.35 | 55.5 | 6.7 | 31
KJ078 | 6.5 | 1950 | 80 | 57 | 105 | 64.2 | 1 | 30.48 | 64.2 | 6.7 | 31
KJ078 | 6.5 | 1950 | 85 | 57 | 105 | 64.2 | 1 | 30.48 | 64.2 | 6.7 | 31
KJ078 | 6.5 | 1950 | 90 | 57 | 105 | 64.2 | 1 | 30.48 | 64.2 | 6.7 | 31
KJ078 | 6.5 | 1950 | 65 | 62 | 105 | 66.9 | 0.38 | 12.06 | 25.4 | 6.7 | 31
KJ078 | 6.5 | 1950 | 70 | 62 | 105 | 66.9 | 0.532 | 16.9 | 35.6 | 6.7 | 31
KJ078 | 6.5 | 1950 | 75 | 62 | 105 | 66.9 | 0.685 | 21.75 | 45.8 | 6.7 | 31
KJ078 | 6.5 | 1950 | 80 | 62 | 105 | 66.9 | 0.837 | 26.59 | 56 | 6.7 | 31
KJ078 | 6.5 | 1950 | 85 | 62 | 105 | 66.9 | 0.933 | 29.63 | 62.4 | 6.7 | 31
KJ078 | 6.5 | 1950 | 90 | 62 | 105 | 66.9 | 0.96 | 30.48 | 64.2 | 6.7 | 31
KJ078 | 6.5 | 1950 | 70 | 67 | 105 | 69.7 | 0.372 | 12.3 | 25.9 | 6.8 | 31
KJ078 | 6.5 | 1950 | 75 | 67 | 105 | 69.7 | 0.518 | 17.14 | 36.1 | 6.8 | 31
KJ078 | 6.5 | 1950 | 80 | 67 | 105 | 69.7 | 0.663 | 21.94 | 46.2 | 6.8 | 31
KJ078 | 6.5 | 1950 | 85 | 67 | 105 | 69.7 | 0.795 | 26.31 | 55.4 | 6.8 | 31
KJ078 | 6.5 | 1950 | 90 | 67 | 105 | 69.7 | 0.92 | 30.44 | 64.1 | 6.8 | 31
KJ078 | 6.5 | 1950 | 75 | 72 | 105 | 77.6 | 0.34 | 12.54 | 26.4 | 6.8 | 31
KJ078 | 6.5 | 1950 | 80 | 72 | 105 | 77.6 | 0.469 | 17.28 | 36.4 | 6.8 | 31
KJ078 | 6.5 | 1950 | 85 | 72 | 105 | 77.6 | 0.599 | 22.08 | 46.5 | 6.8 | 31
KJ078 | 6.5 | 1950 | 90 | 72 | 105 | 77.6 | 0.729 | 26.88 | 56.6 | 6.8 | 31
KJ078 | 6.5 | 1950 | 80 | 77 | 105 | 85.5 | 0.312 | 12.68 | 26.7 | 6.8 | 31
KJ078 | 6.5 | 1950 | 85 | 77 | 105 | 85.5 | 0.44 | 17.85 | 37.6 | 6.8 | 31
KJ078 | 6.5 | 1950 | 90 | 77 | 105 | 85.5 | 0.568 | 23.08 | 48.6 | 6.8 | 31
KJ078 | 6.5 | 1950 | 65 | 57 | 115 | 62.2 | 0.508 | 15 | 31.6 | 7.6 | 32
KJ078 | 6.5 | 1950 | 70 | 57 | 115 | 62.2 | 0.682 | 20.13 | 42.4 | 7.6 | 32
KJ078 | 6.5 | 1950 | 75 | 57 | 115 | 62.2 | 0.854 | 25.21 | 53.1 | 7.6 | 32
KJ078 | 6.5 | 1950 | 80 | 57 | 115 | 62.2 | 1 | 29.53 | 62.2 | 7.6 | 32
KJ078 | 6.5 | 1950 | 85 | 57 | 115 | 62.2 | 1 | 29.53 | 62.2 | 7.6 | 32
KJ078 | 6.5 | 1950 | 90 | 57 | 115 | 62.2 | 1 | 29.53 | 62.2 | 7.6 | 32
KJ078 | 6.5 | 1950 | 65 | 62 | 115 | 63.3 | 0.352 | 10.59 | 22.3 | 7.7 | 32
KJ078 | 6.5 | 1950 | 70 | 62 | 115 | 63.3 | 0.518 | 15.57 | 32.8 | 7.7 | 32
KJ078 | 6.5 | 1950 | 75 | 62 | 115 | 63.3 | 0.684 | 20.56 | 43.3 | 7.7 | 32
KJ078 | 6.5 | 1950 | 80 | 62 | 115 | 63.3 | 0.852 | 25.59 | 53.9 | 7.7 | 32
KJ078 | 6.5 | 1950 | 85 | 62 | 115 | 63.3 | 0.94 | 28.25 | 59.5 | 7.7 | 32
KJ078 | 6.5 | 1950 | 90 | 62 | 115 | 63.3 | 0.979 | 29.44 | 62 | 7.7 | 32
KJ078 | 6.5 | 1950 | 70 | 67 | 115 | 64.5 | 0.36 | 11.02 | 23.2 | 7.7 | 32
KJ078 | 6.5 | 1950 | 75 | 67 | 115 | 64.5 | 0.519 | 15.91 | 33.5 | 7.7 | 32
KJ078 | 6.5 | 1950 | 80 | 67 | 115 | 64.5 | 0.679 | 20.8 | 43.8 | 7.7 | 32
KJ078 | 6.5 | 1950 | 85 | 67 | 115 | 64.5 | 0.819 | 25.07 | 52.8 | 7.7 | 32
KJ078 | 6.5 | 1950 | 90 | 67 | 115 | 64.5 | 0.957 | 29.3 | 61.7 | 7.7 | 32
KJ078 | 6.5 | 1950 | 75 | 72 | 115 | 71.5 | 0.331 | 11.25 | 23.7 | 7.8 | 32
KJ078 | 6.5 | 1950 | 80 | 72 | 115 | 71.5 | 0.471 | 16 | 33.7 | 7.8 | 32
KJ078 | 6.5 | 1950 | 85 | 72 | 115 | 71.5 | 0.611 | 20.75 | 43.7 | 7.8 | 32
KJ078 | 6.5 | 1950 | 90 | 72 | 115 | 71.5 | 0.751 | 25.5 | 53.7 | 7.8 | 32
KJ078 | 6.5 | 1950 | 80 | 77 | 115 | 78.5 | 0.301 | 11.21 | 23.6 | 7.8 | 32
KJ078 | 6.5 | 1950 | 85 | 77 | 115 | 78.5 | 0.442 | 16.48 | 34.7 | 7.8 | 32
KJ078 | 6.5 | 1950 | 90 | 77 | 115 | 78.5 | 0.583 | 21.75 | 45.8 | 7.8 | 32
KJ078 | 6.5 | 1950 | 65 | 57 | 125 | 60.2 | 0.467 | 13.34 | 28.1 | 8.5 | 32
KJ078 | 6.5 | 1950 | 70 | 57 | 125 | 60.2 | 0.654 | 18.71 | 39.4 | 8.5 | 32
KJ078 | 6.5 | 1950 | 75 | 57 | 125 | 60.2 | 0.844 | 24.12 | 50.8 | 8.5 | 32
KJ078 | 6.5 | 1950 | 80 | 57 | 125 | 60.2 | 1 | 28.58 | 60.2 | 8.5 | 32
KJ078 | 6.5 | 1950 | 85 | 57 | 125 | 60.2 | 1 | 28.58 | 60.2 | 8.5 | 32
KJ078 | 6.5 | 1950 | 90 | 57 | 125 | 60.2 | 1 | 28.58 | 60.2 | 8.5 | 32
KJ078 | 6.5 | 1950 | 65 | 62 | 125 | 59.8 | 0.319 | 9.07 | 19.1 | 8.6 | 32
KJ078 | 6.5 | 1950 | 70 | 62 | 125 | 59.8 | 0.502 | 14.25 | 30 | 8.6 | 32
KJ078 | 6.5 | 1950 | 75 | 62 | 125 | 59.8 | 0.684 | 19.42 | 40.9 | 8.6 | 32
KJ078 | 6.5 | 1950 | 80 | 62 | 125 | 59.8 | 0.865 | 24.55 | 51.7 | 8.6 | 32
KJ078 | 6.5 | 1950 | 85 | 62 | 125 | 59.8 | 0.946 | 26.88 | 56.6 | 8.6 | 32
KJ078 | 6.5 | 1950 | 90 | 62 | 125 | 59.8 | 1 | 28.4 | 59.8 | 8.6 | 32
KJ078 | 6.5 | 1950 | 70 | 67 | 125 | 59.3 | 0.346 | 9.73 | 20.5 | 8.6 | 32
KJ078 | 6.5 | 1950 | 75 | 67 | 125 | 59.3 | 0.521 | 14.67 | 30.9 | 8.6 | 32
KJ078 | 6.5 | 1950 | 80 | 67 | 125 | 59.3 | 0.698 | 19.66 | 41.4 | 8.6 | 32
KJ078 | 6.5 | 1950 | 85 | 67 | 125 | 59.3 | 0.845 | 23.79 | 50.1 | 8.6 | 32
KJ078 | 6.5 | 1950 | 90 | 67 | 125 | 59.3 | 0.993 | 27.97 | 58.9 | 8.6 | 32
KJ078 | 6.5 | 1950 | 75 | 72 | 125 | 65.5 | 0.321 | 9.97 | 21 | 8.8 | 32
KJ078 | 6.5 | 1950 | 80 | 72 | 125 | 65.5 | 0.473 | 14.72 | 31 | 8.8 | 32
KJ078 | 6.5 | 1950 | 85 | 72 | 125 | 65.5 | 0.626 | 19.47 | 41 | 8.8 | 32
KJ078 | 6.5 | 1950 | 90 | 72 | 125 | 65.5 | 0.777 | 24.17 | 50.9 | 8.8 | 32
KJ078 | 6.5 | 1950 | 80 | 77 | 125 | 71.6 | 0.288 | 9.78 | 20.6 | 8.9 | 32
KJ078 | 6.5 | 1950 | 85 | 77 | 125 | 71.6 | 0.444 | 15.1 | 31.8 | 8.9 | 32
KJ078 | 6.5 | 1950 | 90 | 77 | 125 | 71.6 | 0.599 | 20.37 | 42.9 | 8.9 | 32
KJ078 | 6.5 | 2275 | 65 | 57 | 75 | 77.8 | 0.562 | 17.79 | 43.7 | 4.5 | 31
KJ078 | 6.5 | 2275 | 70 | 57 | 75 | 77.8 | 0.71 | 22.47 | 55.2 | 4.5 | 31
KJ078 | 6.5 | 2275 | 75 | 57 | 75 | 77.8 | 0.859 | 27.19 | 66.8 | 4.5 | 31
KJ078 | 6.5 | 2275 | 80 | 57 | 75 | 77.8 | 1 | 31.66 | 77.8 | 4.5 | 31
KJ078 | 6.5 | 2275 | 85 | 57 | 75 | 77.8 | 1 | 31.66 | 77.8 | 4.5 | 31
KJ078 | 6.5 | 2275 | 90 | 57 | 75 | 77.8 | 1 | 31.66 | 77.8 | 4.5 | 31
KJ078 | 6.5 | 2275 | 65 | 62 | 75 | 82.6 | 0.418 | 14.04 | 34.5 | 4.5 | 31
KJ078 | 6.5 | 2275 | 70 | 62 | 75 | 82.6 | 0.553 | 18.6 | 45.7 | 4.5 | 31
KJ078 | 6.5 | 2275 | 75 | 62 | 75 | 82.6 | 0.677 | 22.75 | 55.9 | 4.5 | 31
KJ078 | 6.5 | 2275 | 80 | 62 | 75 | 82.6 | 0.826 | 27.76 | 68.2 | 4.5 | 31
KJ078 | 6.5 | 2275 | 85 | 62 | 75 | 82.6 | 0.913 | 30.69 | 75.4 | 4.5 | 31
KJ078 | 6.5 | 2275 | 90 | 62 | 75 | 82.6 | 0.939 | 31.58 | 77.6 | 4.5 | 31
KJ078 | 6.5 | 2275 | 70 | 67 | 75 | 87.5 | 0.414 | 14.73 | 36.2 | 4.4 | 31
KJ078 | 6.5 | 2275 | 75 | 67 | 75 | 87.5 | 0.536 | 19.09 | 46.9 | 4.4 | 31
KJ078 | 6.5 | 2275 | 80 | 67 | 75 | 87.5 | 0.665 | 23.69 | 58.2 | 4.4 | 31
KJ078 | 6.5 | 2275 | 85 | 67 | 75 | 87.5 | 0.781 | 27.8 | 68.3 | 4.4 | 31
KJ078 | 6.5 | 2275 | 90 | 67 | 75 | 87.5 | 0.88 | 31.34 | 77 | 4.4 | 31
KJ078 | 6.5 | 2275 | 75 | 72 | 75 | 97.3 | 0.384 | 15.22 | 37.4 | 4.3 | 31
KJ078 | 6.5 | 2275 | 80 | 72 | 75 | 97.3 | 0.494 | 19.58 | 48.1 | 4.3 | 31
KJ078 | 6.5 | 2275 | 85 | 72 | 75 | 97.3 | 0.604 | 23.93 | 58.8 | 4.3 | 31
KJ078 | 6.5 | 2275 | 90 | 72 | 75 | 97.3 | 0.714 | 28.29 | 69.5 | 4.3 | 31
KJ078 | 6.5 | 2275 | 80 | 77 | 75 | 107 | 0.355 | 15.47 | 38 | 4.3 | 31
KJ078 | 6.5 | 2275 | 85 | 77 | 75 | 107 | 0.461 | 20.07 | 49.3 | 4.3 | 31
KJ078 | 6.5 | 2275 | 90 | 77 | 75 | 107 | 0.566 | 24.66 | 60.6 | 4.3 | 31
KJ078 | 6.5 | 2275 | 65 | 57 | 85 | 75.3 | 0.56 | 17.18 | 42.2 | 5.2 | 31
KJ078 | 6.5 | 2275 | 70 | 57 | 85 | 75.3 | 0.712 | 21.82 | 53.6 | 5.2 | 31
KJ078 | 6.5 | 2275 | 75 | 57 | 85 | 75.3 | 0.865 | 26.5 | 65.1 | 5.2 | 31
KJ078 | 6.5 | 2275 | 80 | 57 | 85 | 75.3 | 1 | 30.65 | 75.3 | 5.2 | 31
KJ078 | 6.5 | 2275 | 85 | 57 | 85 | 75.3 | 1 | 30.65 | 75.3 | 5.2 | 31
KJ078 | 6.5 | 2275 | 90 | 57 | 85 | 75.3 | 1 | 30.65 | 75.3 | 5.2 | 31
KJ078 | 6.5 | 2275 | 65 | 62 | 85 | 78.9 | 0.404 | 12.98 | 31.9 | 5.1 | 31
KJ078 | 6.5 | 2275 | 70 | 62 | 85 | 78.9 | 0.548 | 17.58 | 43.2 | 5.1 | 31
KJ078 | 6.5 | 2275 | 75 | 62 | 85 | 78.9 | 0.686 | 22.02 | 54.1 | 5.1 | 31
KJ078 | 6.5 | 2275 | 80 | 62 | 85 | 78.9 | 0.837 | 26.86 | 66 | 5.1 | 31
KJ078 | 6.5 | 2275 | 85 | 62 | 85 | 78.9 | 0.921 | 29.59 | 72.7 | 5.1 | 31
KJ078 | 6.5 | 2275 | 90 | 62 | 85 | 78.9 | 0.951 | 30.53 | 75 | 5.1 | 31
KJ078 | 6.5 | 2275 | 70 | 67 | 85 | 82.4 | 0.398 | 13.35 | 32.8 | 5.1 | 31
KJ078 | 6.5 | 2275 | 75 | 67 | 85 | 82.4 | 0.533 | 17.87 | 43.9 | 5.1 | 31
KJ078 | 6.5 | 2275 | 80 | 67 | 85 | 82.4 | 0.672 | 22.55 | 55.4 | 5.1 | 31
KJ078 | 6.5 | 2275 | 85 | 67 | 85 | 82.4 | 0.796 | 26.7 | 65.6 | 5.1 | 31
KJ078 | 6.5 | 2275 | 90 | 67 | 85 | 82.4 | 0.909 | 30.48 | 74.9 | 5.1 | 31
KJ078 | 6.5 | 2275 | 75 | 72 | 85 | 91.3 | 0.368 | 13.68 | 33.6 | 5.1 | 31
KJ078 | 6.5 | 2275 | 80 | 72 | 85 | 91.3 | 0.49 | 18.19 | 44.7 | 5.1 | 31
KJ078 | 6.5 | 2275 | 85 | 72 | 85 | 91.3 | 0.612 | 22.75 | 55.9 | 5.1 | 31
KJ078 | 6.5 | 2275 | 90 | 72 | 85 | 91.3 | 0.735 | 27.31 | 67.1 | 5.1 | 31
KJ078 | 6.5 | 2275 | 80 | 77 | 85 | 100.1 | 0.341 | 13.88 | 34.1 | 5 | 31
KJ078 | 6.5 | 2275 | 85 | 77 | 85 | 100.1 | 0.462 | 18.8 | 46.2 | 5 | 31
KJ078 | 6.5 | 2275 | 90 | 77 | 85 | 100.1 | 0.583 | 23.77 | 58.4 | 5 | 31
KJ078 | 6.5 | 2275 | 65 | 57 | 95 | 72.8 | 0.558 | 16.52 | 40.6 | 5.8 | 31
KJ078 | 6.5 | 2275 | 70 | 57 | 95 | 72.8 | 0.714 | 21.16 | 52 | 5.8 | 31
KJ078 | 6.5 | 2275 | 75 | 57 | 95 | 72.8 | 0.871 | 25.8 | 63.4 | 5.8 | 31
KJ078 | 6.5 | 2275 | 80 | 57 | 95 | 72.8 | 1 | 29.63 | 72.8 | 5.8 | 31
KJ078 | 6.5 | 2275 | 85 | 57 | 95 | 72.8 | 1 | 29.63 | 72.8 | 5.8 | 31
KJ078 | 6.5 | 2275 | 90 | 57 | 95 | 72.8 | 1 | 29.63 | 72.8 | 5.8 | 31
KJ078 | 6.5 | 2275 | 65 | 62 | 95 | 75.1 | 0.389 | 11.88 | 29.2 | 5.8 | 31
KJ078 | 6.5 | 2275 | 70 | 62 | 95 | 75.1 | 0.542 | 16.56 | 40.7 | 5.8 | 31
KJ078 | 6.5 | 2275 | 75 | 62 | 95 | 75.1 | 0.695 | 21.25 | 52.2 | 5.8 | 31
KJ078 | 6.5 | 2275 | 80 | 62 | 95 | 75.1 | 0.848 | 25.93 | 63.7 | 5.8 | 31
KJ078 | 6.5 | 2275 | 85 | 62 | 95 | 75.1 | 0.932 | 28.49 | 70 | 5.8 | 31
KJ078 | 6.5 | 2275 | 90 | 62 | 95 | 75.1 | 0.968 | 29.59 | 72.7 | 5.8 | 31
KJ078 | 6.5 | 2275 | 70 | 67 | 95 | 77.4 | 0.38 | 11.97 | 29.4 | 5.8 | 31
KJ078 | 6.5 | 2275 | 75 | 67 | 95 | 77.4 | 0.53 | 16.69 | 41 | 5.8 | 31
KJ078 | 6.5 | 2275 | 80 | 67 | 95 | 77.4 | 0.678 | 21.37 | 52.5 | 5.8 | 31
KJ078 | 6.5 | 2275 | 85 | 67 | 95 | 77.4 | 0.811 | 25.56 | 62.8 | 5.8 | 31
KJ078 | 6.5 | 2275 | 90 | 67 | 95 | 77.4 | 0.938 | 29.55 | 72.6 | 5.8 | 31
KJ078 | 6.5 | 2275 | 75 | 72 | 95 | 85.3 | 0.348 | 12.09 | 29.7 | 5.8 | 31
KJ078 | 6.5 | 2275 | 80 | 72 | 95 | 85.3 | 0.485 | 16.85 | 41.4 | 5.8 | 31
KJ078 | 6.5 | 2275 | 85 | 72 | 95 | 85.3 | 0.621 | 21.57 | 53 | 5.8 | 31
KJ078 | 6.5 | 2275 | 90 | 72 | 95 | 85.3 | 0.757 | 26.29 | 64.6 | 5.8 | 31
KJ078 | 6.5 | 2275 | 80 | 77 | 95 | 93.2 | 0.324 | 12.29 | 30.2 | 5.8 | 31
KJ078 | 6.5 | 2275 | 85 | 77 | 95 | 93.2 | 0.464 | 17.58 | 43.2 | 5.8 | 31
KJ078 | 6.5 | 2275 | 90 | 77 | 95 | 93.2 | 0.602 | 22.83 | 56.1 | 5.8 | 31
KJ078 | 6.5 | 2275 | 65 | 57 | 105 | 69.5 | 0.534 | 15.1 | 37.1 | 6.7 | 31
KJ078 | 6.5 | 2275 | 70 | 57 | 105 | 69.5 | 0.705 | 19.94 | 49 | 6.7 | 31
KJ078 | 6.5 | 2275 | 75 | 57 | 105 | 69.5 | 0.878 | 24.83 | 61 | 6.7 | 31
KJ078 | 6.5 | 2275 | 80 | 57 | 105 | 69.5 | 1 | 28.29 | 69.5 | 6.7 | 31
KJ078 | 6.5 | 2275 | 85 | 57 | 105 | 69.5 | 1 | 28.29 | 69.5 | 6.7 | 31
KJ078 | 6.5 | 2275 | 90 | 57 | 105 | 69.5 | 1 | 28.29 | 69.5 | 6.7 | 31
KJ078 | 6.5 | 2275 | 65 | 62 | 105 | 70.9 | 0.367 | 10.58 | 26 | 6.7 | 31
KJ078 | 6.5 | 2275 | 70 | 62 | 105 | 70.9 | 0.533 | 15.38 | 37.8 | 6.7 | 31
KJ078 | 6.5 | 2275 | 75 | 62 | 105 | 70.9 | 0.7 | 20.19 | 49.6 | 6.7 | 31
KJ078 | 6.5 | 2275 | 80 | 62 | 105 | 70.9 | 0.866 | 24.99 | 61.4 | 6.7 | 31
KJ078 | 6.5 | 2275 | 85 | 62 | 105 | 70.9 | 0.941 | 27.15 | 66.7 | 6.7 | 31
KJ078 | 6.5 | 2275 | 90 | 62 | 105 | 70.9 | 0.977 | 28.21 | 69.3 | 6.7 | 31
KJ078 | 6.5 | 2275 | 70 | 67 | 105 | 72.3 | 0.368 | 10.83 | 26.6 | 6.8 | 31
KJ078 | 6.5 | 2275 | 75 | 67 | 105 | 72.3 | 0.53 | 15.59 | 38.3 | 6.8 | 31
KJ078 | 6.5 | 2275 | 80 | 67 | 105 | 72.3 | 0.69 | 20.31 | 49.9 | 6.8 | 31
KJ078 | 6.5 | 2275 | 85 | 67 | 105 | 72.3 | 0.824 | 24.26 | 59.6 | 6.8 | 31
KJ078 | 6.5 | 2275 | 90 | 67 | 105 | 72.3 | 0.957 | 28.16 | 69.2 | 6.8 | 31
KJ078 | 6.5 | 2275 | 75 | 72 | 105 | 79.1 | 0.34 | 10.95 | 26.9 | 6.8 | 31
KJ078 | 6.5 | 2275 | 80 | 72 | 105 | 79.1 | 0.487 | 15.67 | 38.5 | 6.8 | 31
KJ078 | 6.5 | 2275 | 85 | 72 | 105 | 79.1 | 0.632 | 20.35 | 50 | 6.8 | 31
KJ078 | 6.5 | 2275 | 90 | 72 | 105 | 79.1 | 0.777 | 25.03 | 61.5 | 6.8 | 31
KJ078 | 6.5 | 2275 | 80 | 77 | 105 | 85.8 | 0.315 | 10.99 | 27 | 6.8 | 31
KJ078 | 6.5 | 2275 | 85 | 77 | 105 | 85.8 | 0.471 | 16.44 | 40.4 | 6.8 | 31
KJ078 | 6.5 | 2275 | 90 | 77 | 105 | 85.8 | 0.628 | 21.94 | 53.9 | 6.8 | 31
KJ078 | 6.5 | 2275 | 65 | 57 | 115 | 66.2 | 0.508 | 13.68 | 33.6 | 7.6 | 32
KJ078 | 6.5 | 2275 | 70 | 57 | 115 | 66.2 | 0.695 | 18.72 | 46 | 7.6 | 32
KJ078 | 6.5 | 2275 | 75 | 57 | 115 | 66.2 | 0.884 | 23.81 | 58.5 | 7.6 | 32
KJ078 | 6.5 | 2275 | 80 | 57 | 115 | 66.2 | 1 | 26.94 | 66.2 | 7.6 | 32
KJ078 | 6.5 | 2275 | 85 | 57 | 115 | 66.2 | 1 | 26.94 | 66.2 | 7.6 | 32
KJ078 | 6.5 | 2275 | 90 | 57 | 115 | 66.2 | 1 | 26.94 | 66.2 | 7.6 | 32
KJ078 | 6.5 | 2275 | 65 | 62 | 115 | 66.7 | 0.342 | 9.28 | 22.8 | 7.7 | 32
KJ078 | 6.5 | 2275 | 70 | 62 | 115 | 66.7 | 0.523 | 14.2 | 34.9 | 7.7 | 32
KJ078 | 6.5 | 2275 | 75 | 62 | 115 | 66.7 | 0.705 | 19.13 | 47 | 7.7 | 32
KJ078 | 6.5 | 2275 | 80 | 62 | 115 | 66.7 | 0.888 | 24.09 | 59.2 | 7.7 | 32
KJ078 | 6.5 | 2275 | 85 | 62 | 115 | 66.7 | 0.951 | 25.8 | 63.4 | 7.7 | 32
KJ078 | 6.5 | 2275 | 90 | 62 | 115 | 66.7 | 0.991 | 26.9 | 66.1 | 7.7 | 32
KJ078 | 6.5 | 2275 | 70 | 67 | 115 | 67.3 | 0.354 | 9.69 | 23.8 | 7.7 | 32
KJ078 | 6.5 | 2275 | 75 | 67 | 115 | 67.3 | 0.529 | 14.49 | 35.6 | 7.7 | 32
KJ078 | 6.5 | 2275 | 80 | 67 | 115 | 67.3 | 0.704 | 19.29 | 47.4 | 7.7 | 32
KJ078 | 6.5 | 2275 | 85 | 67 | 115 | 67.3 | 0.837 | 22.91 | 56.3 | 7.7 | 32
KJ078 | 6.5 | 2275 | 90 | 67 | 115 | 67.3 | 0.97 | 26.58 | 65.3 | 7.7 | 32
KJ078 | 6.5 | 2275 | 75 | 72 | 115 | 72.9 | 0.331 | 9.81 | 24.1 | 7.7 | 32
KJ078 | 6.5 | 2275 | 80 | 72 | 115 | 72.9 | 0.488 | 14.49 | 35.6 | 7.7 | 32
KJ078 | 6.5 | 2275 | 85 | 72 | 115 | 72.9 | 0.645 | 19.13 | 47 | 7.7 | 32
KJ078 | 6.5 | 2275 | 90 | 72 | 115 | 72.9 | 0.802 | 23.81 | 58.5 | 7.7 | 32
KJ078 | 6.5 | 2275 | 80 | 77 | 115 | 78.5 | 0.302 | 9.65 | 23.7 | 7.8 | 32
KJ078 | 6.5 | 2275 | 85 | 77 | 115 | 78.5 | 0.48 | 15.34 | 37.7 | 7.8 | 32
KJ078 | 6.5 | 2275 | 90 | 77 | 115 | 78.5 | 0.657 | 21 | 51.6 | 7.8 | 32
KJ078 | 6.5 | 2275 | 65 | 57 | 125 | 62 | 0.485 | 12.25 | 30.1 | 8.6 | 32
KJ078 | 6.5 | 2275 | 70 | 57 | 125 | 62 | 0.695 | 17.54 | 43.1 | 8.6 | 32
KJ078 | 6.5 | 2275 | 75 | 57 | 125 | 62 | 0.903 | 22.79 | 56 | 8.6 | 32
KJ078 | 6.5 | 2275 | 80 | 57 | 125 | 62 | 1 | 25.23 | 62 | 8.6 | 32
KJ078 | 6.5 | 2275 | 85 | 57 | 125 | 62 | 1 | 25.23 | 62 | 8.6 | 32
KJ078 | 6.5 | 2275 | 90 | 57 | 125 | 62 | 1 | 25.23 | 62 | 8.6 | 32
KJ078 | 6.5 | 2275 | 65 | 62 | 125 | 62.1 | 0.314 | 7.94 | 19.5 | 8.6 | 32
KJ078 | 6.5 | 2275 | 70 | 62 | 125 | 62.1 | 0.515 | 13.02 | 32 | 8.6 | 32
KJ078 | 6.5 | 2275 | 75 | 62 | 125 | 62.1 | 0.715 | 18.07 | 44.4 | 8.6 | 32
KJ078 | 6.5 | 2275 | 80 | 62 | 125 | 62.1 | 0.916 | 23.16 | 56.9 | 8.6 | 32
KJ078 | 6.5 | 2275 | 85 | 62 | 125 | 62.1 | 0.968 | 24.46 | 60.1 | 8.6 | 32
KJ078 | 6.5 | 2275 | 90 | 62 | 125 | 62.1 | 0.998 | 25.23 | 62 | 8.6 | 32
KJ078 | 6.5 | 2275 | 70 | 67 | 125 | 62.2 | 0.336 | 8.51 | 20.9 | 8.6 | 32
KJ078 | 6.5 | 2275 | 75 | 67 | 125 | 62.2 | 0.529 | 13.39 | 32.9 | 8.6 | 32
KJ078 | 6.5 | 2275 | 80 | 67 | 125 | 62.2 | 0.72 | 18.23 | 44.8 | 8.6 | 32
KJ078 | 6.5 | 2275 | 85 | 67 | 125 | 62.2 | 0.854 | 21.61 | 53.1 | 8.6 | 32
KJ078 | 6.5 | 2275 | 90 | 67 | 125 | 62.2 | 0.987 | 24.99 | 61.4 | 8.6 | 32
KJ078 | 6.5 | 2275 | 75 | 72 | 125 | 66.7 | 0.319 | 8.67 | 21.3 | 8.7 | 32
KJ078 | 6.5 | 2275 | 80 | 72 | 125 | 66.7 | 0.489 | 13.27 | 32.6 | 8.7 | 32
KJ078 | 6.5 | 2275 | 85 | 72 | 125 | 66.7 | 0.66 | 17.91 | 44 | 8.7 | 32
KJ078 | 6.5 | 2275 | 90 | 72 | 125 | 66.7 | 0.831 | 22.55 | 55.4 | 8.7 | 32
KJ078 | 6.5 | 2275 | 80 | 77 | 125 | 71.2 | 0.288 | 8.34 | 20.5 | 8.8 | 32
KJ078 | 6.5 | 2275 | 85 | 77 | 125 | 71.2 | 0.49 | 14.2 | 34.9 | 8.8 | 32
KJ078 | 6.5 | 2275 | 90 | 77 | 125 | 71.2 | 0.694 | 20.11 | 49.4 | 8.8 | 32
KJ078 | 6.5 | 2600 | 65 | 57 | 75 | 85.7 | 0.548 | 16.74 | 47 | 4.5 | 31
KJ078 | 6.5 | 2600 | 70 | 57 | 75 | 85.7 | 0.694 | 21.19 | 59.5 | 4.5 | 31
KJ078 | 6.5 | 2600 | 75 | 57 | 75 | 85.7 | 0.839 | 25.61 | 71.9 | 4.5 | 31
KJ078 | 6.5 | 2600 | 80 | 57 | 75 | 85.7 | 0.985 | 30.06 | 84.4 | 4.5 | 31
KJ078 | 6.5 | 2600 | 85 | 57 | 75 | 85.7 | 1 | 30.52 | 85.7 | 4.5 | 31
KJ078 | 6.5 | 2600 | 90 | 57 | 75 | 85.7 | 1 | 30.52 | 85.7 | 4.5 | 31
KJ078 | 6.5 | 2600 | 65 | 62 | 75 | 87.9 | 0.407 | 12.75 | 35.8 | 4.4 | 31
KJ078 | 6.5 | 2600 | 70 | 62 | 75 | 87.9 | 0.548 | 17.17 | 48.2 | 4.4 | 31
KJ078 | 6.5 | 2600 | 75 | 62 | 75 | 87.9 | 0.683 | 21.37 | 60 | 4.4 | 31
KJ078 | 6.5 | 2600 | 80 | 62 | 75 | 87.9 | 0.832 | 26.03 | 73.1 | 4.4 | 31
KJ078 | 6.5 | 2600 | 85 | 62 | 75 | 87.9 | 0.914 | 28.6 | 80.3 | 4.4 | 31
KJ078 | 6.5 | 2600 | 90 | 62 | 75 | 87.9 | 0.97 | 30.38 | 85.3 | 4.4 | 31
KJ078 | 6.5 | 2600 | 70 | 67 | 75 | 90.1 | 0.411 | 13.18 | 37 | 4.4 | 31
KJ078 | 6.5 | 2600 | 75 | 67 | 75 | 90.1 | 0.546 | 17.52 | 49.2 | 4.4 | 31
KJ078 | 6.5 | 2600 | 80 | 67 | 75 | 90.1 | 0.686 | 22.01 | 61.8 | 4.4 | 31
KJ078 | 6.5 | 2600 | 85 | 67 | 75 | 90.1 | 0.815 | 26.14 | 73.4 | 4.4 | 31
KJ078 | 6.5 | 2600 | 90 | 67 | 75 | 90.1 | 0.943 | 30.27 | 85 | 4.4 | 31
KJ078 | 6.5 | 2600 | 75 | 72 | 75 | 100 | 0.381 | 13.57 | 38.1 | 4.3 | 31
KJ078 | 6.5 | 2600 | 80 | 72 | 75 | 100 | 0.506 | 18.02 | 50.6 | 4.3 | 31
KJ078 | 6.5 | 2600 | 85 | 72 | 75 | 100 | 0.63 | 22.44 | 63 | 4.3 | 31
KJ078 | 6.5 | 2600 | 90 | 72 | 75 | 100 | 0.754 | 26.85 | 75.4 | 4.3 | 31
KJ078 | 6.5 | 2600 | 80 | 77 | 75 | 109.9 | 0.358 | 14 | 39.3 | 4.3 | 31
KJ078 | 6.5 | 2600 | 85 | 77 | 75 | 109.9 | 0.478 | 18.7 | 52.5 | 4.3 | 31
KJ078 | 6.5 | 2600 | 90 | 77 | 75 | 109.9 | 0.598 | 23.4 | 65.7 | 4.3 | 31
KJ078 | 6.5 | 2600 | 65 | 57 | 85 | 82.5 | 0.543 | 15.95 | 44.8 | 5.1 | 31
KJ078 | 6.5 | 2600 | 70 | 57 | 85 | 82.5 | 0.699 | 20.55 | 57.7 | 5.1 | 31
KJ078 | 6.5 | 2600 | 75 | 57 | 85 | 82.5 | 0.855 | 25.11 | 70.5 | 5.1 | 31
KJ078 | 6.5 | 2600 | 80 | 57 | 85 | 82.5 | 1 | 29.38 | 82.5 | 5.1 | 31
KJ078 | 6.5 | 2600 | 85 | 57 | 85 | 82.5 | 1 | 29.38 | 82.5 | 5.1 | 31
KJ078 | 6.5 | 2600 | 90 | 57 | 85 | 82.5 | 1 | 29.38 | 82.5 | 5.1 | 31
KJ078 | 6.5 | 2600 | 65 | 62 | 85 | 83.8 | 0.391 | 11.68 | 32.8 | 5.1 | 31
KJ078 | 6.5 | 2600 | 70 | 62 | 85 | 83.8 | 0.544 | 16.24 | 45.6 | 5.1 | 31
KJ078 | 6.5 | 2600 | 75 | 62 | 85 | 83.8 | 0.693 | 20.69 | 58.1 | 5.1 | 31
KJ078 | 6.5 | 2600 | 80 | 62 | 85 | 83.8 | 0.85 | 25.36 | 71.2 | 5.1 | 31
KJ078 | 6.5 | 2600 | 85 | 62 | 85 | 83.8 | 0.924 | 27.56 | 77.4 | 5.1 | 31
KJ078 | 6.5 | 2600 | 90 | 62 | 85 | 83.8 | 0.982 | 29.31 | 82.3 | 5.1 | 31
KJ078 | 6.5 | 2600 | 70 | 67 | 85 | 85 | 0.395 | 11.97 | 33.6 | 5.1 | 31
KJ078 | 6.5 | 2600 | 75 | 67 | 85 | 85 | 0.545 | 16.49 | 46.3 | 5.1 | 31
KJ078 | 6.5 | 2600 | 80 | 67 | 85 | 85 | 0.695 | 21.05 | 59.1 | 5.1 | 31
KJ078 | 6.5 | 2600 | 85 | 67 | 85 | 85 | 0.829 | 25.11 | 70.5 | 5.1 | 31
KJ078 | 6.5 | 2600 | 90 | 67 | 85 | 85 | 0.964 | 29.17 | 81.9 | 5.1 | 31
KJ078 | 6.5 | 2600 | 75 | 72 | 85 | 93.4 | 0.367 | 12.22 | 34.3 | 5.1 | 31
KJ078 | 6.5 | 2600 | 80 | 72 | 85 | 93.4 | 0.504 | 16.77 | 47.1 | 5.1 | 31
KJ078 | 6.5 | 2600 | 85 | 72 | 85 | 93.4 | 0.64 | 21.3 | 59.8 | 5.1 | 31
KJ078 | 6.5 | 2600 | 90 | 72 | 85 | 93.4 | 0.777 | 25.85 | 72.6 | 5.1 | 31
KJ078 | 6.5 | 2600 | 80 | 77 | 85 | 101.9 | 0.343 | 12.46 | 35 | 5 | 31
KJ078 | 6.5 | 2600 | 85 | 77 | 85 | 101.9 | 0.483 | 17.52 | 49.2 | 5 | 31
KJ078 | 6.5 | 2600 | 90 | 77 | 85 | 101.9 | 0.621 | 22.54 | 63.3 | 5 | 31
KJ078 | 6.5 | 2600 | 65 | 57 | 95 | 79.4 | 0.538 | 15.21 | 42.7 | 5.8 | 31
KJ078 | 6.5 | 2600 | 70 | 57 | 95 | 79.4 | 0.703 | 19.87 | 55.8 | 5.8 | 31
KJ078 | 6.5 | 2600 | 75 | 57 | 95 | 79.4 | 0.869 | 24.57 | 69 | 5.8 | 31
KJ078 | 6.5 | 2600 | 80 | 57 | 95 | 79.4 | 1 | 28.28 | 79.4 | 5.8 | 31
KJ078 | 6.5 | 2600 | 85 | 57 | 95 | 79.4 | 1 | 28.28 | 79.4 | 5.8 | 31
KJ078 | 6.5 | 2600 | 90 | 57 | 95 | 79.4 | 1 | 28.28 | 79.4 | 5.8 | 31
KJ078 | 6.5 | 2600 | 65 | 62 | 95 | 79.6 | 0.376 | 10.65 | 29.9 | 5.8 | 31
KJ078 | 6.5 | 2600 | 70 | 62 | 95 | 79.6 | 0.54 | 15.31 | 43 | 5.8 | 31
KJ078 | 6.5 | 2600 | 75 | 62 | 95 | 79.6 | 0.706 | 20.01 | 56.2 | 5.8 | 31
KJ078 | 6.5 | 2600 | 80 | 62 | 95 | 79.6 | 0.871 | 24.68 | 69.3 | 5.8 | 31
KJ078 | 6.5 | 2600 | 85 | 62 | 95 | 79.6 | 0.937 | 26.57 | 74.6 | 5.8 | 31
KJ078 | 6.5 | 2600 | 90 | 62 | 95 | 79.6 | 0.996 | 28.24 | 79.3 | 5.8 | 31
KJ078 | 6.5 | 2600 | 70 | 67 | 95 | 79.8 | 0.378 | 10.75 | 30.2 | 5.8 | 31
KJ078 | 6.5 | 2600 | 75 | 67 | 95 | 79.8 | 0.543 | 15.42 | 43.3 | 5.8 | 31
KJ078 | 6.5 | 2600 | 80 | 67 | 95 | 79.8 | 0.708 | 20.12 | 56.5 | 5.8 | 31
KJ078 | 6.5 | 2600 | 85 | 67 | 95 | 79.8 | 0.847 | 24.07 | 67.6 | 5.8 | 31
KJ078 | 6.5 | 2600 | 90 | 67 | 95 | 79.8 | 0.987 | 28.06 | 78.8 | 5.8 | 31
KJ078 | 6.5 | 2600 | 75 | 72 | 95 | 86.9 | 0.351 | 10.86 | 30.5 | 5.8 | 31
KJ078 | 6.5 | 2600 | 80 | 72 | 95 | 86.9 | 0.502 | 15.53 | 43.6 | 5.8 | 31
KJ078 | 6.5 | 2600 | 85 | 72 | 95 | 86.9 | 0.652 | 20.19 | 56.7 | 5.8 | 31
KJ078 | 6.5 | 2600 | 90 | 72 | 95 | 86.9 | 0.803 | 24.86 | 69.8 | 5.8 | 31
KJ078 | 6.5 | 2600 | 80 | 77 | 95 | 93.9 | 0.327 | 10.93 | 30.7 | 5.8 | 31
KJ078 | 6.5 | 2600 | 85 | 77 | 95 | 93.9 | 0.488 | 16.31 | 45.8 | 5.8 | 31
KJ078 | 6.5 | 2600 | 90 | 77 | 95 | 93.9 | 0.649 | 21.69 | 60.9 | 5.8 | 31
KJ078 | 6.5 | 2600 | 65 | 57 | 105 | 74.8 | 0.523 | 13.92 | 39.1 | 6.7 | 31
KJ078 | 6.5 | 2600 | 70 | 57 | 105 | 74.8 | 0.706 | 18.8 | 52.8 | 6.7 | 31
KJ078 | 6.5 | 2600 | 75 | 57 | 105 | 74.8 | 0.888 | 23.65 | 66.4 | 6.7 | 31
KJ078 | 6.5 | 2600 | 80 | 57 | 105 | 74.8 | 1 | 26.64 | 74.8 | 6.7 | 31
KJ078 | 6.5 | 2600 | 85 | 57 | 105 | 74.8 | 1 | 26.64 | 74.8 | 6.7 | 31
KJ078 | 6.5 | 2600 | 90 | 57 | 105 | 74.8 | 1 | 26.64 | 74.8 | 6.7 | 31
KJ078 | 6.5 | 2600 | 65 | 62 | 105 | 74.9 | 0.355 | 9.47 | 26.6 | 6.7 | 31
KJ078 | 6.5 | 2600 | 70 | 62 | 105 | 74.9 | 0.534 | 14.25 | 40 | 6.7 | 31
KJ078 | 6.5 | 2600 | 75 | 62 | 105 | 74.9 | 0.714 | 19.05 | 53.5 | 6.7 | 31
KJ078 | 6.5 | 2600 | 80 | 62 | 105 | 74.9 | 0.893 | 23.82 | 66.9 | 6.7 | 31
KJ078 | 6.5 | 2600 | 85 | 62 | 105 | 74.9 | 0.947 | 25.25 | 70.9 | 6.7 | 31
KJ078 | 6.5 | 2600 | 90 | 62 | 105 | 74.9 | 0.997 | 26.6 | 74.7 | 6.7 | 31
KJ078 | 6.5 | 2600 | 70 | 67 | 105 | 74.9 | 0.363 | 9.69 | 27.2 | 6.7 | 31
KJ078 | 6.5 | 2600 | 75 | 67 | 105 | 74.9 | 0.541 | 14.42 | 40.5 | 6.7 | 31
KJ078 | 6.5 | 2600 | 80 | 67 | 105 | 74.9 | 0.717 | 19.12 | 53.7 | 6.7 | 31
KJ078 | 6.5 | 2600 | 85 | 67 | 105 | 74.9 | 0.852 | 22.72 | 63.8 | 6.7 | 31
KJ078 | 6.5 | 2600 | 90 | 67 | 105 | 74.9 | 0.985 | 26.28 | 73.8 | 6.7 | 31
KJ078 | 6.5 | 2600 | 75 | 72 | 105 | 80.6 | 0.341 | 9.79 | 27.5 | 6.7 | 31
KJ078 | 6.5 | 2600 | 80 | 72 | 105 | 80.6 | 0.502 | 14.42 | 40.5 | 6.7 | 31
KJ078 | 6.5 | 2600 | 85 | 72 | 105 | 80.6 | 0.664 | 19.05 | 53.5 | 6.7 | 31
KJ078 | 6.5 | 2600 | 90 | 72 | 105 | 80.6 | 0.825 | 23.68 | 66.5 | 6.7 | 31
KJ078 | 6.5 | 2600 | 80 | 77 | 105 | 86.2 | 0.317 | 9.72 | 27.3 | 6.8 | 31
KJ078 | 6.5 | 2600 | 85 | 77 | 105 | 86.2 | 0.501 | 15.38 | 43.2 | 6.8 | 31
KJ078 | 6.5 | 2600 | 90 | 77 | 105 | 86.2 | 0.687 | 21.08 | 59.2 | 6.8 | 31
KJ078 | 6.5 | 2600 | 65 | 57 | 115 | 70.2 | 0.507 | 12.68 | 35.6 | 7.7 | 32
KJ078 | 6.5 | 2600 | 70 | 57 | 115 | 70.2 | 0.708 | 17.7 | 49.7 | 7.7 | 32
KJ078 | 6.5 | 2600 | 75 | 57 | 115 | 70.2 | 0.91 | 22.76 | 63.9 | 7.7 | 32
KJ078 | 6.5 | 2600 | 80 | 57 | 115 | 70.2 | 1 | 25 | 70.2 | 7.7 | 32
KJ078 | 6.5 | 2600 | 85 | 57 | 115 | 70.2 | 1 | 25 | 70.2 | 7.7 | 32
KJ078 | 6.5 | 2600 | 90 | 57 | 115 | 70.2 | 1 | 25 | 70.2 | 7.7 | 32
KJ078 | 6.5 | 2600 | 65 | 62 | 115 | 70.2 | 0.332 | 8.3 | 23.3 | 7.7 | 32
KJ078 | 6.5 | 2600 | 70 | 62 | 115 | 70.2 | 0.527 | 13.18 | 37 | 7.7 | 32
KJ078 | 6.5 | 2600 | 75 | 62 | 115 | 70.2 | 0.722 | 18.06 | 50.7 | 7.7 | 32
KJ078 | 6.5 | 2600 | 80 | 62 | 115 | 70.2 | 0.919 | 22.97 | 64.5 | 7.7 | 32
KJ078 | 6.5 | 2600 | 85 | 62 | 115 | 70.2 | 0.959 | 23.97 | 67.3 | 7.7 | 32
KJ078 | 6.5 | 2600 | 90 | 62 | 115 | 70.2 | 0.999 | 24.96 | 70.1 | 7.7 | 32
KJ078 | 6.5 | 2600 | 70 | 67 | 115 | 70.2 | 0.346 | 8.65 | 24.3 | 7.7 | 32
KJ078 | 6.5 | 2600 | 75 | 67 | 115 | 70.2 | 0.536 | 13.39 | 37.6 | 7.7 | 32
KJ078 | 6.5 | 2600 | 80 | 67 | 115 | 70.2 | 0.725 | 18.13 | 50.9 | 7.7 | 32
KJ078 | 6.5 | 2600 | 85 | 67 | 115 | 70.2 | 0.853 | 21.33 | 59.9 | 7.7 | 32
KJ078 | 6.5 | 2600 | 90 | 67 | 115 | 70.2 | 0.981 | 24.54 | 68.9 | 7.7 | 32
KJ078 | 6.5 | 2600 | 75 | 72 | 115 | 74.3 | 0.33 | 8.73 | 24.5 | 7.7 | 32
KJ078 | 6.5 | 2600 | 80 | 72 | 115 | 74.3 | 0.503 | 13.32 | 37.4 | 7.7 | 32
KJ078 | 6.5 | 2600 | 85 | 72 | 115 | 74.3 | 0.677 | 17.91 | 50.3 | 7.7 | 32
KJ078 | 6.5 | 2600 | 90 | 72 | 115 | 74.3 | 0.851 | 22.51 | 63.2 | 7.7 | 32
KJ078 | 6.5 | 2600 | 80 | 77 | 115 | 78.5 | 0.304 | 8.51 | 23.9 | 7.7 | 32
KJ078 | 6.5 | 2600 | 85 | 77 | 115 | 78.5 | 0.518 | 14.49 | 40.7 | 7.7 | 32
KJ078 | 6.5 | 2600 | 90 | 77 | 115 | 78.5 | 0.732 | 20.48 | 57.5 | 7.7 | 32
KJ078 | 6.5 | 2600 | 65 | 57 | 125 | 65 | 0.494 | 11.43 | 32.1 | 8.6 | 32
KJ078 | 6.5 | 2600 | 70 | 57 | 125 | 65 | 0.718 | 16.63 | 46.7 | 8.6 | 32
KJ078 | 6.5 | 2600 | 75 | 57 | 125 | 65 | 0.943 | 21.83 | 61.3 | 8.6 | 32
KJ078 | 6.5 | 2600 | 80 | 57 | 125 | 65 | 1 | 23.15 | 65 | 8.6 | 32
KJ078 | 6.5 | 2600 | 85 | 57 | 125 | 65 | 1 | 23.15 | 65 | 8.6 | 32
KJ078 | 6.5 | 2600 | 90 | 57 | 125 | 65 | 1 | 23.15 | 65 | 8.6 | 32
KJ078 | 6.5 | 2600 | 65 | 62 | 125 | 65 | 0.308 | 7.12 | 20 | 8.6 | 32
KJ078 | 6.5 | 2600 | 70 | 62 | 125 | 65 | 0.523 | 12.11 | 34 | 8.6 | 32
KJ078 | 6.5 | 2600 | 75 | 62 | 125 | 65 | 0.738 | 17.09 | 48 | 8.6 | 32
KJ078 | 6.5 | 2600 | 80 | 62 | 125 | 65 | 0.955 | 22.12 | 62.1 | 8.6 | 32
KJ078 | 6.5 | 2600 | 85 | 62 | 125 | 65 | 0.978 | 22.65 | 63.6 | 8.6 | 32
KJ078 | 6.5 | 2600 | 90 | 62 | 125 | 65 | 1 | 23.15 | 65 | 8.6 | 32
KJ078 | 6.5 | 2600 | 70 | 67 | 125 | 65.1 | 0.329 | 7.62 | 21.4 | 8.6 | 32
KJ078 | 6.5 | 2600 | 75 | 67 | 125 | 65.1 | 0.535 | 12.39 | 34.8 | 8.6 | 32
KJ078 | 6.5 | 2600 | 80 | 67 | 125 | 65.1 | 0.74 | 17.17 | 48.2 | 8.6 | 32
KJ078 | 6.5 | 2600 | 85 | 67 | 125 | 65.1 | 0.862 | 19.98 | 56.1 | 8.6 | 32
KJ078 | 6.5 | 2600 | 90 | 67 | 125 | 65.1 | 0.982 | 22.76 | 63.9 | 8.6 | 32
KJ078 | 6.5 | 2600 | 75 | 72 | 125 | 68 | 0.316 | 7.66 | 21.5 | 8.7 | 32
KJ078 | 6.5 | 2600 | 80 | 72 | 125 | 68 | 0.504 | 12.22 | 34.3 | 8.7 | 32
KJ078 | 6.5 | 2600 | 85 | 72 | 125 | 68 | 0.693 | 16.77 | 47.1 | 8.7 | 32
KJ078 | 6.5 | 2600 | 90 | 72 | 125 | 68 | 0.881 | 21.33 | 59.9 | 8.7 | 32
KJ078 | 6.5 | 2600 | 80 | 77 | 125 | 70.8 | 0.288 | 7.26 | 20.4 | 8.7 | 32
KJ078 | 6.5 | 2600 | 85 | 77 | 125 | 70.8 | 0.538 | 13.57 | 38.1 | 8.7 | 32
KJ078 | 6.5 | 2600 | 90 | 77 | 125 | 70.8 | 0.788 | 19.87 | 55.8 | 8.7 | 32
KJ078 | 6.5 | 2925 | 65 | 57 | 75 | 91 | 0.552 | 15.89 | 50.2 | 4.4 | 31
KJ078 | 6.5 | 2925 | 70 | 57 | 75 | 91 | 0.7 | 20.16 | 63.7 | 4.4 | 31
KJ078 | 6.5 | 2925 | 75 | 57 | 75 | 91 | 0.847 | 24.41 | 77.1 | 4.4 | 31
KJ078 | 6.5 | 2925 | 80 | 57 | 75 | 91 | 0.996 | 28.68 | 90.6 | 4.4 | 31
KJ078 | 6.5 | 2925 | 85 | 57 | 75 | 91 | 1 | 28.81 | 91 | 4.4 | 31
KJ078 | 6.5 | 2925 | 90 | 57 | 75 | 91 | 1 | 28.81 | 91 | 4.4 | 31
KJ078 | 6.5 | 2925 | 65 | 62 | 75 | 92.3 | 0.402 | 11.74 | 37.1 | 4.4 | 31
KJ078 | 6.5 | 2925 | 70 | 62 | 75 | 92.3 | 0.549 | 16.05 | 50.7 | 4.4 | 31
KJ078 | 6.5 | 2925 | 75 | 62 | 75 | 92.3 | 0.693 | 20.26 | 64 | 4.4 | 31
KJ078 | 6.5 | 2925 | 80 | 62 | 75 | 92.3 | 0.845 | 24.69 | 78 | 4.4 | 31
KJ078 | 6.5 | 2925 | 85 | 62 | 75 | 92.3 | 0.923 | 26.97 | 85.2 | 4.4 | 31
KJ078 | 6.5 | 2925 | 90 | 62 | 75 | 92.3 | 0.986 | 28.81 | 91 | 4.4 | 31
KJ078 | 6.5 | 2925 | 70 | 67 | 75 | 92.7 | 0.408 | 11.97 | 37.8 | 4.3 | 31
KJ078 | 6.5 | 2925 | 75 | 67 | 75 | 92.7 | 0.556 | 16.3 | 51.5 | 4.3 | 31
KJ078 | 6.5 | 2925 | 80 | 67 | 75 | 92.7 | 0.707 | 20.73 | 65.5 | 4.3 | 31
KJ078 | 6.5 | 2925 | 85 | 67 | 75 | 92.7 | 0.847 | 24.85 | 78.5 | 4.3 | 31
KJ078 | 6.5 | 2925 | 90 | 67 | 75 | 92.7 | 0.982 | 28.81 | 91 | 4.3 | 31
KJ078 | 6.5 | 2925 | 75 | 72 | 75 | 102.7 | 0.379 | 12.31 | 38.9 | 4.3 | 31
KJ078 | 6.5 | 2925 | 80 | 72 | 75 | 102.7 | 0.516 | 16.78 | 53 | 4.3 | 31
KJ078 | 6.5 | 2925 | 85 | 72 | 75 | 102.7 | 0.653 | 21.24 | 67.1 | 4.3 | 31
KJ078 | 6.5 | 2925 | 90 | 72 | 75 | 102.7 | 0.791 | 25.7 | 81.2 | 4.3 | 31
KJ078 | 6.5 | 2925 | 65 | 57 | 85 | 86.5 | 0.549 | 15.04 | 47.5 | 5.1 | 31
KJ078 | 6.5 | 2925 | 70 | 57 | 85 | 86.5 | 0.713 | 19.53 | 61.7 | 5.1 | 31
KJ078 | 6.5 | 2925 | 75 | 57 | 85 | 86.5 | 0.876 | 23.99 | 75.8 | 5.1 | 31
KJ078 | 6.5 | 2925 | 80 | 57 | 85 | 86.5 | 1 | 27.38 | 86.5 | 5.1 | 31
KJ078 | 6.5 | 2925 | 85 | 57 | 85 | 86.5 | 1 | 27.38 | 86.5 | 5.1 | 31
KJ078 | 6.5 | 2925 | 90 | 57 | 85 | 86.5 | 1 | 27.38 | 86.5 | 5.1 | 31
KJ078 | 6.5 | 2925 | 65 | 62 | 85 | 87 | 0.389 | 10.7 | 33.8 | 5.1 | 31
KJ078 | 6.5 | 2925 | 70 | 62 | 85 | 87 | 0.552 | 15.19 | 48 | 5.1 | 31
KJ078 | 6.5 | 2925 | 75 | 62 | 85 | 87 | 0.714 | 19.66 | 62.1 | 5.1 | 31
KJ078 | 6.5 | 2925 | 80 | 62 | 85 | 87 | 0.879 | 24.22 | 76.5 | 5.1 | 31
KJ078 | 6.5 | 2925 | 85 | 62 | 85 | 87 | 0.945 | 26.02 | 82.2 | 5.1 | 31
KJ078 | 6.5 | 2925 | 90 | 62 | 85 | 87 | 0.993 | 27.35 | 86.4 | 5.1 | 31
KJ078 | 6.5 | 2925 | 70 | 67 | 85 | 87.5 | 0.393 | 10.89 | 34.4 | 5 | 31
KJ078 | 6.5 | 2925 | 75 | 67 | 85 | 87.5 | 0.555 | 15.38 | 48.6 | 5 | 31
KJ078 | 6.5 | 2925 | 80 | 67 | 85 | 87.5 | 0.719 | 19.91 | 62.9 | 5 | 31
KJ078 | 6.5 | 2925 | 85 | 67 | 85 | 87.5 | 0.863 | 23.9 | 75.5 | 5 | 31
KJ078 | 6.5 | 2925 | 90 | 67 | 85 | 87.5 | 0.986 | 27.32 | 86.3 | 5 | 31
KJ078 | 6.5 | 2925 | 75 | 72 | 85 | 95.6 | 0.367 | 11.11 | 35.1 | 5 | 31
KJ078 | 6.5 | 2925 | 80 | 72 | 85 | 95.6 | 0.517 | 15.64 | 49.4 | 5 | 31
KJ078 | 6.5 | 2925 | 85 | 72 | 85 | 95.6 | 0.667 | 20.2 | 63.8 | 5 | 31
KJ078 | 6.5 | 2925 | 90 | 72 | 85 | 95.6 | 0.817 | 24.72 | 78.1 | 5 | 31
KJ078 | 6.5 | 2925 | 65 | 57 | 95 | 82.1 | 0.544 | 14.15 | 44.7 | 5.8 | 31
KJ078 | 6.5 | 2925 | 70 | 57 | 95 | 82.1 | 0.726 | 18.87 | 59.6 | 5.8 | 31
KJ078 | 6.5 | 2925 | 75 | 57 | 95 | 82.1 | 0.909 | 23.62 | 74.6 | 5.8 | 31
KJ078 | 6.5 | 2925 | 80 | 57 | 95 | 82.1 | 1 | 25.99 | 82.1 | 5.8 | 31
KJ078 | 6.5 | 2925 | 85 | 57 | 95 | 82.1 | 1 | 25.99 | 82.1 | 5.8 | 31
KJ078 | 6.5 | 2925 | 90 | 57 | 95 | 82.1 | 1 | 25.99 | 82.1 | 5.8 | 31
KJ078 | 6.5 | 2925 | 65 | 62 | 95 | 82.2 | 0.371 | 9.65 | 30.5 | 5.8 | 31
KJ078 | 6.5 | 2925 | 70 | 62 | 95 | 82.2 | 0.551 | 14.34 | 45.3 | 5.8 | 31
KJ078 | 6.5 | 2925 | 75 | 62 | 95 | 82.2 | 0.731 | 19.03 | 60.1 | 5.8 | 31
KJ078 | 6.5 | 2925 | 80 | 62 | 95 | 82.2 | 0.911 | 23.71 | 74.9 | 5.8 | 31
KJ078 | 6.5 | 2925 | 85 | 62 | 95 | 82.2 | 0.964 | 25.07 | 79.2 | 5.8 | 31
KJ078 | 6.5 | 2925 | 90 | 62 | 95 | 82.2 | 0.999 | 25.99 | 82.1 | 5.8 | 31
KJ078 | 6.5 | 2925 | 70 | 67 | 95 | 82.3 | 0.375 | 9.78 | 30.9 | 5.8 | 31
KJ078 | 6.5 | 2925 | 75 | 67 | 95 | 82.3 | 0.555 | 14.47 | 45.7 | 5.8 | 31
KJ078 | 6.5 | 2925 | 80 | 67 | 95 | 82.3 | 0.734 | 19.12 | 60.4 | 5.8 | 31
KJ078 | 6.5 | 2925 | 85 | 67 | 95 | 82.3 | 0.88 | 22.92 | 72.4 | 5.8 | 31
KJ078 | 6.5 | 2925 | 90 | 67 | 95 | 82.3 | 0.998 | 25.99 | 82.1 | 5.8 | 31
KJ078 | 6.5 | 2925 | 75 | 72 | 95 | 88.5 | 0.353 | 9.88 | 31.2 | 5.8 | 31
KJ078 | 6.5 | 2925 | 80 | 72 | 95 | 88.5 | 0.518 | 14.5 | 45.8 | 5.8 | 31
KJ078 | 6.5 | 2925 | 85 | 72 | 95 | 88.5 | 0.682 | 19.12 | 60.4 | 5.8 | 31
KJ078 | 6.5 | 2925 | 90 | 72 | 95 | 88.5 | 0.849 | 23.77 | 75.1 | 5.8 | 31
KJ078 | 6.5 | 2925 | 65 | 57 | 105 | 77.4 | 0.532 | 13.04 | 41.2 | 6.7 | 31
KJ078 | 6.5 | 2925 | 70 | 57 | 105 | 77.4 | 0.73 | 17.89 | 56.5 | 6.7 | 31
KJ078 | 6.5 | 2925 | 75 | 57 | 105 | 77.4 | 0.929 | 22.76 | 71.9 | 6.7 | 31
KJ078 | 6.5 | 2925 | 80 | 57 | 105 | 77.4 | 1 | 24.5 | 77.4 | 6.7 | 31
KJ078 | 6.5 | 2925 | 85 | 57 | 105 | 77.4 | 1 | 24.5 | 77.4 | 6.7 | 31
KJ078 | 6.5 | 2925 | 90 | 57 | 105 | 77.4 | 1 | 24.5 | 77.4 | 6.7 | 31
KJ078 | 6.5 | 2925 | 65 | 62 | 105 | 77.5 | 0.351 | 8.61 | 27.2 | 6.7 | 31
KJ078 | 6.5 | 2925 | 70 | 62 | 105 | 77.5 | 0.545 | 13.36 | 42.2 | 6.7 | 31
KJ078 | 6.5 | 2925 | 75 | 62 | 105 | 77.5 | 0.739 | 18.14 | 57.3 | 6.7 | 31
KJ078 | 6.5 | 2925 | 80 | 62 | 105 | 77.5 | 0.933 | 22.89 | 72.3 | 6.7 | 31
KJ078 | 6.5 | 2925 | 85 | 62 | 105 | 77.5 | 0.97 | 23.81 | 75.2 | 6.7 | 31
KJ078 | 6.5 | 2925 | 90 | 62 | 105 | 77.5 | 0.997 | 24.47 | 77.3 | 6.7 | 31
KJ078 | 6.5 | 2925 | 70 | 67 | 105 | 77.6 | 0.36 | 8.83 | 27.9 | 6.7 | 31
KJ078 | 6.5 | 2925 | 75 | 67 | 105 | 77.6 | 0.55 | 13.52 | 42.7 | 6.7 | 31
KJ078 | 6.5 | 2925 | 80 | 67 | 105 | 77.6 | 0.74 | 18.17 | 57.4 | 6.7 | 31
KJ078 | 6.5 | 2925 | 85 | 67 | 105 | 77.6 | 0.876 | 21.53 | 68 | 6.7 | 31
KJ078 | 6.5 | 2925 | 90 | 67 | 105 | 77.6 | 0.995 | 24.44 | 77.2 | 6.7 | 31
KJ078 | 6.5 | 2925 | 75 | 72 | 105 | 82.1 | 0.342 | 8.9 | 28.1 | 6.7 | 31
KJ078 | 6.5 | 2925 | 80 | 72 | 105 | 82.1 | 0.518 | 13.45 | 42.5 | 6.7 | 31
KJ078 | 6.5 | 2925 | 85 | 72 | 105 | 82.1 | 0.694 | 18.04 | 57 | 6.7 | 31
KJ078 | 6.5 | 2925 | 90 | 72 | 105 | 82.1 | 0.871 | 22.63 | 71.5 | 6.7 | 31
KJ078 | 6.5 | 2925 | 65 | 57 | 115 | 72.4 | 0.519 | 11.9 | 37.6 | 7.7 | 32
KJ078 | 6.5 | 2925 | 70 | 57 | 115 | 72.4 | 0.738 | 16.9 | 53.4 | 7.7 | 32
KJ078 | 6.5 | 2925 | 75 | 57 | 115 | 72.4 | 0.956 | 21.91 | 69.2 | 7.7 | 32
KJ078 | 6.5 | 2925 | 80 | 57 | 115 | 72.4 | 1 | 22.92 | 72.4 | 7.7 | 32
KJ078 | 6.5 | 2925 | 85 | 57 | 115 | 72.4 | 1 | 22.92 | 72.4 | 7.7 | 32
KJ078 | 6.5 | 2925 | 90 | 57 | 115 | 72.4 | 1 | 22.92 | 72.4 | 7.7 | 32
KJ078 | 6.5 | 2925 | 65 | 62 | 115 | 72.6 | 0.328 | 7.53 | 23.8 | 7.7 | 32
KJ078 | 6.5 | 2925 | 70 | 62 | 115 | 72.6 | 0.539 | 12.38 | 39.1 | 7.7 | 32
KJ078 | 6.5 | 2925 | 75 | 62 | 115 | 72.6 | 0.751 | 17.25 | 54.5 | 7.7 | 32
KJ078 | 6.5 | 2925 | 80 | 62 | 115 | 72.6 | 0.961 | 22.1 | 69.8 | 7.7 | 32
KJ078 | 6.5 | 2925 | 85 | 62 | 115 | 72.6 | 0.979 | 22.51 | 71.1 | 7.7 | 32
KJ078 | 6.5 | 2925 | 90 | 62 | 115 | 72.6 | 0.997 | 22.92 | 72.4 | 7.7 | 32
KJ078 | 6.5 | 2925 | 70 | 67 | 115 | 72.8 | 0.341 | 7.85 | 24.8 | 7.7 | 32
KJ078 | 6.5 | 2925 | 75 | 67 | 115 | 72.8 | 0.545 | 12.57 | 39.7 | 7.7 | 32
KJ078 | 6.5 | 2925 | 80 | 67 | 115 | 72.8 | 0.749 | 17.25 | 54.5 | 7.7 | 32
KJ078 | 6.5 | 2925 | 85 | 67 | 115 | 72.8 | 0.872 | 20.1 | 63.5 | 7.7 | 32
KJ078 | 6.5 | 2925 | 90 | 67 | 115 | 72.8 | 0.995 | 22.92 | 72.4 | 7.7 | 32
KJ078 | 6.5 | 2925 | 75 | 72 | 115 | 75.7 | 0.329 | 7.88 | 24.9 | 7.7 | 32
KJ078 | 6.5 | 2925 | 80 | 72 | 115 | 75.7 | 0.518 | 12.41 | 39.2 | 7.7 | 32
KJ078 | 6.5 | 2925 | 85 | 72 | 115 | 75.7 | 0.708 | 16.97 | 53.6 | 7.7 | 32
KJ078 | 6.5 | 2925 | 90 | 72 | 115 | 75.7 | 0.897 | 21.49 | 67.9 | 7.7 | 32
KJ078 | 6.5 | 2925 | 65 | 57 | 125 | 68.3 | 0.498 | 10.76 | 34 | 8.6 | 32
KJ078 | 6.5 | 2925 | 70 | 57 | 125 | 68.3 | 0.736 | 15.92 | 50.3 | 8.6 | 32
KJ078 | 6.5 | 2925 | 75 | 57 | 125 | 68.3 | 0.975 | 21.08 | 66.6 | 8.6 | 32
KJ078 | 6.5 | 2925 | 80 | 57 | 125 | 68.3 | 0.99 | 21.4 | 67.6 | 8.6 | 32
KJ078 | 6.5 | 2925 | 85 | 57 | 125 | 68.3 | 0.99 | 21.4 | 67.6 | 8.6 | 32
KJ078 | 6.5 | 2925 | 90 | 57 | 125 | 68.3 | 0.99 | 21.4 | 67.6 | 8.6 | 32
KJ078 | 6.5 | 2925 | 65 | 62 | 125 | 68.4 | 0.3 | 6.49 | 20.5 | 8.6 | 32
KJ078 | 6.5 | 2925 | 70 | 62 | 125 | 68.4 | 0.528 | 11.43 | 36.1 | 8.6 | 32
KJ078 | 6.5 | 2925 | 75 | 62 | 125 | 68.4 | 0.754 | 16.33 | 51.6 | 8.6 | 32
KJ078 | 6.5 | 2925 | 80 | 62 | 125 | 68.4 | 0.98 | 21.21 | 67 | 8.6 | 32
KJ078 | 6.5 | 2925 | 85 | 62 | 125 | 68.4 | 0.98 | 21.21 | 67 | 8.6 | 32
KJ078 | 6.5 | 2925 | 90 | 62 | 125 | 68.4 | 0.98 | 21.21 | 67 | 8.6 | 32
KJ078 | 6.5 | 2925 | 70 | 67 | 125 | 68.5 | 0.318 | 6.9 | 21.8 | 8.6 | 32
KJ078 | 6.5 | 2925 | 75 | 67 | 125 | 68.5 | 0.536 | 11.62 | 36.7 | 8.6 | 32
KJ078 | 6.5 | 2925 | 80 | 67 | 125 | 68.5 | 0.753 | 16.33 | 51.6 | 8.6 | 32
KJ078 | 6.5 | 2925 | 85 | 67 | 125 | 68.5 | 0.861 | 18.68 | 59 | 8.6 | 32
KJ078 | 6.5 | 2925 | 90 | 67 | 125 | 68.5 | 0.969 | 21.02 | 66.4 | 8.6 | 32
KJ078 | 6.5 | 2925 | 75 | 72 | 125 | 69.2 | 0.314 | 6.87 | 21.7 | 8.6 | 32
KJ078 | 6.5 | 2925 | 80 | 72 | 125 | 69.2 | 0.519 | 11.36 | 35.9 | 8.6 | 32
KJ078 | 6.5 | 2925 | 85 | 72 | 125 | 69.2 | 0.724 | 15.86 | 50.1 | 8.6 | 32
KJ078 | 6.5 | 2925 | 90 | 72 | 125 | 69.2 | 0.929 | 20.35 | 64.3 | 8.6 | 32
KJ078 | 6.5 | 3250 | 65 | 57 | 75 | 93 | 0.575 | 15.24 | 53.5 | 4.3 | 31
KJ078 | 6.5 | 3250 | 70 | 57 | 75 | 93 | 0.73 | 19.34 | 67.9 | 4.3 | 31
KJ078 | 6.5 | 3250 | 75 | 57 | 75 | 93 | 0.885 | 23.45 | 82.3 | 4.3 | 31
KJ078 | 6.5 | 3250 | 80 | 57 | 75 | 93 | 1 | 26.5 | 93 | 4.3 | 31
KJ078 | 6.5 | 3250 | 85 | 57 | 75 | 93 | 1 | 26.5 | 93 | 4.3 | 31
KJ078 | 6.5 | 3250 | 90 | 57 | 75 | 93 | 1 | 26.5 | 93 | 4.3 | 31
KJ078 | 6.5 | 3250 | 65 | 62 | 75 | 94.3 | 0.407 | 10.94 | 38.4 | 4.3 | 31
KJ078 | 6.5 | 3250 | 70 | 62 | 75 | 94.3 | 0.564 | 15.16 | 53.2 | 4.3 | 31
KJ078 | 6.5 | 3250 | 75 | 62 | 75 | 94.3 | 0.722 | 19.4 | 68.1 | 4.3 | 31
KJ078 | 6.5 | 3250 | 80 | 62 | 75 | 94.3 | 0.88 | 23.65 | 83 | 4.3 | 31
KJ078 | 6.5 | 3250 | 85 | 62 | 75 | 94.3 | 0.954 | 25.64 | 90 | 4.3 | 31
KJ078 | 6.5 | 3250 | 90 | 62 | 75 | 94.3 | 0.986 | 26.5 | 93 | 4.3 | 31
KJ078 | 6.5 | 3250 | 70 | 67 | 75 | 95.4 | 0.405 | 11 | 38.6 | 4.3 | 31
KJ078 | 6.5 | 3250 | 75 | 67 | 75 | 95.4 | 0.565 | 15.36 | 53.9 | 4.3 | 31
KJ078 | 6.5 | 3250 | 80 | 67 | 75 | 95.4 | 0.725 | 19.72 | 69.2 | 4.3 | 31
KJ078 | 6.5 | 3250 | 85 | 67 | 75 | 95.4 | 0.876 | 23.82 | 83.6 | 4.3 | 31
KJ078 | 6.5 | 3250 | 90 | 67 | 75 | 95.4 | 0.975 | 26.5 | 93 | 4.3 | 31
KJ078 | 6.5 | 3250 | 75 | 72 | 75 | 105.4 | 0.377 | 11.31 | 39.7 | 4.3 | 31
KJ078 | 6.5 | 3250 | 80 | 72 | 75 | 105.4 | 0.526 | 15.78 | 55.4 | 4.3 | 31
KJ078 | 6.5 | 3250 | 85 | 72 | 75 | 105.4 | 0.676 | 20.28 | 71.2 | 4.3 | 31
KJ078 | 6.5 | 3250 | 90 | 72 | 75 | 105.4 | 0.825 | 24.79 | 87 | 4.3 | 31
KJ078 | 6.5 | 3250 | 65 | 57 | 85 | 90 | 0.558 | 14.3 | 50.2 | 5 | 31
KJ078 | 6.5 | 3250 | 70 | 57 | 85 | 90 | 0.73 | 18.72 | 65.7 | 5 | 31
KJ078 | 6.5 | 3250 | 75 | 57 | 85 | 90 | 0.902 | 23.13 | 81.2 | 5 | 31
KJ078 | 6.5 | 3250 | 80 | 57 | 85 | 90 | 1 | 25.64 | 90 | 5 | 31
KJ078 | 6.5 | 3250 | 85 | 57 | 85 | 90 | 1 | 25.64 | 90 | 5 | 31
KJ078 | 6.5 | 3250 | 90 | 57 | 85 | 90 | 1 | 25.64 | 90 | 5 | 31
KJ078 | 6.5 | 3250 | 65 | 62 | 85 | 90 | 0.386 | 9.89 | 34.7 | 5 | 31
KJ078 | 6.5 | 3250 | 70 | 62 | 85 | 90 | 0.56 | 14.36 | 50.4 | 5 | 31
KJ078 | 6.5 | 3250 | 75 | 62 | 85 | 90 | 0.734 | 18.83 | 66.1 | 5 | 31
KJ078 | 6.5 | 3250 | 80 | 62 | 85 | 90 | 0.908 | 23.28 | 81.7 | 5 | 31
KJ078 | 6.5 | 3250 | 85 | 62 | 85 | 90 | 0.966 | 24.76 | 86.9 | 5 | 31
KJ078 | 6.5 | 3250 | 90 | 62 | 85 | 90 | 1 | 25.64 | 90 | 5 | 31
KJ078 | 6.5 | 3250 | 70 | 67 | 85 | 90 | 0.39 | 10 | 35.1 | 5 | 31
KJ078 | 6.5 | 3250 | 75 | 67 | 85 | 90 | 0.566 | 14.5 | 50.9 | 5 | 31
KJ078 | 6.5 | 3250 | 80 | 67 | 85 | 90 | 0.741 | 19 | 66.7 | 5 | 31
KJ078 | 6.5 | 3250 | 85 | 67 | 85 | 90 | 0.893 | 22.91 | 80.4 | 5 | 31
KJ078 | 6.5 | 3250 | 90 | 67 | 85 | 90 | 1 | 25.64 | 90 | 5 | 31
KJ078 | 6.5 | 3250 | 75 | 72 | 85 | 97.8 | 0.366 | 10.2 | 35.8 | 5 | 31
KJ078 | 6.5 | 3250 | 80 | 72 | 85 | 97.8 | 0.529 | 14.73 | 51.7 | 5 | 31
KJ078 | 6.5 | 3250 | 85 | 72 | 85 | 97.8 | 0.692 | 19.29 | 67.7 | 5 | 31
KJ078 | 6.5 | 3250 | 90 | 72 | 85 | 97.8 | 0.855 | 23.82 | 83.6 | 5 | 31
KJ078 | 6.5 | 3250 | 65 | 57 | 95 | 84.2 | 0.556 | 13.33 | 46.8 | 5.7 | 31
KJ078 | 6.5 | 3250 | 70 | 57 | 95 | 84.2 | 0.754 | 18.09 | 63.5 | 5.7 | 31
KJ078 | 6.5 | 3250 | 75 | 57 | 95 | 84.2 | 0.951 | 22.82 | 80.1 | 5.7 | 31
KJ078 | 6.5 | 3250 | 80 | 57 | 95 | 84.2 | 0.998 | 23.93 | 84 | 5.7 | 31
KJ078 | 6.5 | 3250 | 85 | 57 | 95 | 84.2 | 0.998 | 23.93 | 84 | 5.7 | 31
KJ078 | 6.5 | 3250 | 90 | 57 | 95 | 84.2 | 0.998 | 23.93 | 84 | 5.7 | 31
KJ078 | 6.5 | 3250 | 65 | 62 | 95 | 84.5 | 0.368 | 8.86 | 31.1 | 5.7 | 31
KJ078 | 6.5 | 3250 | 70 | 62 | 95 | 84.5 | 0.563 | 13.56 | 47.6 | 5.7 | 31
KJ078 | 6.5 | 3250 | 75 | 62 | 95 | 84.5 | 0.759 | 18.26 | 64.1 | 5.7 | 31
KJ078 | 6.5 | 3250 | 80 | 62 | 95 | 84.5 | 0.953 | 22.93 | 80.5 | 5.7 | 31
KJ078 | 6.5 | 3250 | 85 | 62 | 95 | 84.5 | 0.992 | 23.87 | 83.8 | 5.7 | 31
KJ078 | 6.5 | 3250 | 90 | 62 | 95 | 84.5 | 0.994 | 23.93 | 84 | 5.7 | 31
KJ078 | 6.5 | 3250 | 70 | 67 | 95 | 84.8 | 0.374 | 9.03 | 31.7 | 5.7 | 31
KJ078 | 6.5 | 3250 | 75 | 67 | 95 | 84.8 | 0.566 | 13.68 | 48 | 5.7 | 31
KJ078 | 6.5 | 3250 | 80 | 67 | 95 | 84.8 | 0.758 | 18.32 | 64.3 | 5.7 | 31
KJ078 | 6.5 | 3250 | 85 | 67 | 95 | 84.8 | 0.912 | 22.02 | 77.3 | 5.7 | 31
KJ078 | 6.5 | 3250 | 90 | 67 | 95 | 84.8 | 0.991 | 23.93 | 84 | 5.7 | 31
KJ078 | 6.5 | 3250 | 75 | 72 | 95 | 90.1 | 0.354 | 9.09 | 31.9 | 5.7 | 31
KJ078 | 6.5 | 3250 | 80 | 72 | 95 | 90.1 | 0.534 | 13.7 | 48.1 | 5.7 | 31
KJ078 | 6.5 | 3250 | 85 | 72 | 95 | 90.1 | 0.713 | 18.29 | 64.2 | 5.7 | 31
KJ078 | 6.5 | 3250 | 90 | 72 | 95 | 90.1 | 0.891 | 22.88 | 80.3 | 5.7 | 31
KJ078 | 6.5 | 3250 | 65 | 57 | 105 | 80 | 0.54 | 12.31 | 43.2 | 6.7 | 31
KJ078 | 6.5 | 3250 | 70 | 57 | 105 | 80 | 0.754 | 17.18 | 60.3 | 6.7 | 31
KJ078 | 6.5 | 3250 | 75 | 57 | 105 | 80 | 0.968 | 22.05 | 77.4 | 6.7 | 31
KJ078 | 6.5 | 3250 | 80 | 57 | 105 | 80 | 0.986 | 22.48 | 78.9 | 6.7 | 31
KJ078 | 6.5 | 3250 | 85 | 57 | 105 | 80 | 0.986 | 22.48 | 78.9 | 6.7 | 31
KJ078 | 6.5 | 3250 | 90 | 57 | 105 | 80 | 0.986 | 22.48 | 78.9 | 6.7 | 31
KJ078 | 6.5 | 3250 | 65 | 62 | 105 | 80.1 | 0.346 | 7.89 | 27.7 | 6.7 | 31
KJ078 | 6.5 | 3250 | 70 | 62 | 105 | 80.1 | 0.554 | 12.65 | 44.4 | 6.7 | 31
KJ078 | 6.5 | 3250 | 75 | 62 | 105 | 80.1 | 0.763 | 17.41 | 61.1 | 6.7 | 31
KJ078 | 6.5 | 3250 | 80 | 62 | 105 | 80.1 | 0.971 | 22.17 | 77.8 | 6.7 | 31
KJ078 | 6.5 | 3250 | 85 | 62 | 105 | 80.1 | 0.984 | 22.45 | 78.8 | 6.7 | 31
KJ078 | 6.5 | 3250 | 90 | 62 | 105 | 80.1 | 0.984 | 22.45 | 78.8 | 6.7 | 31
KJ078 | 6.5 | 3250 | 70 | 67 | 105 | 80.2 | 0.357 | 8.15 | 28.6 | 6.7 | 31
KJ078 | 6.5 | 3250 | 75 | 67 | 105 | 80.2 | 0.56 | 12.79 | 44.9 | 6.7 | 31
KJ078 | 6.5 | 3250 | 80 | 67 | 105 | 80.2 | 0.763 | 17.44 | 61.2 | 6.7 | 31
KJ078 | 6.5 | 3250 | 85 | 67 | 105 | 80.2 | 0.9 | 20.57 | 72.2 | 6.7 | 31
KJ078 | 6.5 | 3250 | 90 | 67 | 105 | 80.2 | 0.98 | 22.39 | 78.6 | 6.7 | 31
KJ078 | 6.5 | 3250 | 75 | 72 | 105 | 83.6 | 0.342 | 8.15 | 28.6 | 6.7 | 31
KJ078 | 6.5 | 3250 | 80 | 72 | 105 | 83.6 | 0.533 | 12.71 | 44.6 | 6.7 | 31
KJ078 | 6.5 | 3250 | 85 | 72 | 105 | 83.6 | 0.724 | 17.24 | 60.5 | 6.7 | 31
KJ078 | 6.5 | 3250 | 90 | 72 | 105 | 83.6 | 0.915 | 21.79 | 76.5 | 6.7 | 31
KJ078 | 6.5 | 3250 | 65 | 57 | 115 | 75.3 | 0.526 | 11.28 | 39.6 | 7.7 | 32
KJ078 | 6.5 | 3250 | 70 | 57 | 115 | 75.3 | 0.758 | 16.27 | 57.1 | 7.7 | 32
KJ078 | 6.5 | 3250 | 75 | 57 | 115 | 75.3 | 0.981 | 21.05 | 73.9 | 7.7 | 32
KJ078 | 6.5 | 3250 | 80 | 57 | 115 | 75.3 | 0.981 | 21.05 | 73.9 | 7.7 | 32
KJ078 | 6.5 | 3250 | 85 | 57 | 115 | 75.3 | 0.981 | 21.05 | 73.9 | 7.7 | 32
KJ078 | 6.5 | 3250 | 90 | 57 | 115 | 75.3 | 0.981 | 21.05 | 73.9 | 7.7 | 32
KJ078 | 6.5 | 3250 | 65 | 62 | 115 | 75.4 | 0.322 | 6.92 | 24.3 | 7.7 | 32
KJ078 | 6.5 | 3250 | 70 | 62 | 115 | 75.4 | 0.548 | 11.77 | 41.3 | 7.7 | 32
KJ078 | 6.5 | 3250 | 75 | 62 | 115 | 75.4 | 0.772 | 16.58 | 58.2 | 7.7 | 32
KJ078 | 6.5 | 3250 | 80 | 62 | 115 | 75.4 | 0.996 | 21.4 | 75.1 | 7.7 | 32
KJ078 | 6.5 | 3250 | 85 | 62 | 115 | 75.4 | 0.995 | 21.37 | 75 | 7.7 | 32
KJ078 | 6.5 | 3250 | 70 | 67 | 115 | 75.5 | 0.336 | 7.24 | 25.4 | 7.6 | 32
KJ078 | 6.5 | 3250 | 75 | 67 | 115 | 75.5 | 0.552 | 11.88 | 41.7 | 7.6 | 32
KJ078 | 6.5 | 3250 | 80 | 67 | 115 | 75.5 | 0.77 | 16.55 | 58.1 | 7.6 | 32
KJ078 | 6.5 | 3250 | 85 | 67 | 115 | 75.5 | 0.889 | 19.12 | 67.1 | 7.6 | 32
KJ078 | 6.5 | 3250 | 90 | 67 | 115 | 75.5 | 0.976 | 21 | 73.7 | 7.6 | 32
KJ078 | 6.5 | 3250 | 75 | 72 | 115 | 77 | 0.329 | 7.21 | 25.3 | 7.6 | 32
KJ078 | 6.5 | 3250 | 80 | 72 | 115 | 77 | 0.534 | 11.71 | 41.1 | 7.6 | 32
KJ078 | 6.5 | 3250 | 85 | 72 | 115 | 77 | 0.739 | 16.21 | 56.9 | 7.6 | 32
KJ078 | 6.5 | 3250 | 90 | 72 | 115 | 77 | 0.943 | 20.68 | 72.6 | 7.6 | 32
KJ078 | 6.5 | 3250 | 65 | 57 | 125 | 70.1 | 0.514 | 10.26 | 36 | 8.7 | 32
KJ078 | 6.5 | 3250 | 70 | 57 | 125 | 70.1 | 0.77 | 15.38 | 54 | 8.7 | 32
KJ078 | 6.5 | 3250 | 75 | 57 | 125 | 70.1 | 0.981 | 19.6 | 68.8 | 8.7 | 32
KJ078 | 6.5 | 3250 | 80 | 57 | 125 | 70.1 | 0.981 | 19.6 | 68.8 | 8.7 | 32
KJ078 | 6.5 | 3250 | 85 | 57 | 125 | 70.1 | 0.981 | 19.6 | 68.8 | 8.7 | 32
KJ078 | 6.5 | 3250 | 90 | 57 | 125 | 70.1 | 0.981 | 19.6 | 68.8 | 8.7 | 32
KJ078 | 6.5 | 3250 | 65 | 62 | 125 | 70.3 | 0.297 | 5.95 | 20.9 | 8.6 | 32
KJ078 | 6.5 | 3250 | 70 | 62 | 125 | 70.3 | 0.542 | 10.85 | 38.1 | 8.6 | 32
KJ078 | 6.5 | 3250 | 75 | 62 | 125 | 70.3 | 0.785 | 15.73 | 55.2 | 8.6 | 32
KJ078 | 6.5 | 3250 | 80 | 62 | 125 | 70.3 | 0.979 | 19.6 | 68.8 | 8.6 | 32
KJ078 | 6.5 | 3250 | 85 | 62 | 125 | 70.3 | 0.979 | 19.6 | 68.8 | 8.6 | 32
KJ078 | 6.5 | 3250 | 90 | 62 | 125 | 70.3 | 0.979 | 19.6 | 68.8 | 8.6 | 32
KJ078 | 6.5 | 3250 | 70 | 67 | 125 | 70.4 | 0.315 | 6.32 | 22.2 | 8.6 | 32
KJ078 | 6.5 | 3250 | 75 | 67 | 125 | 70.4 | 0.548 | 11 | 38.6 | 8.6 | 32
KJ078 | 6.5 | 3250 | 80 | 67 | 125 | 70.4 | 0.781 | 15.67 | 55 | 8.6 | 32
KJ078 | 6.5 | 3250 | 85 | 67 | 125 | 70.4 | 0.881 | 17.66 | 62 | 8.6 | 32
KJ078 | 6.5 | 3250 | 90 | 67 | 125 | 70.4 | 0.977 | 19.6 | 68.8 | 8.6 | 32
KJ078 | 6.5 | 3250 | 75 | 72 | 125 | 70.5 | 0.312 | 6.27 | 22 | 8.6 | 32
KJ078 | 6.5 | 3250 | 80 | 72 | 125 | 70.5 | 0.533 | 10.71 | 37.6 | 8.6 | 32
KJ078 | 6.5 | 3250 | 85 | 72 | 125 | 70.5 | 0.755 | 15.16 | 53.2 | 8.6 | 32
KJ078 | 6.5 | 3250 | 90 | 72 | 125 | 70.5 | 0.976 | 19.6 | 68.8 | 8.6 | 32
KJ090 | 7.5 | 1875 | 65 | 62 | 75 | 88.3 | 0.445 | 19.41 | 39.3 | 4.6 | 33
KJ090 | 7.5 | 1875 | 70 | 62 | 75 | 88.3 | 0.541 | 23.6 | 47.8 | 4.6 | 33
KJ090 | 7.5 | 1875 | 75 | 62 | 75 | 88.3 | 0.644 | 28.1 | 56.9 | 4.6 | 33
KJ090 | 7.5 | 1875 | 80 | 62 | 75 | 88.3 | 0.733 | 31.95 | 64.7 | 4.6 | 33
KJ090 | 7.5 | 1875 | 85 | 62 | 75 | 88.3 | 0.887 | 38.67 | 78.3 | 4.6 | 33
KJ090 | 7.5 | 1875 | 90 | 62 | 75 | 88.3 | 1 | 43.6 | 88.3 | 4.6 | 33
KJ090 | 7.5 | 1875 | 70 | 67 | 75 | 97 | 0.41 | 19.65 | 39.8 | 4.7 | 33
KJ090 | 7.5 | 1875 | 75 | 67 | 75 | 97 | 0.512 | 24.54 | 49.7 | 4.7 | 33
KJ090 | 7.5 | 1875 | 80 | 67 | 75 | 97 | 0.598 | 28.64 | 58 | 4.7 | 33
KJ090 | 7.5 | 1875 | 85 | 67 | 75 | 97 | 0.72 | 34.47 | 69.8 | 4.7 | 33
KJ090 | 7.5 | 1875 | 90 | 67 | 75 | 97 | 0.841 | 40.3 | 81.6 | 4.7 | 33
KJ090 | 7.5 | 1875 | 75 | 72 | 75 | 108.8 | 0.382 | 20.54 | 41.6 | 4.7 | 33
KJ090 | 7.5 | 1875 | 80 | 72 | 75 | 108.8 | 0.472 | 25.33 | 51.3 | 4.7 | 33
KJ090 | 7.5 | 1875 | 85 | 72 | 75 | 108.8 | 0.561 | 30.12 | 61 | 4.7 | 33
KJ090 | 7.5 | 1875 | 90 | 72 | 75 | 108.8 | 0.65 | 34.91 | 70.7 | 4.7 | 33
KJ090 | 7.5 | 1875 | 80 | 77 | 75 | 120.5 | 0.37 | 22.02 | 44.6 | 4.8 | 33
KJ090 | 7.5 | 1875 | 85 | 77 | 75 | 120.5 | 0.433 | 25.78 | 52.2 | 4.8 | 33
KJ090 | 7.5 | 1875 | 90 | 77 | 75 | 120.5 | 0.497 | 29.58 | 59.9 | 4.8 | 33
KJ090 | 7.5 | 1875 | 65 | 62 | 85 | 83.8 | 0.427 | 17.68 | 35.8 | 5.5 | 33
KJ090 | 7.5 | 1875 | 70 | 62 | 85 | 83.8 | 0.542 | 22.42 | 45.4 | 5.5 | 33
KJ090 | 7.5 | 1875 | 75 | 62 | 85 | 83.8 | 0.661 | 27.36 | 55.4 | 5.5 | 33
KJ090 | 7.5 | 1875 | 80 | 62 | 85 | 83.8 | 0.772 | 31.95 | 64.7 | 5.5 | 33
KJ090 | 7.5 | 1875 | 85 | 62 | 85 | 83.8 | 0.914 | 37.83 | 76.6 | 5.5 | 33
KJ090 | 7.5 | 1875 | 90 | 62 | 85 | 83.8 | 1 | 41.38 | 83.8 | 5.5 | 33
KJ090 | 7.5 | 1875 | 70 | 67 | 85 | 91 | 0.403 | 18.12 | 36.7 | 5.5 | 33
KJ090 | 7.5 | 1875 | 75 | 67 | 85 | 91 | 0.513 | 23.06 | 46.7 | 5.5 | 33
KJ090 | 7.5 | 1875 | 80 | 67 | 85 | 91 | 0.613 | 27.56 | 55.8 | 5.5 | 33
KJ090 | 7.5 | 1875 | 85 | 67 | 85 | 91 | 0.745 | 33.48 | 67.8 | 5.5 | 33
KJ090 | 7.5 | 1875 | 90 | 67 | 85 | 91 | 0.876 | 39.36 | 79.7 | 5.5 | 33
KJ090 | 7.5 | 1875 | 75 | 72 | 85 | 101.4 | 0.369 | 18.47 | 37.4 | 5.5 | 33
KJ090 | 7.5 | 1875 | 80 | 72 | 85 | 101.4 | 0.464 | 23.21 | 47 | 5.5 | 33
KJ090 | 7.5 | 1875 | 85 | 72 | 85 | 101.4 | 0.557 | 27.9 | 56.5 | 5.5 | 33
KJ090 | 7.5 | 1875 | 90 | 72 | 85 | 101.4 | 0.651 | 32.59 | 66 | 5.5 | 33
KJ090 | 7.5 | 1875 | 80 | 77 | 85 | 111.8 | 0.341 | 18.81 | 38.1 | 5.5 | 33
KJ090 | 7.5 | 1875 | 85 | 77 | 85 | 111.8 | 0.404 | 22.32 | 45.2 | 5.5 | 33
KJ090 | 7.5 | 1875 | 90 | 77 | 85 | 111.8 | 0.468 | 25.83 | 52.3 | 5.5 | 33
KJ090 | 7.5 | 1875 | 65 | 62 | 95 | 79.3 | 0.407 | 15.95 | 32.3 | 6.2 | 33
KJ090 | 7.5 | 1875 | 70 | 62 | 95 | 79.3 | 0.544 | 21.28 | 43.1 | 6.2 | 33
KJ090 | 7.5 | 1875 | 75 | 62 | 95 | 79.3 | 0.681 | 26.67 | 54 | 6.2 | 33
KJ090 | 7.5 | 1875 | 80 | 62 | 95 | 79.3 | 0.817 | 32 | 64.8 | 6.2 | 33
KJ090 | 7.5 | 1875 | 85 | 62 | 95 | 79.3 | 0.945 | 36.99 | 74.9 | 6.2 | 33
KJ090 | 7.5 | 1875 | 90 | 62 | 95 | 79.3 | 1 | 39.16 | 79.3 | 6.2 | 33
KJ090 | 7.5 | 1875 | 70 | 67 | 95 | 84.9 | 0.396 | 16.59 | 33.6 | 6.2 | 33
KJ090 | 7.5 | 1875 | 75 | 67 | 95 | 84.9 | 0.514 | 21.53 | 43.6 | 6.2 | 33
KJ090 | 7.5 | 1875 | 80 | 67 | 95 | 84.9 | 0.633 | 26.52 | 53.7 | 6.2 | 33
KJ090 | 7.5 | 1875 | 85 | 67 | 95 | 84.9 | 0.775 | 32.49 | 65.8 | 6.2 | 33
KJ090 | 7.5 | 1875 | 90 | 67 | 95 | 84.9 | 0.918 | 38.47 | 77.9 | 6.2 | 33
KJ090 | 7.5 | 1875 | 75 | 72 | 95 | 94 | 0.354 | 16.44 | 33.3 | 6.2 | 33
KJ090 | 7.5 | 1875 | 80 | 72 | 95 | 94 | 0.453 | 21.04 | 42.6 | 6.2 | 33
KJ090 | 7.5 | 1875 | 85 | 72 | 95 | 94 | 0.553 | 25.68 | 52 | 6.2 | 33
KJ090 | 7.5 | 1875 | 90 | 72 | 95 | 94 | 0.652 | 30.27 | 61.3 | 6.2 | 33
KJ090 | 7.5 | 1875 | 80 | 77 | 95 | 103.2 | 0.306 | 15.6 | 31.6 | 6.2 | 33
KJ090 | 7.5 | 1875 | 85 | 77 | 95 | 103.2 | 0.369 | 18.81 | 38.1 | 6.2 | 33
KJ090 | 7.5 | 1875 | 90 | 77 | 95 | 103.2 | 0.433 | 22.07 | 44.7 | 6.2 | 33
KJ090 | 7.5 | 1875 | 65 | 62 | 105 | 74.9 | 0.389 | 14.37 | 29.1 | 7.3 | 33
KJ090 | 7.5 | 1875 | 70 | 62 | 105 | 74.9 | 0.53 | 19.6 | 39.7 | 7.3 | 33
KJ090 | 7.5 | 1875 | 75 | 62 | 105 | 74.9 | 0.672 | 24.84 | 50.3 | 7.3 | 33
KJ090 | 7.5 | 1875 | 80 | 62 | 105 | 74.9 | 0.812 | 30.02 | 60.8 | 7.3 | 33
KJ090 | 7.5 | 1875 | 85 | 62 | 105 | 74.9 | 0.939 | 34.72 | 70.3 | 7.3 | 33
KJ090 | 7.5 | 1875 | 90 | 62 | 105 | 74.9 | 1 | 36.99 | 74.9 | 7.3 | 33
KJ090 | 7.5 | 1875 | 70 | 67 | 105 | 78.9 | 0.383 | 14.91 | 30.2 | 7.3 | 33
KJ090 | 7.5 | 1875 | 75 | 67 | 105 | 78.9 | 0.511 | 19.9 | 40.3 | 7.3 | 33
KJ090 | 7.5 | 1875 | 80 | 67 | 105 | 78.9 | 0.639 | 24.89 | 50.4 | 7.3 | 33
KJ090 | 7.5 | 1875 | 85 | 67 | 105 | 78.9 | 0.791 | 30.81 | 62.4 | 7.3 | 33
KJ090 | 7.5 | 1875 | 90 | 67 | 105 | 78.9 | 0.944 | 36.79 | 74.5 | 7.3 | 33
KJ090 | 7.5 | 1875 | 75 | 72 | 105 | 87.1 | 0.348 | 14.96 | 30.3 | 7.3 | 33
KJ090 | 7.5 | 1875 | 80 | 72 | 105 | 87.1 | 0.458 | 19.7 | 39.9 | 7.3 | 33
KJ090 | 7.5 | 1875 | 85 | 72 | 105 | 87.1 | 0.568 | 24.44 | 49.5 | 7.3 | 33
KJ090 | 7.5 | 1875 | 90 | 72 | 105 | 87.1 | 0.679 | 29.19 | 59.1 | 7.3 | 33
KJ090 | 7.5 | 1875 | 80 | 77 | 105 | 95.3 | 0.31 | 14.57 | 29.5 | 7.4 | 33
KJ090 | 7.5 | 1875 | 85 | 77 | 105 | 95.3 | 0.384 | 18.07 | 36.6 | 7.4 | 33
KJ090 | 7.5 | 1875 | 90 | 77 | 105 | 95.3 | 0.459 | 21.58 | 43.7 | 7.4 | 33
KJ090 | 7.5 | 1875 | 65 | 62 | 115 | 70.6 | 0.367 | 12.79 | 25.9 | 8.3 | 34
KJ090 | 7.5 | 1875 | 70 | 62 | 115 | 70.6 | 0.513 | 17.88 | 36.2 | 8.3 | 34
KJ090 | 7.5 | 1875 | 75 | 62 | 115 | 70.6 | 0.66 | 23.01 | 46.6 | 8.3 | 34
KJ090 | 7.5 | 1875 | 80 | 62 | 115 | 70.6 | 0.806 | 28.1 | 56.9 | 8.3 | 34
KJ090 | 7.5 | 1875 | 85 | 62 | 115 | 70.6 | 0.929 | 32.4 | 65.6 | 8.3 | 34
KJ090 | 7.5 | 1875 | 90 | 62 | 115 | 70.6 | 1 | 34.86 | 70.6 | 8.3 | 34
KJ090 | 7.5 | 1875 | 70 | 67 | 115 | 73 | 0.368 | 13.28 | 26.9 | 8.3 | 34
KJ090 | 7.5 | 1875 | 75 | 67 | 115 | 73 | 0.507 | 18.27 | 37 | 8.3 | 34
KJ090 | 7.5 | 1875 | 80 | 67 | 115 | 73 | 0.645 | 23.26 | 47.1 | 8.3 | 34
KJ090 | 7.5 | 1875 | 85 | 67 | 115 | 73 | 0.81 | 29.19 | 59.1 | 8.3 | 34
KJ090 | 7.5 | 1875 | 90 | 67 | 115 | 73 | 0.974 | 35.11 | 71.1 | 8.3 | 34
KJ090 | 7.5 | 1875 | 75 | 72 | 115 | 80.2 | 0.34 | 13.48 | 27.3 | 8.3 | 34
KJ090 | 7.5 | 1875 | 80 | 72 | 115 | 80.2 | 0.464 | 18.37 | 37.2 | 8.3 | 34
KJ090 | 7.5 | 1875 | 85 | 72 | 115 | 80.2 | 0.587 | 23.26 | 47.1 | 8.3 | 34
KJ090 | 7.5 | 1875 | 90 | 72 | 115 | 80.2 | 0.709 | 28.1 | 56.9 | 8.3 | 34
KJ090 | 7.5 | 1875 | 80 | 77 | 115 | 87.3 | 0.314 | 13.53 | 27.4 | 8.3 | 34
KJ090 | 7.5 | 1875 | 85 | 77 | 115 | 87.3 | 0.402 | 17.33 | 35.1 | 8.3 | 34
KJ090 | 7.5 | 1875 | 90 | 77 | 115 | 87.3 | 0.489 | 21.09 | 42.7 | 8.3 | 34
KJ090 | 7.5 | 1875 | 65 | 62 | 125 | 66.2 | 0.343 | 11.21 | 22.7 | 9.3 | 34
KJ090 | 7.5 | 1875 | 70 | 62 | 125 | 66.2 | 0.495 | 16.2 | 32.8 | 9.3 | 34
KJ090 | 7.5 | 1875 | 75 | 62 | 125 | 66.2 | 0.648 | 21.19 | 42.9 | 9.3 | 34
KJ090 | 7.5 | 1875 | 80 | 62 | 125 | 66.2 | 0.801 | 26.17 | 53 | 9.3 | 34
KJ090 | 7.5 | 1875 | 85 | 62 | 125 | 66.2 | 0.921 | 30.12 | 61 | 9.3 | 34
KJ090 | 7.5 | 1875 | 90 | 62 | 125 | 66.2 | 1 | 32.69 | 66.2 | 9.3 | 34
KJ090 | 7.5 | 1875 | 70 | 67 | 125 | 67 | 0.351 | 11.6 | 23.5 | 9.3 | 34
KJ090 | 7.5 | 1875 | 75 | 67 | 125 | 67 | 0.501 | 16.59 | 33.6 | 9.3 | 34
KJ090 | 7.5 | 1875 | 80 | 67 | 125 | 67 | 0.652 | 21.58 | 43.7 | 9.3 | 34
KJ090 | 7.5 | 1875 | 85 | 67 | 125 | 67 | 0.831 | 27.51 | 55.7 | 9.3 | 34
KJ090 | 7.5 | 1875 | 90 | 67 | 125 | 67 | 1 | 33.09 | 67 | 9.3 | 34
KJ090 | 7.5 | 1875 | 75 | 72 | 125 | 73.2 | 0.333 | 12.05 | 24.4 | 9.3 | 34
KJ090 | 7.5 | 1875 | 80 | 72 | 125 | 73.2 | 0.471 | 17.04 | 34.5 | 9.3 | 34
KJ090 | 7.5 | 1875 | 85 | 72 | 125 | 73.2 | 0.609 | 22.02 | 44.6 | 9.3 | 34
KJ090 | 7.5 | 1875 | 90 | 72 | 125 | 73.2 | 0.749 | 27.06 | 54.8 | 9.3 | 34
KJ090 | 7.5 | 1875 | 80 | 77 | 125 | 79.4 | 0.319 | 12.49 | 25.3 | 9.4 | 34
KJ090 | 7.5 | 1875 | 85 | 77 | 125 | 79.4 | 0.422 | 16.54 | 33.5 | 9.4 | 34
KJ090 | 7.5 | 1875 | 90 | 77 | 125 | 79.4 | 0.526 | 20.64 | 41.8 | 9.4 | 34
KJ090 | 7.5 | 2250 | 65 | 57 | 75 | 86.5 | 0.594 | 21.15 | 51.4 | 4.6 | 33
KJ090 | 7.5 | 2250 | 70 | 57 | 75 | 86.5 | 0.714 | 25.43 | 61.8 | 4.6 | 33
KJ090 | 7.5 | 2250 | 75 | 57 | 75 | 86.5 | 0.834 | 29.67 | 72.1 | 4.6 | 33
KJ090 | 7.5 | 2250 | 80 | 57 | 75 | 86.5 | 0.953 | 33.91 | 82.4 | 4.6 | 33
KJ090 | 7.5 | 2250 | 85 | 57 | 75 | 86.5 | 1 | 35.6 | 86.5 | 4.6 | 33
KJ090 | 7.5 | 2250 | 90 | 57 | 75 | 86.5 | 1 | 35.6 | 86.5 | 4.6 | 33
KJ090 | 7.5 | 2250 | 65 | 62 | 75 | 93.5 | 0.431 | 16.58 | 40.3 | 4.6 | 33
KJ090 | 7.5 | 2250 | 70 | 62 | 75 | 93.5 | 0.547 | 21.03 | 51.1 | 4.6 | 33
KJ090 | 7.5 | 2250 | 75 | 62 | 75 | 93.5 | 0.668 | 25.72 | 62.5 | 4.6 | 33
KJ090 | 7.5 | 2250 | 80 | 62 | 75 | 93.5 | 0.779 | 29.96 | 72.8 | 4.6 | 33
KJ090 | 7.5 | 2250 | 85 | 62 | 75 | 93.5 | 0.906 | 34.86 | 84.7 | 4.6 | 33
KJ090 | 7.5 | 2250 | 90 | 62 | 75 | 93.5 | 1 | 38.48 | 93.5 | 4.6 | 33
KJ090 | 7.5 | 2250 | 70 | 67 | 75 | 100.5 | 0.403 | 16.67 | 40.5 | 4.7 | 33
KJ090 | 7.5 | 2250 | 75 | 67 | 75 | 100.5 | 0.522 | 21.6 | 52.5 | 4.7 | 33
KJ090 | 7.5 | 2250 | 80 | 67 | 75 | 100.5 | 0.628 | 25.97 | 63.1 | 4.7 | 33
KJ090 | 7.5 | 2250 | 85 | 67 | 75 | 100.5 | 0.754 | 31.19 | 75.8 | 4.7 | 33
KJ090 | 7.5 | 2250 | 90 | 67 | 75 | 100.5 | 0.88 | 36.38 | 88.4 | 4.7 | 33
KJ090 | 7.5 | 2250 | 75 | 72 | 75 | 111.5 | 0.374 | 17.16 | 41.7 | 4.7 | 33
KJ090 | 7.5 | 2250 | 80 | 72 | 75 | 111.5 | 0.48 | 22.02 | 53.5 | 4.7 | 33
KJ090 | 7.5 | 2250 | 85 | 72 | 75 | 111.5 | 0.586 | 26.87 | 65.3 | 4.7 | 33
KJ090 | 7.5 | 2250 | 90 | 72 | 75 | 111.5 | 0.691 | 31.73 | 77.1 | 4.7 | 33
KJ090 | 7.5 | 2250 | 80 | 77 | 75 | 122.5 | 0.358 | 18.02 | 43.8 | 4.8 | 33
KJ090 | 7.5 | 2250 | 85 | 77 | 75 | 122.5 | 0.448 | 22.59 | 54.9 | 4.8 | 33
KJ090 | 7.5 | 2250 | 90 | 77 | 75 | 122.5 | 0.538 | 27.12 | 65.9 | 4.8 | 33
KJ090 | 7.5 | 2250 | 65 | 57 | 85 | 83.2 | 0.576 | 19.71 | 47.9 | 5.5 | 33
KJ090 | 7.5 | 2250 | 70 | 57 | 85 | 83.2 | 0.718 | 24.57 | 59.7 | 5.5 | 33
KJ090 | 7.5 | 2250 | 75 | 57 | 85 | 83.2 | 0.859 | 29.42 | 71.5 | 5.5 | 33
KJ090 | 7.5 | 2250 | 80 | 57 | 85 | 83.2 | 1 | 34.24 | 83.2 | 5.5 | 33
KJ090 | 7.5 | 2250 | 85 | 57 | 85 | 83.2 | 1 | 34.24 | 83.2 | 5.5 | 33
KJ090 | 7.5 | 2250 | 90 | 57 | 85 | 83.2 | 1 | 34.24 | 83.2 | 5.5 | 33
KJ090 | 7.5 | 2250 | 65 | 62 | 85 | 88.7 | 0.414 | 15.1 | 36.7 | 5.5 | 33
KJ090 | 7.5 | 2250 | 70 | 62 | 85 | 88.7 | 0.547 | 19.96 | 48.5 | 5.5 | 33
KJ090 | 7.5 | 2250 | 75 | 62 | 85 | 88.7 | 0.682 | 24.9 | 60.5 | 5.5 | 33
KJ090 | 7.5 | 2250 | 80 | 62 | 85 | 88.7 | 0.812 | 29.63 | 72 | 5.5 | 33
KJ090 | 7.5 | 2250 | 85 | 62 | 85 | 88.7 | 0.928 | 33.87 | 82.3 | 5.5 | 33
KJ090 | 7.5 | 2250 | 90 | 62 | 85 | 88.7 | 1 | 36.5 | 88.7 | 5.5 | 33
KJ090 | 7.5 | 2250 | 70 | 67 | 85 | 94.3 | 0.396 | 15.35 | 37.3 | 5.5 | 33
KJ090 | 7.5 | 2250 | 75 | 67 | 85 | 94.3 | 0.524 | 20.33 | 49.4 | 5.5 | 33
KJ090 | 7.5 | 2250 | 80 | 67 | 85 | 94.3 | 0.645 | 25.02 | 60.8 | 5.5 | 33
KJ090 | 7.5 | 2250 | 85 | 67 | 85 | 94.3 | 0.776 | 30.12 | 73.2 | 5.5 | 33
KJ090 | 7.5 | 2250 | 90 | 67 | 85 | 94.3 | 0.908 | 35.23 | 85.6 | 5.5 | 33
KJ090 | 7.5 | 2250 | 75 | 72 | 85 | 103.9 | 0.364 | 15.56 | 37.8 | 5.5 | 33
KJ090 | 7.5 | 2250 | 80 | 72 | 85 | 103.9 | 0.476 | 20.37 | 49.5 | 5.5 | 33
KJ090 | 7.5 | 2250 | 85 | 72 | 85 | 103.9 | 0.589 | 25.19 | 61.2 | 5.5 | 33
KJ090 | 7.5 | 2250 | 90 | 72 | 85 | 103.9 | 0.701 | 29.96 | 72.8 | 5.5 | 33
KJ090 | 7.5 | 2250 | 80 | 77 | 85 | 113.5 | 0.337 | 15.72 | 38.2 | 5.5 | 33
KJ090 | 7.5 | 2250 | 85 | 77 | 85 | 113.5 | 0.433 | 20.21 | 49.1 | 5.5 | 33
KJ090 | 7.5 | 2250 | 90 | 77 | 85 | 113.5 | 0.529 | 24.69 | 60 | 5.5 | 33
KJ090 | 7.5 | 2250 | 65 | 57 | 95 | 79.8 | 0.555 | 18.23 | 44.3 | 6.3 | 33
KJ090 | 7.5 | 2250 | 70 | 57 | 95 | 79.8 | 0.722 | 23.7 | 57.6 | 6.3 | 33
KJ090 | 7.5 | 2250 | 75 | 57 | 95 | 79.8 | 0.888 | 29.18 | 70.9 | 6.3 | 33
KJ090 | 7.5 | 2250 | 80 | 57 | 95 | 79.8 | 1 | 32.84 | 79.8 | 6.3 | 33
KJ090 | 7.5 | 2250 | 85 | 57 | 95 | 79.8 | 1 | 32.84 | 79.8 | 6.3 | 33
KJ090 | 7.5 | 2250 | 90 | 57 | 95 | 79.8 | 1 | 32.84 | 79.8 | 6.3 | 33
KJ090 | 7.5 | 2250 | 65 | 62 | 95 | 84 | 0.395 | 13.66 | 33.2 | 6.3 | 33
KJ090 | 7.5 | 2250 | 70 | 62 | 95 | 84 | 0.546 | 18.89 | 45.9 | 6.3 | 33
KJ090 | 7.5 | 2250 | 75 | 62 | 95 | 84 | 0.698 | 24.12 | 58.6 | 6.3 | 33
KJ090 | 7.5 | 2250 | 80 | 62 | 95 | 84 | 0.849 | 29.34 | 71.3 | 6.3 | 33
KJ090 | 7.5 | 2250 | 85 | 62 | 95 | 84 | 0.951 | 32.88 | 79.9 | 6.3 | 33
KJ090 | 7.5 | 2250 | 90 | 62 | 95 | 84 | 1 | 34.57 | 84 | 6.3 | 33
KJ090 | 7.5 | 2250 | 70 | 67 | 95 | 88.1 | 0.388 | 14.07 | 34.2 | 6.3 | 33
KJ090 | 7.5 | 2250 | 75 | 67 | 95 | 88.1 | 0.526 | 19.05 | 46.3 | 6.3 | 33
KJ090 | 7.5 | 2250 | 80 | 67 | 95 | 88.1 | 0.663 | 24.03 | 58.4 | 6.3 | 33
KJ090 | 7.5 | 2250 | 85 | 67 | 95 | 88.1 | 0.801 | 29.05 | 70.6 | 6.3 | 33
KJ090 | 7.5 | 2250 | 90 | 67 | 95 | 88.1 | 0.94 | 34.07 | 82.8 | 6.3 | 33
KJ090 | 7.5 | 2250 | 75 | 72 | 95 | 96.3 | 0.353 | 13.99 | 34 | 6.3 | 33
KJ090 | 7.5 | 2250 | 80 | 72 | 95 | 96.3 | 0.472 | 18.72 | 45.5 | 6.3 | 33
KJ090 | 7.5 | 2250 | 85 | 72 | 95 | 96.3 | 0.592 | 23.46 | 57 | 6.3 | 33
KJ090 | 7.5 | 2250 | 90 | 72 | 95 | 96.3 | 0.711 | 28.19 | 68.5 | 6.3 | 33
KJ090 | 7.5 | 2250 | 80 | 77 | 95 | 104.5 | 0.312 | 13.42 | 32.6 | 6.3 | 33
KJ090 | 7.5 | 2250 | 85 | 77 | 95 | 104.5 | 0.415 | 17.86 | 43.4 | 6.3 | 33
KJ090 | 7.5 | 2250 | 90 | 77 | 95 | 104.5 | 0.519 | 22.3 | 54.2 | 6.3 | 33
KJ090 | 7.5 | 2250 | 65 | 57 | 105 | 75.9 | 0.534 | 16.67 | 40.5 | 7.3 | 33
KJ090 | 7.5 | 2250 | 70 | 57 | 105 | 75.9 | 0.706 | 22.06 | 53.6 | 7.3 | 33
KJ090 | 7.5 | 2250 | 75 | 57 | 105 | 75.9 | 0.877 | 27.41 | 66.6 | 7.3 | 33
KJ090 | 7.5 | 2250 | 80 | 57 | 105 | 75.9 | 1 | 31.23 | 75.9 | 7.3 | 33
KJ090 | 7.5 | 2250 | 85 | 57 | 105 | 75.9 | 1 | 31.23 | 75.9 | 7.3 | 33
KJ090 | 7.5 | 2250 | 90 | 57 | 105 | 75.9 | 1 | 31.23 | 75.9 | 7.3 | 33
KJ090 | 7.5 | 2250 | 65 | 62 | 105 | 79 | 0.375 | 12.18 | 29.6 | 7.3 | 33
KJ090 | 7.5 | 2250 | 70 | 62 | 105 | 79 | 0.533 | 17.33 | 42.1 | 7.3 | 33
KJ090 | 7.5 | 2250 | 75 | 62 | 105 | 79 | 0.692 | 22.51 | 54.7 | 7.3 | 33
KJ090 | 7.5 | 2250 | 80 | 62 | 105 | 79 | 0.851 | 27.65 | 67.2 | 7.3 | 33
KJ090 | 7.5 | 2250 | 85 | 62 | 105 | 79 | 0.949 | 30.86 | 75 | 7.3 | 33
KJ090 | 7.5 | 2250 | 90 | 62 | 105 | 79 | 1 | 32.51 | 79 | 7.3 | 33
KJ090 | 7.5 | 2250 | 70 | 67 | 105 | 82 | 0.374 | 12.63 | 30.7 | 7.3 | 33
KJ090 | 7.5 | 2250 | 75 | 67 | 105 | 82 | 0.522 | 17.61 | 42.8 | 7.3 | 33
KJ090 | 7.5 | 2250 | 80 | 67 | 105 | 82 | 0.668 | 22.55 | 54.8 | 7.3 | 33
KJ090 | 7.5 | 2250 | 85 | 67 | 105 | 82 | 0.813 | 27.45 | 66.7 | 7.3 | 33
KJ090 | 7.5 | 2250 | 90 | 67 | 105 | 82 | 0.96 | 32.39 | 78.7 | 7.3 | 33
KJ090 | 7.5 | 2250 | 75 | 72 | 105 | 89.2 | 0.345 | 12.67 | 30.8 | 7.3 | 33
KJ090 | 7.5 | 2250 | 80 | 72 | 105 | 89.2 | 0.475 | 17.45 | 42.4 | 7.3 | 33
KJ090 | 7.5 | 2250 | 85 | 72 | 105 | 89.2 | 0.605 | 22.22 | 54 | 7.3 | 33
KJ090 | 7.5 | 2250 | 90 | 72 | 105 | 89.2 | 0.735 | 27 | 65.6 | 7.3 | 33
KJ090 | 7.5 | 2250 | 80 | 77 | 105 | 96.4 | 0.311 | 12.35 | 30 | 7.4 | 33
KJ090 | 7.5 | 2250 | 85 | 77 | 105 | 96.4 | 0.428 | 17 | 41.3 | 7.4 | 33
KJ090 | 7.5 | 2250 | 90 | 77 | 105 | 96.4 | 0.546 | 21.65 | 52.6 | 7.4 | 33
KJ090 | 7.5 | 2250 | 65 | 57 | 115 | 72.1 | 0.509 | 15.1 | 36.7 | 8.3 | 34
KJ090 | 7.5 | 2250 | 70 | 57 | 115 | 72.1 | 0.687 | 20.37 | 49.5 | 8.3 | 34
KJ090 | 7.5 | 2250 | 75 | 57 | 115 | 72.1 | 0.864 | 25.64 | 62.3 | 8.3 | 34
KJ090 | 7.5 | 2250 | 80 | 57 | 115 | 72.1 | 1 | 29.67 | 72.1 | 8.3 | 34
KJ090 | 7.5 | 2250 | 85 | 57 | 115 | 72.1 | 1 | 29.67 | 72.1 | 8.3 | 34
KJ090 | 7.5 | 2250 | 90 | 57 | 115 | 72.1 | 1 | 29.67 | 72.1 | 8.3 | 34
KJ090 | 7.5 | 2250 | 65 | 62 | 115 | 74 | 0.35 | 10.66 | 25.9 | 8.3 | 34
KJ090 | 7.5 | 2250 | 70 | 62 | 115 | 74 | 0.518 | 15.76 | 38.3 | 8.3 | 34
KJ090 | 7.5 | 2250 | 75 | 62 | 115 | 74 | 0.685 | 20.86 | 50.7 | 8.3 | 34
KJ090 | 7.5 | 2250 | 80 | 62 | 115 | 74 | 0.853 | 25.97 | 63.1 | 8.3 | 34
KJ090 | 7.5 | 2250 | 85 | 62 | 115 | 74 | 0.947 | 28.85 | 70.1 | 8.3 | 34
KJ090 | 7.5 | 2250 | 90 | 62 | 115 | 74 | 1 | 30.45 | 74 | 8.3 | 34
KJ090 | 7.5 | 2250 | 70 | 67 | 115 | 76 | 0.358 | 11.19 | 27.2 | 8.3 | 34
KJ090 | 7.5 | 2250 | 75 | 67 | 115 | 76 | 0.516 | 16.13 | 39.2 | 8.3 | 34
KJ090 | 7.5 | 2250 | 80 | 67 | 115 | 76 | 0.675 | 21.11 | 51.3 | 8.3 | 34
KJ090 | 7.5 | 2250 | 85 | 67 | 115 | 76 | 0.828 | 25.88 | 62.9 | 8.3 | 34
KJ090 | 7.5 | 2250 | 90 | 67 | 115 | 76 | 0.98 | 30.66 | 74.5 | 8.3 | 34
KJ090 | 7.5 | 2250 | 75 | 72 | 115 | 82.2 | 0.337 | 11.4 | 27.7 | 8.4 | 34
KJ090 | 7.5 | 2250 | 80 | 72 | 115 | 82.2 | 0.479 | 16.21 | 39.4 | 8.4 | 34
KJ090 | 7.5 | 2250 | 85 | 72 | 115 | 82.2 | 0.622 | 21.03 | 51.1 | 8.4 | 34
KJ090 | 7.5 | 2250 | 90 | 72 | 115 | 82.2 | 0.764 | 25.84 | 62.8 | 8.4 | 34
KJ090 | 7.5 | 2250 | 80 | 77 | 115 | 88.3 | 0.311 | 11.32 | 27.5 | 8.4 | 34
KJ090 | 7.5 | 2250 | 85 | 77 | 115 | 88.3 | 0.445 | 16.17 | 39.3 | 8.4 | 34
KJ090 | 7.5 | 2250 | 90 | 77 | 115 | 88.3 | 0.578 | 20.99 | 51 | 8.4 | 34
KJ090 | 7.5 | 2250 | 65 | 57 | 125 | 68.2 | 0.484 | 13.58 | 33 | 9.4 | 34
KJ090 | 7.5 | 2250 | 70 | 57 | 125 | 68.2 | 0.667 | 18.72 | 45.5 | 9.4 | 34
KJ090 | 7.5 | 2250 | 75 | 57 | 125 | 68.2 | 0.849 | 23.83 | 57.9 | 9.4 | 34
KJ090 | 7.5 | 2250 | 80 | 57 | 125 | 68.2 | 1 | 28.07 | 68.2 | 9.4 | 34
KJ090 | 7.5 | 2250 | 85 | 57 | 125 | 68.2 | 1 | 28.07 | 68.2 | 9.4 | 34
KJ090 | 7.5 | 2250 | 90 | 57 | 125 | 68.2 | 1 | 28.07 | 68.2 | 9.4 | 34
KJ090 | 7.5 | 2250 | 65 | 62 | 125 | 69.1 | 0.323 | 9.18 | 22.3 | 9.4 | 34
KJ090 | 7.5 | 2250 | 70 | 62 | 125 | 69.1 | 0.501 | 14.24 | 34.6 | 9.4 | 34
KJ090 | 7.5 | 2250 | 75 | 62 | 125 | 69.1 | 0.677 | 19.26 | 46.8 | 9.4 | 34
KJ090 | 7.5 | 2250 | 80 | 62 | 125 | 69.1 | 0.855 | 24.32 | 59.1 | 9.4 | 34
KJ090 | 7.5 | 2250 | 85 | 62 | 125 | 69.1 | 0.944 | 26.83 | 65.2 | 9.4 | 34
KJ090 | 7.5 | 2250 | 90 | 62 | 125 | 69.1 | 1 | 28.44 | 69.1 | 9.4 | 34
KJ090 | 7.5 | 2250 | 70 | 67 | 125 | 69.9 | 0.339 | 9.75 | 23.7 | 9.4 | 34
KJ090 | 7.5 | 2250 | 75 | 67 | 125 | 69.9 | 0.511 | 14.69 | 35.7 | 9.4 | 34
KJ090 | 7.5 | 2250 | 80 | 67 | 125 | 69.9 | 0.682 | 19.63 | 47.7 | 9.4 | 34
KJ090 | 7.5 | 2250 | 85 | 67 | 125 | 69.9 | 0.844 | 24.28 | 59 | 9.4 | 34
KJ090 | 7.5 | 2250 | 90 | 67 | 125 | 69.9 | 1 | 28.77 | 69.9 | 9.4 | 34
KJ090 | 7.5 | 2250 | 75 | 72 | 125 | 75.1 | 0.328 | 10.12 | 24.6 | 9.4 | 34
KJ090 | 7.5 | 2250 | 80 | 72 | 125 | 75.1 | 0.483 | 14.94 | 36.3 | 9.4 | 34
KJ090 | 7.5 | 2250 | 85 | 72 | 125 | 75.1 | 0.64 | 19.79 | 48.1 | 9.4 | 34
KJ090 | 7.5 | 2250 | 90 | 72 | 125 | 75.1 | 0.798 | 24.65 | 59.9 | 9.4 | 34
KJ090 | 7.5 | 2250 | 80 | 77 | 125 | 80.2 | 0.312 | 10.29 | 25 | 9.5 | 34
KJ090 | 7.5 | 2250 | 85 | 77 | 125 | 80.2 | 0.464 | 15.31 | 37.2 | 9.5 | 34
KJ090 | 7.5 | 2250 | 90 | 77 | 125 | 80.2 | 0.617 | 20.37 | 49.5 | 9.5 | 34
KJ090 | 7.5 | 2625 | 65 | 57 | 75 | 93.4 | 0.588 | 19.37 | 54.9 | 4.6 | 33
KJ090 | 7.5 | 2625 | 70 | 57 | 75 | 93.4 | 0.726 | 23.92 | 67.8 | 4.6 | 33
KJ090 | 7.5 | 2625 | 75 | 57 | 75 | 93.4 | 0.864 | 28.47 | 80.7 | 4.6 | 33
KJ090 | 7.5 | 2625 | 80 | 57 | 75 | 93.4 | 0.979 | 32.24 | 91.4 | 4.6 | 33
KJ090 | 7.5 | 2625 | 85 | 57 | 75 | 93.4 | 1 | 32.95 | 93.4 | 4.6 | 33
KJ090 | 7.5 | 2625 | 90 | 57 | 75 | 93.4 | 1 | 32.95 | 93.4 | 4.6 | 33
KJ090 | 7.5 | 2625 | 65 | 62 | 75 | 98.7 | 0.418 | 14.57 | 41.3 | 4.6 | 33
KJ090 | 7.5 | 2625 | 70 | 62 | 75 | 98.7 | 0.552 | 19.22 | 54.5 | 4.6 | 33
KJ090 | 7.5 | 2625 | 75 | 62 | 75 | 98.7 | 0.69 | 24.02 | 68.1 | 4.6 | 33
KJ090 | 7.5 | 2625 | 80 | 62 | 75 | 98.7 | 0.82 | 28.54 | 80.9 | 4.6 | 33
KJ090 | 7.5 | 2625 | 85 | 62 | 75 | 98.7 | 0.922 | 32.1 | 91 | 4.6 | 33
KJ090 | 7.5 | 2625 | 90 | 62 | 75 | 98.7 | 1 | 34.81 | 98.7 | 4.6 | 33
KJ090 | 7.5 | 2625 | 70 | 67 | 75 | 103.9 | 0.397 | 14.53 | 41.2 | 4.7 | 33
KJ090 | 7.5 | 2625 | 75 | 67 | 75 | 103.9 | 0.531 | 19.47 | 55.2 | 4.7 | 33
KJ090 | 7.5 | 2625 | 80 | 67 | 75 | 103.9 | 0.657 | 24.09 | 68.3 | 4.7 | 33
KJ090 | 7.5 | 2625 | 85 | 67 | 75 | 103.9 | 0.787 | 28.85 | 81.8 | 4.7 | 33
KJ090 | 7.5 | 2625 | 90 | 67 | 75 | 103.9 | 0.917 | 33.62 | 95.3 | 4.7 | 33
KJ090 | 7.5 | 2625 | 75 | 72 | 75 | 114.2 | 0.366 | 14.74 | 41.8 | 4.7 | 33
KJ090 | 7.5 | 2625 | 80 | 72 | 75 | 114.2 | 0.488 | 19.65 | 55.7 | 4.7 | 33
KJ090 | 7.5 | 2625 | 85 | 72 | 75 | 114.2 | 0.609 | 24.55 | 69.6 | 4.7 | 33
KJ090 | 7.5 | 2625 | 90 | 72 | 75 | 114.2 | 0.731 | 29.45 | 83.5 | 4.7 | 33
KJ090 | 7.5 | 2625 | 80 | 77 | 75 | 124.4 | 0.346 | 15.2 | 43.1 | 4.7 | 33
KJ090 | 7.5 | 2625 | 85 | 77 | 75 | 124.4 | 0.462 | 20.28 | 57.5 | 4.7 | 33
KJ090 | 7.5 | 2625 | 90 | 77 | 75 | 124.4 | 0.577 | 25.33 | 71.8 | 4.7 | 33
KJ090 | 7.5 | 2625 | 65 | 57 | 85 | 89.7 | 0.571 | 18.06 | 51.2 | 5.5 | 33
KJ090 | 7.5 | 2625 | 70 | 57 | 85 | 89.7 | 0.727 | 23 | 65.2 | 5.5 | 33
KJ090 | 7.5 | 2625 | 75 | 57 | 85 | 89.7 | 0.882 | 27.9 | 79.1 | 5.5 | 33
KJ090 | 7.5 | 2625 | 80 | 57 | 85 | 89.7 | 1 | 31.64 | 89.7 | 5.5 | 33
KJ090 | 7.5 | 2625 | 85 | 57 | 85 | 89.7 | 1 | 31.64 | 89.7 | 5.5 | 33
KJ090 | 7.5 | 2625 | 90 | 57 | 85 | 89.7 | 1 | 31.64 | 89.7 | 5.5 | 33
KJ090 | 7.5 | 2625 | 65 | 62 | 85 | 93.7 | 0.402 | 13.3 | 37.7 | 5.5 | 33
KJ090 | 7.5 | 2625 | 70 | 62 | 85 | 93.7 | 0.551 | 18.2 | 51.6 | 5.5 | 33
KJ090 | 7.5 | 2625 | 75 | 62 | 85 | 93.7 | 0.701 | 23.17 | 65.7 | 5.5 | 33
KJ090 | 7.5 | 2625 | 80 | 62 | 85 | 93.7 | 0.847 | 28.01 | 79.4 | 5.5 | 33
KJ090 | 7.5 | 2625 | 85 | 62 | 85 | 93.7 | 0.939 | 31.04 | 88 | 5.5 | 33
KJ090 | 7.5 | 2625 | 90 | 62 | 85 | 93.7 | 1 | 33.05 | 93.7 | 5.5 | 33
KJ090 | 7.5 | 2625 | 70 | 67 | 85 | 97.6 | 0.389 | 13.4 | 38 | 5.5 | 33
KJ090 | 7.5 | 2625 | 75 | 67 | 85 | 97.6 | 0.534 | 18.38 | 52.1 | 5.5 | 33
KJ090 | 7.5 | 2625 | 80 | 67 | 85 | 97.6 | 0.673 | 23.17 | 65.7 | 5.5 | 33
KJ090 | 7.5 | 2625 | 85 | 67 | 85 | 97.6 | 0.805 | 27.72 | 78.6 | 5.5 | 33
KJ090 | 7.5 | 2625 | 90 | 67 | 85 | 97.6 | 0.938 | 32.28 | 91.5 | 5.5 | 33
KJ090 | 7.5 | 2625 | 75 | 72 | 85 | 106.4 | 0.359 | 13.47 | 38.2 | 5.5 | 33
KJ090 | 7.5 | 2625 | 80 | 72 | 85 | 106.4 | 0.489 | 18.34 | 52 | 5.5 | 33
KJ090 | 7.5 | 2625 | 85 | 72 | 85 | 106.4 | 0.618 | 23.21 | 65.8 | 5.5 | 33
KJ090 | 7.5 | 2625 | 90 | 72 | 85 | 106.4 | 0.748 | 28.08 | 79.6 | 5.5 | 33
KJ090 | 7.5 | 2625 | 80 | 77 | 85 | 115.2 | 0.332 | 13.51 | 38.3 | 5.5 | 33
KJ090 | 7.5 | 2625 | 85 | 77 | 85 | 115.2 | 0.46 | 18.69 | 53 | 5.5 | 33
KJ090 | 7.5 | 2625 | 90 | 77 | 85 | 115.2 | 0.588 | 23.88 | 67.7 | 5.5 | 33
KJ090 | 7.5 | 2625 | 65 | 57 | 95 | 85.9 | 0.553 | 16.75 | 47.5 | 6.3 | 33
KJ090 | 7.5 | 2625 | 70 | 57 | 95 | 85.9 | 0.728 | 22.05 | 62.5 | 6.3 | 33
KJ090 | 7.5 | 2625 | 75 | 57 | 95 | 85.9 | 0.902 | 27.34 | 77.5 | 6.3 | 33
KJ090 | 7.5 | 2625 | 80 | 57 | 95 | 85.9 | 1 | 30.3 | 85.9 | 6.3 | 33
KJ090 | 7.5 | 2625 | 85 | 57 | 95 | 85.9 | 1 | 30.3 | 85.9 | 6.3 | 33
KJ090 | 7.5 | 2625 | 90 | 57 | 95 | 85.9 | 1 | 30.3 | 85.9 | 6.3 | 33
KJ090 | 7.5 | 2625 | 65 | 62 | 95 | 88.6 | 0.385 | 12.03 | 34.1 | 6.3 | 33
KJ090 | 7.5 | 2625 | 70 | 62 | 95 | 88.6 | 0.55 | 17.18 | 48.7 | 6.3 | 33
KJ090 | 7.5 | 2625 | 75 | 62 | 95 | 88.6 | 0.713 | 22.29 | 63.2 | 6.3 | 33
KJ090 | 7.5 | 2625 | 80 | 62 | 95 | 88.6 | 0.878 | 27.44 | 77.8 | 6.3 | 33
KJ090 | 7.5 | 2625 | 85 | 62 | 95 | 88.6 | 0.958 | 29.95 | 84.9 | 6.3 | 33
KJ090 | 7.5 | 2625 | 90 | 62 | 95 | 88.6 | 1 | 31.25 | 88.6 | 6.3 | 33
KJ090 | 7.5 | 2625 | 70 | 67 | 95 | 91.3 | 0.381 | 12.28 | 34.8 | 6.3 | 33
KJ090 | 7.5 | 2625 | 75 | 67 | 95 | 91.3 | 0.536 | 17.25 | 48.9 | 6.3 | 33
KJ090 | 7.5 | 2625 | 80 | 67 | 95 | 91.3 | 0.691 | 22.26 | 63.1 | 6.3 | 33
KJ090 | 7.5 | 2625 | 85 | 67 | 95 | 91.3 | 0.826 | 26.6 | 75.4 | 6.3 | 33
KJ090 | 7.5 | 2625 | 90 | 67 | 95 | 91.3 | 0.962 | 30.97 | 87.8 | 6.3 | 33
KJ090 | 7.5 | 2625 | 75 | 72 | 95 | 98.6 | 0.351 | 12.2 | 34.6 | 6.3 | 33
KJ090 | 7.5 | 2625 | 80 | 72 | 95 | 98.6 | 0.49 | 17.04 | 48.3 | 6.3 | 33
KJ090 | 7.5 | 2625 | 85 | 72 | 95 | 98.6 | 0.629 | 21.87 | 62 | 6.3 | 33
KJ090 | 7.5 | 2625 | 90 | 72 | 95 | 98.6 | 0.768 | 26.7 | 75.7 | 6.3 | 33
KJ090 | 7.5 | 2625 | 80 | 77 | 95 | 105.9 | 0.317 | 11.85 | 33.6 | 6.3 | 33
KJ090 | 7.5 | 2625 | 85 | 77 | 95 | 105.9 | 0.459 | 17.14 | 48.6 | 6.3 | 33
KJ090 | 7.5 | 2625 | 90 | 77 | 95 | 105.9 | 0.601 | 22.43 | 63.6 | 6.3 | 33
KJ090 | 7.5 | 2625 | 65 | 57 | 105 | 81 | 0.531 | 15.17 | 43 | 7.3 | 33
KJ090 | 7.5 | 2625 | 70 | 57 | 105 | 81 | 0.716 | 20.46 | 58 | 7.3 | 33
KJ090 | 7.5 | 2625 | 75 | 57 | 105 | 81 | 0.901 | 25.75 | 73 | 7.3 | 33
KJ090 | 7.5 | 2625 | 80 | 57 | 105 | 81 | 1 | 28.57 | 81 | 7.3 | 33
KJ090 | 7.5 | 2625 | 85 | 57 | 105 | 81 | 1 | 28.57 | 81 | 7.3 | 33
KJ090 | 7.5 | 2625 | 90 | 57 | 105 | 81 | 1 | 28.57 | 81 | 7.3 | 33
KJ090 | 7.5 | 2625 | 65 | 62 | 105 | 83.1 | 0.361 | 10.58 | 30 | 7.3 | 33
KJ090 | 7.5 | 2625 | 70 | 62 | 105 | 83.1 | 0.537 | 15.73 | 44.6 | 7.3 | 33
KJ090 | 7.5 | 2625 | 75 | 62 | 105 | 83.1 | 0.711 | 20.85 | 59.1 | 7.3 | 33
KJ090 | 7.5 | 2625 | 80 | 62 | 105 | 83.1 | 0.886 | 25.96 | 73.6 | 7.3 | 33
KJ090 | 7.5 | 2625 | 85 | 62 | 105 | 83.1 | 0.959 | 28.11 | 79.7 | 7.3 | 33
KJ090 | 7.5 | 2625 | 90 | 62 | 105 | 83.1 | 1 | 29.31 | 83.1 | 7.3 | 33
KJ090 | 7.5 | 2625 | 70 | 67 | 105 | 85.1 | 0.365 | 10.97 | 31.1 | 7.3 | 33
KJ090 | 7.5 | 2625 | 75 | 67 | 105 | 85.1 | 0.531 | 15.94 | 45.2 | 7.3 | 33
KJ090 | 7.5 | 2625 | 80 | 67 | 105 | 85.1 | 0.697 | 20.92 | 59.3 | 7.3 | 33
KJ090 | 7.5 | 2625 | 85 | 67 | 105 | 85.1 | 0.834 | 25.04 | 71 | 7.3 | 33
KJ090 | 7.5 | 2625 | 90 | 67 | 105 | 85.1 | 0.973 | 29.21 | 82.8 | 7.3 | 33
KJ090 | 7.5 | 2625 | 75 | 72 | 105 | 91.4 | 0.342 | 11.04 | 31.3 | 7.3 | 33
KJ090 | 7.5 | 2625 | 80 | 72 | 105 | 91.4 | 0.491 | 15.84 | 44.9 | 7.3 | 33
KJ090 | 7.5 | 2625 | 85 | 72 | 105 | 91.4 | 0.64 | 20.63 | 58.5 | 7.3 | 33
KJ090 | 7.5 | 2625 | 90 | 72 | 105 | 91.4 | 0.79 | 25.47 | 72.2 | 7.3 | 33
KJ090 | 7.5 | 2625 | 80 | 77 | 105 | 97.6 | 0.314 | 10.79 | 30.6 | 7.3 | 33
KJ090 | 7.5 | 2625 | 85 | 77 | 105 | 97.6 | 0.472 | 16.26 | 46.1 | 7.3 | 33
KJ090 | 7.5 | 2625 | 90 | 77 | 105 | 97.6 | 0.63 | 21.69 | 61.5 | 7.3 | 33
KJ090 | 7.5 | 2625 | 65 | 57 | 115 | 76 | 0.507 | 13.58 | 38.5 | 8.4 | 34
KJ090 | 7.5 | 2625 | 70 | 57 | 115 | 76 | 0.703 | 18.84 | 53.4 | 8.4 | 34
KJ090 | 7.5 | 2625 | 75 | 57 | 115 | 76 | 0.9 | 24.13 | 68.4 | 8.4 | 34
KJ090 | 7.5 | 2625 | 80 | 57 | 115 | 76 | 1 | 26.81 | 76 | 8.4 | 34
KJ090 | 7.5 | 2625 | 85 | 57 | 115 | 76 | 1 | 26.81 | 76 | 8.4 | 34
KJ090 | 7.5 | 2625 | 90 | 57 | 115 | 76 | 1 | 26.81 | 76 | 8.4 | 34
KJ090 | 7.5 | 2625 | 65 | 62 | 115 | 77.5 | 0.335 | 9.17 | 26 | 8.4 | 34
KJ090 | 7.5 | 2625 | 70 | 62 | 115 | 77.5 | 0.521 | 14.25 | 40.4 | 8.4 | 34
KJ090 | 7.5 | 2625 | 75 | 62 | 115 | 77.5 | 0.708 | 19.37 | 54.9 | 8.4 | 34
KJ090 | 7.5 | 2625 | 80 | 62 | 115 | 77.5 | 0.895 | 24.48 | 69.4 | 8.4 | 34
KJ090 | 7.5 | 2625 | 85 | 62 | 115 | 77.5 | 0.961 | 26.28 | 74.5 | 8.4 | 34
KJ090 | 7.5 | 2625 | 90 | 62 | 115 | 77.5 | 1 | 27.34 | 77.5 | 8.4 | 34
KJ090 | 7.5 | 2625 | 70 | 67 | 115 | 79 | 0.348 | 9.7 | 27.5 | 8.4 | 34
KJ090 | 7.5 | 2625 | 75 | 67 | 115 | 79 | 0.525 | 14.64 | 41.5 | 8.4 | 34
KJ090 | 7.5 | 2625 | 80 | 67 | 115 | 79 | 0.703 | 19.58 | 55.5 | 8.4 | 34
KJ090 | 7.5 | 2625 | 85 | 67 | 115 | 79 | 0.844 | 23.53 | 66.7 | 8.4 | 34
KJ090 | 7.5 | 2625 | 90 | 67 | 115 | 79 | 0.986 | 27.48 | 77.9 | 8.4 | 34
KJ090 | 7.5 | 2625 | 75 | 72 | 115 | 84.2 | 0.333 | 9.88 | 28 | 8.4 | 34
KJ090 | 7.5 | 2625 | 80 | 72 | 115 | 84.2 | 0.494 | 14.67 | 41.6 | 8.4 | 34
KJ090 | 7.5 | 2625 | 85 | 72 | 115 | 84.2 | 0.654 | 19.44 | 55.1 | 8.4 | 34
KJ090 | 7.5 | 2625 | 90 | 72 | 115 | 84.2 | 0.815 | 24.2 | 68.6 | 8.4 | 34
KJ090 | 7.5 | 2625 | 80 | 77 | 115 | 89.4 | 0.309 | 9.74 | 27.6 | 8.5 | 34
KJ090 | 7.5 | 2625 | 85 | 77 | 115 | 89.4 | 0.487 | 15.34 | 43.5 | 8.5 | 34
KJ090 | 7.5 | 2625 | 90 | 77 | 115 | 89.4 | 0.663 | 20.92 | 59.3 | 8.5 | 34
KJ090 | 7.5 | 2625 | 65 | 57 | 125 | 71.1 | 0.477 | 11.96 | 33.9 | 9.4 | 34
KJ090 | 7.5 | 2625 | 70 | 57 | 125 | 71.1 | 0.686 | 17.21 | 48.8 | 9.4 | 34
KJ090 | 7.5 | 2625 | 75 | 57 | 125 | 71.1 | 0.897 | 22.5 | 63.8 | 9.4 | 34
KJ090 | 7.5 | 2625 | 80 | 57 | 125 | 71.1 | 1 | 25.08 | 71.1 | 9.4 | 34
KJ090 | 7.5 | 2625 | 85 | 57 | 125 | 71.1 | 1 | 25.08 | 71.1 | 9.4 | 34
KJ090 | 7.5 | 2625 | 90 | 57 | 125 | 71.1 | 1 | 25.08 | 71.1 | 9.4 | 34
KJ090 | 7.5 | 2625 | 65 | 62 | 125 | 72 | 0.304 | 7.72 | 21.9 | 9.4 | 34
KJ090 | 7.5 | 2625 | 70 | 62 | 125 | 72 | 0.504 | 12.8 | 36.3 | 9.4 | 34
KJ090 | 7.5 | 2625 | 75 | 62 | 125 | 72 | 0.706 | 17.92 | 50.8 | 9.4 | 34
KJ090 | 7.5 | 2625 | 80 | 62 | 125 | 72 | 0.906 | 23 | 65.2 | 9.4 | 34
KJ090 | 7.5 | 2625 | 85 | 62 | 125 | 72 | 0.962 | 24.44 | 69.3 | 9.4 | 34
KJ090 | 7.5 | 2625 | 90 | 62 | 125 | 72 | 1 | 25.4 | 72 | 9.4 | 34
KJ090 | 7.5 | 2625 | 70 | 67 | 125 | 72.8 | 0.327 | 8.4 | 23.8 | 9.4 | 34
KJ090 | 7.5 | 2625 | 75 | 67 | 125 | 72.8 | 0.518 | 13.3 | 37.7 | 9.4 | 34
KJ090 | 7.5 | 2625 | 80 | 67 | 125 | 72.8 | 0.71 | 18.24 | 51.7 | 9.4 | 34
KJ090 | 7.5 | 2625 | 85 | 67 | 125 | 72.8 | 0.856 | 21.98 | 62.3 | 9.4 | 34
KJ090 | 7.5 | 2625 | 90 | 67 | 125 | 72.8 | 1 | 25.68 | 72.8 | 9.4 | 34
KJ090 | 7.5 | 2625 | 75 | 72 | 125 | 77 | 0.321 | 8.71 | 24.7 | 9.4 | 34
KJ090 | 7.5 | 2625 | 80 | 72 | 125 | 77 | 0.496 | 13.47 | 38.2 | 9.4 | 34
KJ090 | 7.5 | 2625 | 85 | 72 | 125 | 77 | 0.67 | 18.2 | 51.6 | 9.4 | 34
KJ090 | 7.5 | 2625 | 90 | 72 | 125 | 77 | 0.845 | 22.96 | 65.1 | 9.4 | 34
KJ090 | 7.5 | 2625 | 80 | 77 | 125 | 81.1 | 0.305 | 8.71 | 24.7 | 9.5 | 34
KJ090 | 7.5 | 2625 | 85 | 77 | 125 | 81.1 | 0.504 | 14.43 | 40.9 | 9.5 | 34
KJ090 | 7.5 | 2625 | 90 | 77 | 125 | 81.1 | 0.705 | 20.18 | 57.2 | 9.5 | 34
KJ090 | 7.5 | 3000 | 65 | 57 | 75 | 100.3 | 0.583 | 18.06 | 58.5 | 4.7 | 33
KJ090 | 7.5 | 3000 | 70 | 57 | 75 | 100.3 | 0.736 | 22.78 | 73.8 | 4.7 | 33
KJ090 | 7.5 | 3000 | 75 | 57 | 75 | 100.3 | 0.889 | 27.53 | 89.2 | 4.7 | 33
KJ090 | 7.5 | 3000 | 80 | 57 | 75 | 100.3 | 1 | 30.96 | 100.3 | 4.7 | 33
KJ090 | 7.5 | 3000 | 85 | 57 | 75 | 100.3 | 1 | 30.96 | 100.3 | 4.7 | 33
KJ090 | 7.5 | 3000 | 90 | 57 | 75 | 100.3 | 1 | 30.96 | 100.3 | 4.7 | 33
KJ090 | 7.5 | 3000 | 65 | 62 | 75 | 103.9 | 0.407 | 13.06 | 42.3 | 4.7 | 33
KJ090 | 7.5 | 3000 | 70 | 62 | 75 | 103.9 | 0.557 | 17.87 | 57.9 | 4.7 | 33
KJ090 | 7.5 | 3000 | 75 | 62 | 75 | 103.9 | 0.709 | 22.75 | 73.7 | 4.7 | 33
KJ090 | 7.5 | 3000 | 80 | 62 | 75 | 103.9 | 0.857 | 27.47 | 89 | 4.7 | 33
KJ090 | 7.5 | 3000 | 85 | 62 | 75 | 103.9 | 0.936 | 30.03 | 97.3 | 4.7 | 33
KJ090 | 7.5 | 3000 | 90 | 62 | 75 | 103.9 | 1 | 32.07 | 103.9 | 4.7 | 33
KJ090 | 7.5 | 3000 | 70 | 67 | 75 | 107.4 | 0.39 | 12.93 | 41.9 | 4.7 | 33
KJ090 | 7.5 | 3000 | 75 | 67 | 75 | 107.4 | 0.54 | 17.9 | 58 | 4.7 | 33
KJ090 | 7.5 | 3000 | 80 | 67 | 75 | 107.4 | 0.684 | 22.69 | 73.5 | 4.7 | 33
KJ090 | 7.5 | 3000 | 85 | 67 | 75 | 107.4 | 0.818 | 27.1 | 87.8 | 4.7 | 33
KJ090 | 7.5 | 3000 | 90 | 67 | 75 | 107.4 | 0.951 | 31.51 | 102.1 | 4.7 | 33
KJ090 | 7.5 | 3000 | 75 | 72 | 75 | 116.9 | 0.358 | 12.93 | 41.9 | 4.7 | 33
KJ090 | 7.5 | 3000 | 80 | 72 | 75 | 116.9 | 0.495 | 17.87 | 57.9 | 4.7 | 33
KJ090 | 7.5 | 3000 | 85 | 72 | 75 | 116.9 | 0.632 | 22.81 | 73.9 | 4.7 | 33
KJ090 | 7.5 | 3000 | 90 | 72 | 75 | 116.9 | 0.77 | 27.78 | 90 | 4.7 | 33
KJ090 | 7.5 | 3000 | 80 | 77 | 75 | 126.4 | 0.335 | 13.09 | 42.4 | 4.8 | 33
KJ090 | 7.5 | 3000 | 85 | 77 | 75 | 126.4 | 0.475 | 18.55 | 60.1 | 4.8 | 33
KJ090 | 7.5 | 3000 | 90 | 77 | 75 | 126.4 | 0.616 | 24.01 | 77.8 | 4.8 | 33
KJ090 | 7.5 | 3000 | 65 | 57 | 85 | 96.2 | 0.568 | 16.85 | 54.6 | 5.5 | 33
KJ090 | 7.5 | 3000 | 70 | 57 | 85 | 96.2 | 0.734 | 21.79 | 70.6 | 5.5 | 33
KJ090 | 7.5 | 3000 | 75 | 57 | 85 | 96.2 | 0.901 | 26.76 | 86.7 | 5.5 | 33
KJ090 | 7.5 | 3000 | 80 | 57 | 85 | 96.2 | 1 | 29.69 | 96.2 | 5.5 | 33
KJ090 | 7.5 | 3000 | 85 | 57 | 85 | 96.2 | 1 | 29.69 | 96.2 | 5.5 | 33
KJ090 | 7.5 | 3000 | 90 | 57 | 85 | 96.2 | 1 | 29.69 | 96.2 | 5.5 | 33
KJ090 | 7.5 | 3000 | 65 | 62 | 85 | 98.6 | 0.391 | 11.91 | 38.6 | 5.5 | 33
KJ090 | 7.5 | 3000 | 70 | 62 | 85 | 98.6 | 0.554 | 16.85 | 54.6 | 5.5 | 33
KJ090 | 7.5 | 3000 | 75 | 62 | 85 | 98.6 | 0.718 | 21.85 | 70.8 | 5.5 | 33
KJ090 | 7.5 | 3000 | 80 | 62 | 85 | 98.6 | 0.879 | 26.76 | 86.7 | 5.5 | 33
KJ090 | 7.5 | 3000 | 85 | 62 | 85 | 98.6 | 0.949 | 28.89 | 93.6 | 5.5 | 33
KJ090 | 7.5 | 3000 | 90 | 62 | 85 | 98.6 | 1 | 30.43 | 98.6 | 5.5 | 33
KJ090 | 7.5 | 3000 | 70 | 67 | 85 | 101 | 0.383 | 11.94 | 38.7 | 5.5 | 33
KJ090 | 7.5 | 3000 | 75 | 67 | 85 | 101 | 0.543 | 16.91 | 54.8 | 5.5 | 33
KJ090 | 7.5 | 3000 | 80 | 67 | 85 | 101 | 0.699 | 21.79 | 70.6 | 5.5 | 33
KJ090 | 7.5 | 3000 | 85 | 67 | 85 | 101 | 0.832 | 25.93 | 84 | 5.5 | 33
KJ090 | 7.5 | 3000 | 90 | 67 | 85 | 101 | 0.964 | 30.06 | 97.4 | 5.5 | 33
KJ090 | 7.5 | 3000 | 75 | 72 | 85 | 108.9 | 0.354 | 11.91 | 38.6 | 5.5 | 33
KJ090 | 7.5 | 3000 | 80 | 72 | 85 | 108.9 | 0.5 | 16.82 | 54.5 | 5.5 | 33
KJ090 | 7.5 | 3000 | 85 | 72 | 85 | 108.9 | 0.647 | 21.76 | 70.5 | 5.5 | 33
KJ090 | 7.5 | 3000 | 90 | 72 | 85 | 108.9 | 0.793 | 26.67 | 86.4 | 5.5 | 33
KJ090 | 7.5 | 3000 | 80 | 77 | 85 | 116.8 | 0.33 | 11.88 | 38.5 | 5.5 | 33
KJ090 | 7.5 | 3000 | 85 | 77 | 85 | 116.8 | 0.488 | 17.59 | 57 | 5.5 | 33
KJ090 | 7.5 | 3000 | 90 | 77 | 85 | 116.8 | 0.646 | 23.3 | 75.5 | 5.5 | 33
KJ090 | 7.5 | 3000 | 65 | 57 | 95 | 92 | 0.551 | 15.65 | 50.7 | 6.3 | 33
KJ090 | 7.5 | 3000 | 70 | 57 | 95 | 92 | 0.733 | 20.8 | 67.4 | 6.3 | 33
KJ090 | 7.5 | 3000 | 75 | 57 | 95 | 92 | 0.915 | 25.99 | 84.2 | 6.3 | 33
KJ090 | 7.5 | 3000 | 80 | 57 | 95 | 92 | 1 | 28.4 | 92 | 6.3 | 33
KJ090 | 7.5 | 3000 | 85 | 57 | 95 | 92 | 1 | 28.4 | 92 | 6.3 | 33
KJ090 | 7.5 | 3000 | 90 | 57 | 95 | 92 | 1 | 28.4 | 92 | 6.3 | 33
KJ090 | 7.5 | 3000 | 65 | 62 | 95 | 93.3 | 0.375 | 10.8 | 35 | 6.3 | 33
KJ090 | 7.5 | 3000 | 70 | 62 | 95 | 93.3 | 0.551 | 15.86 | 51.4 | 6.3 | 33
KJ090 | 7.5 | 3000 | 75 | 62 | 95 | 93.3 | 0.728 | 20.96 | 67.9 | 6.3 | 33
KJ090 | 7.5 | 3000 | 80 | 62 | 95 | 93.3 | 0.904 | 26.02 | 84.3 | 6.3 | 33
KJ090 | 7.5 | 3000 | 85 | 62 | 95 | 93.3 | 0.964 | 27.75 | 89.9 | 6.3 | 33
KJ090 | 7.5 | 3000 | 90 | 62 | 95 | 93.3 | 1 | 28.8 | 93.3 | 6.3 | 33
KJ090 | 7.5 | 3000 | 70 | 67 | 95 | 94.5 | 0.375 | 10.93 | 35.4 | 6.3 | 33
KJ090 | 7.5 | 3000 | 75 | 67 | 95 | 94.5 | 0.546 | 15.93 | 51.6 | 6.3 | 33
KJ090 | 7.5 | 3000 | 80 | 67 | 95 | 94.5 | 0.716 | 20.9 | 67.7 | 6.3 | 33
KJ090 | 7.5 | 3000 | 85 | 67 | 95 | 94.5 | 0.849 | 24.75 | 80.2 | 6.3 | 33
KJ090 | 7.5 | 3000 | 90 | 67 | 95 | 94.5 | 0.981 | 28.61 | 92.7 | 6.3 | 33
KJ090 | 7.5 | 3000 | 75 | 72 | 95 | 100.9 | 0.35 | 10.9 | 35.3 | 6.3 | 33
KJ090 | 7.5 | 3000 | 80 | 72 | 95 | 100.9 | 0.507 | 15.8 | 51.2 | 6.3 | 33
KJ090 | 7.5 | 3000 | 85 | 72 | 95 | 100.9 | 0.664 | 20.68 | 67 | 6.3 | 33
KJ090 | 7.5 | 3000 | 90 | 72 | 95 | 100.9 | 0.822 | 25.59 | 82.9 | 6.3 | 33
KJ090 | 7.5 | 3000 | 80 | 77 | 95 | 107.2 | 0.323 | 10.68 | 34.6 | 6.3 | 33
KJ090 | 7.5 | 3000 | 85 | 77 | 95 | 107.2 | 0.503 | 16.64 | 53.9 | 6.3 | 33
KJ090 | 7.5 | 3000 | 90 | 77 | 95 | 107.2 | 0.682 | 22.56 | 73.1 | 6.3 | 33
KJ090 | 7.5 | 3000 | 65 | 57 | 105 | 86 | 0.528 | 14.01 | 45.4 | 7.4 | 33
KJ090 | 7.5 | 3000 | 70 | 57 | 105 | 86 | 0.726 | 19.26 | 62.4 | 7.4 | 33
KJ090 | 7.5 | 3000 | 75 | 57 | 105 | 86 | 0.922 | 24.48 | 79.3 | 7.4 | 33
KJ090 | 7.5 | 3000 | 80 | 57 | 105 | 86 | 1 | 26.54 | 86 | 7.4 | 33
KJ090 | 7.5 | 3000 | 85 | 57 | 105 | 86 | 1 | 26.54 | 86 | 7.4 | 33
KJ090 | 7.5 | 3000 | 90 | 57 | 105 | 86 | 1 | 26.54 | 86 | 7.4 | 33
KJ090 | 7.5 | 3000 | 65 | 62 | 105 | 87.1 | 0.35 | 9.41 | 30.5 | 7.4 | 33
KJ090 | 7.5 | 3000 | 70 | 62 | 105 | 87.1 | 0.54 | 14.51 | 47 | 7.4 | 33
KJ090 | 7.5 | 3000 | 75 | 62 | 105 | 87.1 | 0.729 | 19.6 | 63.5 | 7.4 | 33
KJ090 | 7.5 | 3000 | 80 | 62 | 105 | 87.1 | 0.918 | 24.69 | 80 | 7.4 | 33
KJ090 | 7.5 | 3000 | 85 | 62 | 105 | 87.1 | 0.97 | 26.08 | 84.5 | 7.4 | 33
KJ090 | 7.5 | 3000 | 90 | 62 | 105 | 87.1 | 1 | 26.88 | 87.1 | 7.4 | 33
KJ090 | 7.5 | 3000 | 70 | 67 | 105 | 88.2 | 0.358 | 9.75 | 31.6 | 7.4 | 33
KJ090 | 7.5 | 3000 | 75 | 67 | 105 | 88.2 | 0.541 | 14.72 | 47.7 | 7.4 | 33
KJ090 | 7.5 | 3000 | 80 | 67 | 105 | 88.2 | 0.722 | 19.66 | 63.7 | 7.4 | 33
KJ090 | 7.5 | 3000 | 85 | 67 | 105 | 88.2 | 0.854 | 23.24 | 75.3 | 7.4 | 33
KJ090 | 7.5 | 3000 | 90 | 67 | 105 | 88.2 | 0.986 | 26.85 | 87 | 7.4 | 33
KJ090 | 7.5 | 3000 | 75 | 72 | 105 | 93.5 | 0.34 | 9.81 | 31.8 | 7.4 | 33
KJ090 | 7.5 | 3000 | 80 | 72 | 105 | 93.5 | 0.508 | 14.66 | 47.5 | 7.4 | 33
KJ090 | 7.5 | 3000 | 85 | 72 | 105 | 93.5 | 0.675 | 19.48 | 63.1 | 7.4 | 33
KJ090 | 7.5 | 3000 | 90 | 72 | 105 | 93.5 | 0.842 | 24.29 | 78.7 | 7.4 | 33
KJ090 | 7.5 | 3000 | 80 | 77 | 105 | 98.8 | 0.316 | 9.63 | 31.2 | 7.4 | 33
KJ090 | 7.5 | 3000 | 85 | 77 | 105 | 98.8 | 0.514 | 15.68 | 50.8 | 7.4 | 33
KJ090 | 7.5 | 3000 | 90 | 77 | 105 | 98.8 | 0.713 | 21.73 | 70.4 | 7.4 | 33
KJ090 | 7.5 | 3000 | 65 | 57 | 115 | 80 | 0.503 | 12.41 | 40.2 | 8.4 | 34
KJ090 | 7.5 | 3000 | 70 | 57 | 115 | 80 | 0.716 | 17.69 | 57.3 | 8.4 | 34
KJ090 | 7.5 | 3000 | 75 | 57 | 115 | 80 | 0.93 | 22.96 | 74.4 | 8.4 | 34
KJ090 | 7.5 | 3000 | 80 | 57 | 115 | 80 | 1 | 24.69 | 80 | 8.4 | 34
KJ090 | 7.5 | 3000 | 85 | 57 | 115 | 80 | 1 | 24.69 | 80 | 8.4 | 34
KJ090 | 7.5 | 3000 | 90 | 57 | 115 | 80 | 1 | 24.69 | 80 | 8.4 | 34
KJ090 | 7.5 | 3000 | 65 | 62 | 115 | 81 | 0.321 | 8.02 | 26 | 8.4 | 34
KJ090 | 7.5 | 3000 | 70 | 62 | 115 | 81 | 0.525 | 13.12 | 42.5 | 8.4 | 34
KJ090 | 7.5 | 3000 | 75 | 62 | 115 | 81 | 0.73 | 18.24 | 59.1 | 8.4 | 34
KJ090 | 7.5 | 3000 | 80 | 62 | 115 | 81 | 0.933 | 23.33 | 75.6 | 8.4 | 34
KJ090 | 7.5 | 3000 | 85 | 62 | 115 | 81 | 0.975 | 24.38 | 79 | 8.4 | 34
KJ090 | 7.5 | 3000 | 90 | 62 | 115 | 81 | 1 | 25 | 81 | 8.4 | 34
KJ090 | 7.5 | 3000 | 70 | 67 | 115 | 82 | 0.339 | 8.58 | 27.8 | 8.4 | 34
KJ090 | 7.5 | 3000 | 75 | 67 | 115 | 82 | 0.533 | 13.49 | 43.7 | 8.4 | 34
KJ090 | 7.5 | 3000 | 80 | 67 | 115 | 82 | 0.728 | 18.43 | 59.7 | 8.4 | 34
KJ090 | 7.5 | 3000 | 85 | 67 | 115 | 82 | 0.86 | 21.76 | 70.5 | 8.4 | 34
KJ090 | 7.5 | 3000 | 90 | 67 | 115 | 82 | 0.99 | 25.06 | 81.2 | 8.4 | 34
KJ090 | 7.5 | 3000 | 75 | 72 | 115 | 86.2 | 0.329 | 8.77 | 28.4 | 8.5 | 34
KJ090 | 7.5 | 3000 | 80 | 72 | 115 | 86.2 | 0.507 | 13.49 | 43.7 | 8.5 | 34
KJ090 | 7.5 | 3000 | 85 | 72 | 115 | 86.2 | 0.686 | 18.24 | 59.1 | 8.5 | 34
KJ090 | 7.5 | 3000 | 90 | 72 | 115 | 86.2 | 0.863 | 22.96 | 74.4 | 8.5 | 34
KJ090 | 7.5 | 3000 | 80 | 77 | 115 | 90.4 | 0.308 | 8.58 | 27.8 | 8.5 | 34
KJ090 | 7.5 | 3000 | 85 | 77 | 115 | 90.4 | 0.528 | 14.72 | 47.7 | 8.5 | 34
KJ090 | 7.5 | 3000 | 90 | 77 | 115 | 90.4 | 0.748 | 20.86 | 67.6 | 8.5 | 34
KJ090 | 7.5 | 3000 | 65 | 57 | 125 | 74 | 0.472 | 10.77 | 34.9 | 9.5 | 34
KJ090 | 7.5 | 3000 | 70 | 57 | 125 | 74 | 0.705 | 16.11 | 52.2 | 9.5 | 34
KJ090 | 7.5 | 3000 | 75 | 57 | 125 | 74 | 0.941 | 21.48 | 69.6 | 9.5 | 34
KJ090 | 7.5 | 3000 | 80 | 57 | 125 | 74 | 1 | 22.84 | 74 | 9.5 | 34
KJ090 | 7.5 | 3000 | 85 | 57 | 125 | 74 | 1 | 22.84 | 74 | 9.5 | 34
KJ090 | 7.5 | 3000 | 90 | 57 | 125 | 74 | 1 | 22.84 | 74 | 9.5 | 34
KJ090 | 7.5 | 3000 | 65 | 62 | 125 | 74.8 | 0.287 | 6.64 | 21.5 | 9.5 | 34
KJ090 | 7.5 | 3000 | 70 | 62 | 125 | 74.8 | 0.509 | 11.76 | 38.1 | 9.5 | 34
KJ090 | 7.5 | 3000 | 75 | 62 | 125 | 74.8 | 0.731 | 16.88 | 54.7 | 9.5 | 34
KJ090 | 7.5 | 3000 | 80 | 62 | 125 | 74.8 | 0.953 | 22.01 | 71.3 | 9.5 | 34
KJ090 | 7.5 | 3000 | 85 | 62 | 125 | 74.8 | 0.983 | 22.69 | 73.5 | 9.5 | 34
KJ090 | 7.5 | 3000 | 90 | 62 | 125 | 74.8 | 1 | 23.09 | 74.8 | 9.5 | 34
KJ090 | 7.5 | 3000 | 70 | 67 | 125 | 75.7 | 0.317 | 7.41 | 24 | 9.5 | 34
KJ090 | 7.5 | 3000 | 75 | 67 | 125 | 75.7 | 0.526 | 12.28 | 39.8 | 9.5 | 34
KJ090 | 7.5 | 3000 | 80 | 67 | 125 | 75.7 | 0.736 | 17.19 | 55.7 | 9.5 | 34
KJ090 | 7.5 | 3000 | 85 | 67 | 125 | 75.7 | 0.867 | 20.25 | 65.6 | 9.5 | 34
KJ090 | 7.5 | 3000 | 90 | 67 | 125 | 75.7 | 0.997 | 23.3 | 75.5 | 9.5 | 34
KJ090 | 7.5 | 3000 | 75 | 72 | 125 | 78.8 | 0.316 | 7.69 | 24.9 | 9.5 | 34
KJ090 | 7.5 | 3000 | 80 | 72 | 125 | 78.8 | 0.508 | 12.35 | 40 | 9.5 | 34
KJ090 | 7.5 | 3000 | 85 | 72 | 125 | 78.8 | 0.699 | 17.01 | 55.1 | 9.5 | 34
KJ090 | 7.5 | 3000 | 90 | 72 | 125 | 78.8 | 0.891 | 21.67 | 70.2 | 9.5 | 34
KJ090 | 7.5 | 3000 | 80 | 77 | 125 | 82 | 0.298 | 7.53 | 24.4 | 9.5 | 34
KJ090 | 7.5 | 3000 | 85 | 77 | 125 | 82 | 0.544 | 13.77 | 44.6 | 9.5 | 34
KJ090 | 7.5 | 3000 | 90 | 77 | 125 | 82 | 0.791 | 20.03 | 64.9 | 9.5 | 34
KJ090 | 7.5 | 3375 | 65 | 57 | 75 | 107.2 | 0.578 | 17.01 | 62 | 4.7 | 33
KJ090 | 7.5 | 3375 | 70 | 57 | 75 | 107.2 | 0.745 | 21.92 | 79.9 | 4.7 | 33
KJ090 | 7.5 | 3375 | 75 | 57 | 75 | 107.2 | 0.912 | 26.83 | 97.8 | 4.7 | 33
KJ090 | 7.5 | 3375 | 80 | 57 | 75 | 107.2 | 0.999 | 29.38 | 107.1 | 4.7 | 33
KJ090 | 7.5 | 3375 | 85 | 57 | 75 | 107.2 | 0.999 | 29.38 | 107.1 | 4.7 | 33
KJ090 | 7.5 | 3375 | 90 | 57 | 75 | 107.2 | 0.999 | 29.38 | 107.1 | 4.7 | 33
KJ090 | 7.5 | 3375 | 65 | 62 | 75 | 109 | 0.397 | 11.88 | 43.3 | 4.7 | 33
KJ090 | 7.5 | 3375 | 70 | 62 | 75 | 109 | 0.561 | 16.79 | 61.2 | 4.7 | 33
KJ090 | 7.5 | 3375 | 75 | 62 | 75 | 109 | 0.728 | 21.76 | 79.3 | 4.7 | 33
KJ090 | 7.5 | 3375 | 80 | 62 | 75 | 109 | 0.892 | 26.67 | 97.2 | 4.7 | 33
KJ090 | 7.5 | 3375 | 85 | 62 | 75 | 109 | 0.951 | 28.45 | 103.7 | 4.7 | 33
KJ090 | 7.5 | 3375 | 90 | 62 | 75 | 109 | 1 | 29.9 | 109 | 4.7 | 33
KJ090 | 7.5 | 3375 | 70 | 67 | 75 | 110.8 | 0.384 | 11.69 | 42.6 | 4.7 | 33
KJ090 | 7.5 | 3375 | 75 | 67 | 75 | 110.8 | 0.549 | 16.68 | 60.8 | 4.7 | 33
KJ090 | 7.5 | 3375 | 80 | 67 | 75 | 110.8 | 0.71 | 21.59 | 78.7 | 4.7 | 33
KJ090 | 7.5 | 3375 | 85 | 67 | 75 | 110.8 | 0.847 | 25.73 | 93.8 | 4.7 | 33
KJ090 | 7.5 | 3375 | 90 | 67 | 75 | 110.8 | 0.983 | 29.88 | 108.9 | 4.7 | 33
KJ090 | 7.5 | 3375 | 75 | 72 | 75 | 119.6 | 0.351 | 11.52 | 42 | 4.7 | 33
KJ090 | 7.5 | 3375 | 80 | 72 | 75 | 119.6 | 0.503 | 16.49 | 60.1 | 4.7 | 33
KJ090 | 7.5 | 3375 | 85 | 72 | 75 | 119.6 | 0.655 | 21.48 | 78.3 | 4.7 | 33
KJ090 | 7.5 | 3375 | 90 | 72 | 75 | 119.6 | 0.806 | 26.45 | 96.4 | 4.7 | 33
KJ090 | 7.5 | 3375 | 65 | 57 | 85 | 102.7 | 0.564 | 15.88 | 57.9 | 5.5 | 33
KJ090 | 7.5 | 3375 | 70 | 57 | 85 | 102.7 | 0.741 | 20.88 | 76.1 | 5.5 | 33
KJ090 | 7.5 | 3375 | 75 | 57 | 85 | 102.7 | 0.918 | 25.87 | 94.3 | 5.5 | 33
KJ090 | 7.5 | 3375 | 80 | 57 | 85 | 102.7 | 1 | 28.18 | 102.7 | 5.5 | 33
KJ090 | 7.5 | 3375 | 85 | 57 | 85 | 102.7 | 1 | 28.18 | 102.7 | 5.5 | 33
KJ090 | 7.5 | 3375 | 90 | 57 | 85 | 102.7 | 1 | 28.18 | 102.7 | 5.5 | 33
KJ090 | 7.5 | 3375 | 65 | 62 | 85 | 103.5 | 0.383 | 10.86 | 39.6 | 5.5 | 33
KJ090 | 7.5 | 3375 | 70 | 62 | 85 | 103.5 | 0.557 | 15.83 | 57.7 | 5.5 | 33
KJ090 | 7.5 | 3375 | 75 | 62 | 85 | 103.5 | 0.733 | 20.82 | 75.9 | 5.5 | 33
KJ090 | 7.5 | 3375 | 80 | 62 | 85 | 103.5 | 0.908 | 25.79 | 94 | 5.5 | 33
KJ090 | 7.5 | 3375 | 85 | 62 | 85 | 103.5 | 0.959 | 27.24 | 99.3 | 5.5 | 33
KJ090 | 7.5 | 3375 | 90 | 62 | 85 | 103.5 | 1 | 28.4 | 103.5 | 5.5 | 33
KJ090 | 7.5 | 3375 | 70 | 67 | 85 | 104.3 | 0.377 | 10.78 | 39.3 | 5.5 | 33
KJ090 | 7.5 | 3375 | 75 | 67 | 85 | 104.3 | 0.551 | 15.78 | 57.5 | 5.5 | 33
KJ090 | 7.5 | 3375 | 80 | 67 | 85 | 104.3 | 0.724 | 20.71 | 75.5 | 5.5 | 33
KJ090 | 7.5 | 3375 | 85 | 67 | 85 | 104.3 | 0.857 | 24.53 | 89.4 | 5.5 | 33
KJ090 | 7.5 | 3375 | 90 | 67 | 85 | 104.3 | 0.99 | 28.34 | 103.3 | 5.5 | 33
KJ090 | 7.5 | 3375 | 75 | 72 | 85 | 113.7 | 0.343 | 10.7 | 39 | 5.5 | 33
KJ090 | 7.5 | 3375 | 80 | 72 | 85 | 113.7 | 0.502 | 15.67 | 57.1 | 5.5 | 33
KJ090 | 7.5 | 3375 | 85 | 72 | 85 | 113.7 | 0.661 | 20.63 | 75.2 | 5.5 | 33
KJ090 | 7.5 | 3375 | 90 | 72 | 85 | 113.7 | 0.82 | 25.57 | 93.2 | 5.5 | 33
KJ090 | 7.5 | 3375 | 65 | 57 | 95 | 98.1 | 0.549 | 14.79 | 53.9 | 6.3 | 33
KJ090 | 7.5 | 3375 | 70 | 57 | 95 | 98.1 | 0.738 | 19.86 | 72.4 | 6.3 | 33
KJ090 | 7.5 | 3375 | 75 | 57 | 95 | 98.1 | 0.926 | 24.91 | 90.8 | 6.3 | 33
KJ090 | 7.5 | 3375 | 80 | 57 | 95 | 98.1 | 1 | 26.91 | 98.1 | 6.3 | 33
KJ090 | 7.5 | 3375 | 85 | 57 | 95 | 98.1 | 1 | 26.91 | 98.1 | 6.3 | 33
KJ090 | 7.5 | 3375 | 90 | 57 | 95 | 98.1 | 1 | 26.91 | 98.1 | 6.3 | 33
KJ090 | 7.5 | 3375 | 65 | 62 | 95 | 97.9 | 0.367 | 9.85 | 35.9 | 6.3 | 33
KJ090 | 7.5 | 3375 | 70 | 62 | 95 | 97.9 | 0.554 | 14.87 | 54.2 | 6.3 | 33
KJ090 | 7.5 | 3375 | 75 | 62 | 95 | 97.9 | 0.741 | 19.89 | 72.5 | 6.3 | 33
KJ090 | 7.5 | 3375 | 80 | 62 | 95 | 97.9 | 0.927 | 24.91 | 90.8 | 6.3 | 33
KJ090 | 7.5 | 3375 | 85 | 62 | 95 | 97.9 | 0.97 | 26.06 | 95 | 6.3 | 33
KJ090 | 7.5 | 3375 | 90 | 62 | 95 | 97.9 | 1 | 26.86 | 97.9 | 6.3 | 33
KJ090 | 7.5 | 3375 | 70 | 67 | 95 | 97.7 | 0.369 | 9.9 | 36.1 | 6.3 | 33
KJ090 | 7.5 | 3375 | 75 | 67 | 95 | 97.7 | 0.555 | 14.87 | 54.2 | 6.3 | 33
KJ090 | 7.5 | 3375 | 80 | 67 | 95 | 97.7 | 0.741 | 19.86 | 72.4 | 6.3 | 33
KJ090 | 7.5 | 3375 | 85 | 67 | 95 | 97.7 | 0.87 | 23.32 | 85 | 6.3 | 33
KJ090 | 7.5 | 3375 | 90 | 67 | 95 | 97.7 | 0.999 | 26.78 | 97.6 | 6.3 | 33
KJ090 | 7.5 | 3375 | 75 | 72 | 95 | 103.2 | 0.349 | 9.88 | 36 | 6.4 | 33
KJ090 | 7.5 | 3375 | 80 | 72 | 95 | 103.2 | 0.523 | 14.81 | 54 | 6.4 | 33
KJ090 | 7.5 | 3375 | 85 | 72 | 95 | 103.2 | 0.699 | 19.78 | 72.1 | 6.4 | 33
KJ090 | 7.5 | 3375 | 90 | 72 | 95 | 103.2 | 0.873 | 24.72 | 90.1 | 6.4 | 33
KJ090 | 7.5 | 3375 | 65 | 57 | 105 | 91.1 | 0.526 | 13.14 | 47.9 | 7.4 | 33
KJ090 | 7.5 | 3375 | 70 | 57 | 105 | 91.1 | 0.733 | 18.33 | 66.8 | 7.4 | 33
KJ090 | 7.5 | 3375 | 75 | 57 | 105 | 91.1 | 0.941 | 23.51 | 85.7 | 7.4 | 33
KJ090 | 7.5 | 3375 | 80 | 57 | 105 | 91.1 | 1 | 24.99 | 91.1 | 7.4 | 33
KJ090 | 7.5 | 3375 | 85 | 57 | 105 | 91.1 | 1 | 24.99 | 91.1 | 7.4 | 33
KJ090 | 7.5 | 3375 | 90 | 57 | 105 | 91.1 | 1 | 24.99 | 91.1 | 7.4 | 33
KJ090 | 7.5 | 3375 | 65 | 62 | 105 | 91.2 | 0.34 | 8.5 | 31 | 7.4 | 33
KJ090 | 7.5 | 3375 | 70 | 62 | 105 | 91.2 | 0.542 | 13.55 | 49.4 | 7.4 | 33
KJ090 | 7.5 | 3375 | 75 | 62 | 105 | 91.2 | 0.745 | 18.63 | 67.9 | 7.4 | 33
KJ090 | 7.5 | 3375 | 80 | 62 | 105 | 91.2 | 0.947 | 23.7 | 86.4 | 7.4 | 33
KJ090 | 7.5 | 3375 | 85 | 62 | 105 | 91.2 | 0.978 | 24.47 | 89.2 | 7.4 | 33
KJ090 | 7.5 | 3375 | 90 | 62 | 105 | 91.2 | 1 | 25.02 | 91.2 | 7.4 | 33
KJ090 | 7.5 | 3375 | 70 | 67 | 105 | 91.3 | 0.352 | 8.81 | 32.1 | 7.4 | 33
KJ090 | 7.5 | 3375 | 75 | 67 | 105 | 91.3 | 0.549 | 13.74 | 50.1 | 7.4 | 33
KJ090 | 7.5 | 3375 | 80 | 67 | 105 | 91.3 | 0.747 | 18.71 | 68.2 | 7.4 | 33
KJ090 | 7.5 | 3375 | 85 | 67 | 105 | 91.3 | 0.872 | 21.84 | 79.6 | 7.4 | 33
KJ090 | 7.5 | 3375 | 90 | 67 | 105 | 91.3 | 0.998 | 24.99 | 91.1 | 7.4 | 33
KJ090 | 7.5 | 3375 | 75 | 72 | 105 | 95.7 | 0.338 | 8.86 | 32.3 | 7.4 | 33
KJ090 | 7.5 | 3375 | 80 | 72 | 105 | 95.7 | 0.522 | 13.72 | 50 | 7.4 | 33
KJ090 | 7.5 | 3375 | 85 | 72 | 105 | 95.7 | 0.706 | 18.55 | 67.6 | 7.4 | 33
KJ090 | 7.5 | 3375 | 90 | 72 | 105 | 95.7 | 0.89 | 23.37 | 85.2 | 7.4 | 33
KJ090 | 7.5 | 3375 | 65 | 57 | 115 | 84 | 0.499 | 11.5 | 41.9 | 8.4 | 34
KJ090 | 7.5 | 3375 | 70 | 57 | 115 | 84 | 0.729 | 16.79 | 61.2 | 8.4 | 34
KJ090 | 7.5 | 3375 | 75 | 57 | 115 | 84 | 0.958 | 22.09 | 80.5 | 8.4 | 34
KJ090 | 7.5 | 3375 | 80 | 57 | 115 | 84 | 1 | 23.05 | 84 | 8.4 | 34
KJ090 | 7.5 | 3375 | 85 | 57 | 115 | 84 | 1 | 23.05 | 84 | 8.4 | 34
KJ090 | 7.5 | 3375 | 90 | 57 | 115 | 84 | 1 | 23.05 | 84 | 8.4 | 34
KJ090 | 7.5 | 3375 | 65 | 62 | 115 | 84.5 | 0.308 | 7.13 | 26 | 8.4 | 34
KJ090 | 7.5 | 3375 | 70 | 62 | 115 | 84.5 | 0.529 | 12.26 | 44.7 | 8.4 | 34
KJ090 | 7.5 | 3375 | 75 | 62 | 115 | 84.5 | 0.749 | 17.37 | 63.3 | 8.4 | 34
KJ090 | 7.5 | 3375 | 80 | 62 | 115 | 84.5 | 0.969 | 22.47 | 81.9 | 8.4 | 34
KJ090 | 7.5 | 3375 | 85 | 62 | 115 | 84.5 | 0.987 | 22.88 | 83.4 | 8.4 | 34
KJ090 | 7.5 | 3375 | 90 | 62 | 115 | 84.5 | 1 | 23.18 | 84.5 | 8.4 | 34
KJ090 | 7.5 | 3375 | 70 | 67 | 115 | 85 | 0.331 | 7.71 | 28.1 | 8.4 | 34
KJ090 | 7.5 | 3375 | 75 | 67 | 115 | 85 | 0.541 | 12.62 | 46 | 8.4 | 34
KJ090 | 7.5 | 3375 | 80 | 67 | 115 | 85 | 0.752 | 17.53 | 63.9 | 8.4 | 34
KJ090 | 7.5 | 3375 | 85 | 67 | 115 | 85 | 0.874 | 20.38 | 74.3 | 8.4 | 34
KJ090 | 7.5 | 3375 | 90 | 67 | 115 | 85 | 0.995 | 23.21 | 84.6 | 8.4 | 34
KJ090 | 7.5 | 3375 | 75 | 72 | 115 | 88.2 | 0.325 | 7.87 | 28.7 | 8.5 | 34
KJ090 | 7.5 | 3375 | 80 | 72 | 115 | 88.2 | 0.52 | 12.59 | 45.9 | 8.5 | 34
KJ090 | 7.5 | 3375 | 85 | 72 | 115 | 88.2 | 0.715 | 17.31 | 63.1 | 8.5 | 34
KJ090 | 7.5 | 3375 | 90 | 72 | 115 | 88.2 | 0.91 | 22.03 | 80.3 | 8.5 | 34
KJ090 | 7.5 | 3375 | 65 | 57 | 125 | 76.9 | 0.466 | 9.82 | 35.8 | 9.5 | 34
KJ090 | 7.5 | 3375 | 70 | 57 | 125 | 76.9 | 0.723 | 15.25 | 55.6 | 9.5 | 34
KJ090 | 7.5 | 3375 | 75 | 57 | 125 | 76.9 | 0.98 | 20.69 | 75.4 | 9.5 | 34
KJ090 | 7.5 | 3375 | 80 | 57 | 125 | 76.9 | 1 | 21.1 | 76.9 | 9.5 | 34
KJ090 | 7.5 | 3375 | 85 | 57 | 125 | 76.9 | 1 | 21.1 | 76.9 | 9.5 | 34
KJ090 | 7.5 | 3375 | 90 | 57 | 125 | 76.9 | 1 | 21.1 | 76.9 | 9.5 | 34
KJ090 | 7.5 | 3375 | 65 | 62 | 125 | 77.7 | 0.272 | 5.79 | 21.1 | 9.5 | 34
KJ090 | 7.5 | 3375 | 70 | 62 | 125 | 77.7 | 0.514 | 10.95 | 39.9 | 9.5 | 34
KJ090 | 7.5 | 3375 | 75 | 62 | 125 | 77.7 | 0.754 | 16.08 | 58.6 | 9.5 | 34
KJ090 | 7.5 | 3375 | 80 | 62 | 125 | 77.7 | 0.996 | 21.23 | 77.4 | 9.5 | 34
KJ090 | 7.5 | 3375 | 85 | 62 | 125 | 77.7 | 1 | 21.32 | 77.7 | 9.5 | 34
KJ090 | 7.5 | 3375 | 90 | 62 | 125 | 77.7 | 1 | 21.32 | 77.7 | 9.5 | 34
KJ090 | 7.5 | 3375 | 70 | 67 | 125 | 78.6 | 0.307 | 6.61 | 24.1 | 9.5 | 34
KJ090 | 7.5 | 3375 | 75 | 67 | 125 | 78.6 | 0.533 | 11.5 | 41.9 | 9.5 | 34
KJ090 | 7.5 | 3375 | 80 | 67 | 125 | 78.6 | 0.758 | 16.35 | 59.6 | 9.5 | 34
KJ090 | 7.5 | 3375 | 85 | 67 | 125 | 78.6 | 0.877 | 18.9 | 68.9 | 9.5 | 34
KJ090 | 7.5 | 3375 | 90 | 67 | 125 | 78.6 | 0.994 | 21.43 | 78.1 | 9.5 | 34
KJ090 | 7.5 | 3375 | 75 | 72 | 125 | 80.7 | 0.311 | 6.89 | 25.1 | 9.5 | 34
KJ090 | 7.5 | 3375 | 80 | 72 | 125 | 80.7 | 0.519 | 11.5 | 41.9 | 9.5 | 34
KJ090 | 7.5 | 3375 | 85 | 72 | 125 | 80.7 | 0.726 | 16.08 | 58.6 | 9.5 | 34
KJ090 | 7.5 | 3375 | 90 | 72 | 125 | 80.7 | 0.934 | 20.69 | 75.4 | 9.5 | 34
KJ090 | 7.5 | 3750 | 65 | 57 | 75 | 114.1 | 0.574 | 16.17 | 65.5 | 4.7 | 33
KJ090 | 7.5 | 3750 | 70 | 57 | 75 | 114.1 | 0.753 | 21.21 | 85.9 | 4.7 | 33
KJ090 | 7.5 | 3750 | 75 | 57 | 75 | 114.1 | 0.932 | 26.25 | 106.3 | 4.7 | 33
KJ090 | 7.5 | 3750 | 80 | 57 | 75 | 114.1 | 0.997 | 28.1 | 113.8 | 4.7 | 33
KJ090 | 7.5 | 3750 | 85 | 57 | 75 | 114.1 | 0.997 | 28.1 | 113.8 | 4.7 | 33
KJ090 | 7.5 | 3750 | 90 | 57 | 75 | 114.1 | 0.997 | 28.1 | 113.8 | 4.7 | 33
KJ090 | 7.5 | 3750 | 65 | 62 | 75 | 114.2 | 0.387 | 10.91 | 44.2 | 4.7 | 33
KJ090 | 7.5 | 3750 | 70 | 62 | 75 | 114.2 | 0.566 | 15.95 | 64.6 | 4.7 | 33
KJ090 | 7.5 | 3750 | 75 | 62 | 75 | 114.2 | 0.743 | 20.96 | 84.9 | 4.7 | 33
KJ090 | 7.5 | 3750 | 80 | 62 | 75 | 114.2 | 0.922 | 26 | 105.3 | 4.7 | 33
KJ090 | 7.5 | 3750 | 85 | 62 | 75 | 114.2 | 0.963 | 27.16 | 110 | 4.7 | 33
KJ090 | 7.5 | 3750 | 90 | 62 | 75 | 114.2 | 1 | 28.2 | 114.2 | 4.7 | 33
KJ090 | 7.5 | 3750 | 70 | 67 | 75 | 114.3 | 0.379 | 10.69 | 43.3 | 4.7 | 33
KJ090 | 7.5 | 3750 | 75 | 67 | 75 | 114.3 | 0.556 | 15.68 | 63.5 | 4.7 | 33
KJ090 | 7.5 | 3750 | 80 | 67 | 75 | 114.3 | 0.733 | 20.69 | 83.8 | 4.7 | 33
KJ090 | 7.5 | 3750 | 85 | 67 | 75 | 114.3 | 0.873 | 24.64 | 99.8 | 4.7 | 33
KJ090 | 7.5 | 3750 | 90 | 67 | 75 | 114.3 | 1 | 28.22 | 114.3 | 4.7 | 33
KJ090 | 7.5 | 3750 | 75 | 72 | 75 | 122.3 | 0.345 | 10.42 | 42.2 | 4.7 | 33
KJ090 | 7.5 | 3750 | 80 | 72 | 75 | 122.3 | 0.51 | 15.41 | 62.4 | 4.7 | 33
KJ090 | 7.5 | 3750 | 85 | 72 | 75 | 122.3 | 0.675 | 20.4 | 82.6 | 4.7 | 33
KJ090 | 7.5 | 3750 | 90 | 72 | 75 | 122.3 | 0.841 | 25.38 | 102.8 | 4.7 | 33
KJ090 | 7.5 | 3750 | 65 | 57 | 85 | 107.4 | 0.571 | 15.14 | 61.3 | 5.5 | 33
KJ090 | 7.5 | 3750 | 70 | 57 | 85 | 107.4 | 0.76 | 20.15 | 81.6 | 5.5 | 33
KJ090 | 7.5 | 3750 | 75 | 57 | 85 | 107.4 | 0.949 | 25.16 | 101.9 | 5.5 | 33
KJ090 | 7.5 | 3750 | 80 | 57 | 85 | 107.4 | 1 | 26.52 | 107.4 | 5.5 | 33
KJ090 | 7.5 | 3750 | 85 | 57 | 85 | 107.4 | 1 | 26.52 | 107.4 | 5.5 | 33
KJ090 | 7.5 | 3750 | 90 | 57 | 85 | 107.4 | 1 | 26.52 | 107.4 | 5.5 | 33
KJ090 | 7.5 | 3750 | 65 | 62 | 85 | 108.4 | 0.374 | 10 | 40.5 | 5.5 | 33
KJ090 | 7.5 | 3750 | 70 | 62 | 85 | 108.4 | 0.561 | 15.01 | 60.8 | 5.5 | 33
KJ090 | 7.5 | 3750 | 75 | 62 | 85 | 108.4 | 0.748 | 20.02 | 81.1 | 5.5 | 33
KJ090 | 7.5 | 3750 | 80 | 62 | 85 | 108.4 | 0.935 | 25.01 | 101.3 | 5.5 | 33
KJ090 | 7.5 | 3750 | 85 | 62 | 85 | 108.4 | 0.969 | 25.93 | 105 | 5.5 | 33
KJ090 | 7.5 | 3750 | 90 | 62 | 85 | 108.4 | 1 | 26.77 | 108.4 | 5.5 | 33
KJ090 | 7.5 | 3750 | 70 | 67 | 85 | 109.1 | 0.367 | 9.88 | 40 | 5.5 | 33
KJ090 | 7.5 | 3750 | 75 | 67 | 85 | 109.1 | 0.552 | 14.86 | 60.2 | 5.5 | 33
KJ090 | 7.5 | 3750 | 80 | 67 | 85 | 109.1 | 0.738 | 19.88 | 80.5 | 5.5 | 33
KJ090 | 7.5 | 3750 | 85 | 67 | 85 | 109.1 | 0.869 | 23.41 | 94.8 | 5.5 | 33
KJ090 | 7.5 | 3750 | 90 | 67 | 85 | 109.1 | 1 | 26.94 | 109.1 | 5.5 | 33
KJ090 | 7.5 | 3750 | 75 | 72 | 85 | 113.9 | 0.346 | 9.73 | 39.4 | 5.5 | 33
KJ090 | 7.5 | 3750 | 80 | 72 | 85 | 113.9 | 0.523 | 14.72 | 59.6 | 5.5 | 33
KJ090 | 7.5 | 3750 | 85 | 72 | 85 | 113.9 | 0.701 | 19.7 | 79.8 | 5.5 | 33
KJ090 | 7.5 | 3750 | 90 | 72 | 85 | 113.9 | 0.878 | 24.69 | 100 | 5.5 | 33
KJ090 | 7.5 | 3750 | 65 | 57 | 95 | 100.9 | 0.566 | 14.1 | 57.1 | 6.2 | 33
KJ090 | 7.5 | 3750 | 70 | 57 | 95 | 100.9 | 0.766 | 19.09 | 77.3 | 6.2 | 33
KJ090 | 7.5 | 3750 | 75 | 57 | 95 | 100.9 | 0.965 | 24.05 | 97.4 | 6.2 | 33
KJ090 | 7.5 | 3750 | 80 | 57 | 95 | 100.9 | 1 | 24.91 | 100.9 | 6.2 | 33
KJ090 | 7.5 | 3750 | 85 | 57 | 95 | 100.9 | 1 | 24.91 | 100.9 | 6.2 | 33
KJ090 | 7.5 | 3750 | 90 | 57 | 95 | 100.9 | 1 | 24.91 | 100.9 | 6.2 | 33
KJ090 | 7.5 | 3750 | 65 | 62 | 95 | 102.6 | 0.359 | 9.09 | 36.8 | 6.2 | 33
KJ090 | 7.5 | 3750 | 70 | 62 | 95 | 102.6 | 0.556 | 14.07 | 57 | 6.2 | 33
KJ090 | 7.5 | 3750 | 75 | 62 | 95 | 102.6 | 0.752 | 19.06 | 77.2 | 6.2 | 33
KJ090 | 7.5 | 3750 | 80 | 62 | 95 | 102.6 | 0.949 | 24.05 | 97.4 | 6.2 | 33
KJ090 | 7.5 | 3750 | 85 | 62 | 95 | 102.6 | 0.975 | 24.69 | 100 | 6.2 | 33
KJ090 | 7.5 | 3750 | 90 | 62 | 95 | 102.6 | 1 | 25.33 | 102.6 | 6.2 | 33
KJ090 | 7.5 | 3750 | 70 | 67 | 95 | 104.2 | 0.352 | 9.06 | 36.7 | 6.2 | 33
KJ090 | 7.5 | 3750 | 75 | 67 | 95 | 104.2 | 0.546 | 14.05 | 56.9 | 6.2 | 33
KJ090 | 7.5 | 3750 | 80 | 67 | 95 | 104.2 | 0.74 | 19.04 | 77.1 | 6.2 | 33
KJ090 | 7.5 | 3750 | 85 | 67 | 95 | 104.2 | 0.862 | 22.17 | 89.8 | 6.2 | 33
KJ090 | 7.5 | 3750 | 90 | 67 | 95 | 104.2 | 0.985 | 25.33 | 102.6 | 6.2 | 33
KJ090 | 7.5 | 3750 | 75 | 72 | 95 | 105.4 | 0.347 | 9.04 | 36.6 | 6.2 | 33
KJ090 | 7.5 | 3750 | 80 | 72 | 95 | 105.4 | 0.54 | 14.05 | 56.9 | 6.2 | 33
KJ090 | 7.5 | 3750 | 85 | 72 | 95 | 105.4 | 0.731 | 19.04 | 77.1 | 6.2 | 33
KJ090 | 7.5 | 3750 | 90 | 72 | 95 | 105.4 | 0.923 | 24.02 | 97.3 | 6.2 | 33
KJ090 | 7.5 | 3750 | 65 | 57 | 105 | 94.4 | 0.533 | 12.42 | 50.3 | 7.4 | 33
KJ090 | 7.5 | 3750 | 70 | 57 | 105 | 94.4 | 0.754 | 17.58 | 71.2 | 7.4 | 33
KJ090 | 7.5 | 3750 | 75 | 57 | 105 | 94.4 | 0.975 | 22.72 | 92 | 7.4 | 33
KJ090 | 7.5 | 3750 | 80 | 57 | 105 | 94.4 | 1 | 23.31 | 94.4 | 7.4 | 33
KJ090 | 7.5 | 3750 | 85 | 57 | 105 | 94.4 | 1 | 23.31 | 94.4 | 7.4 | 33
KJ090 | 7.5 | 3750 | 90 | 57 | 105 | 94.4 | 1 | 23.31 | 94.4 | 7.4 | 33
KJ090 | 7.5 | 3750 | 65 | 62 | 105 | 95.3 | 0.329 | 7.75 | 31.4 | 7.4 | 33
KJ090 | 7.5 | 3750 | 70 | 62 | 105 | 95.3 | 0.545 | 12.81 | 51.9 | 7.4 | 33
KJ090 | 7.5 | 3750 | 75 | 62 | 105 | 95.3 | 0.759 | 17.85 | 72.3 | 7.4 | 33
KJ090 | 7.5 | 3750 | 80 | 62 | 105 | 95.3 | 0.973 | 22.89 | 92.7 | 7.4 | 33
KJ090 | 7.5 | 3750 | 85 | 62 | 105 | 95.3 | 0.985 | 23.19 | 93.9 | 7.4 | 33
KJ090 | 7.5 | 3750 | 90 | 62 | 105 | 95.3 | 0.998 | 23.48 | 95.1 | 7.4 | 33
KJ090 | 7.5 | 3750 | 70 | 67 | 105 | 96.1 | 0.338 | 8.02 | 32.5 | 7.4 | 33
KJ090 | 7.5 | 3750 | 75 | 67 | 105 | 96.1 | 0.547 | 12.99 | 52.6 | 7.4 | 33
KJ090 | 7.5 | 3750 | 80 | 67 | 105 | 96.1 | 0.755 | 17.93 | 72.6 | 7.4 | 33
KJ090 | 7.5 | 3750 | 85 | 67 | 105 | 96.1 | 0.873 | 20.72 | 83.9 | 7.4 | 33
KJ090 | 7.5 | 3750 | 90 | 67 | 105 | 96.1 | 0.992 | 23.53 | 95.3 | 7.4 | 33
KJ090 | 7.5 | 3750 | 75 | 72 | 105 | 97.8 | 0.335 | 8.1 | 32.8 | 7.4 | 33
KJ090 | 7.5 | 3750 | 80 | 72 | 105 | 97.8 | 0.537 | 12.96 | 52.5 | 7.4 | 33
KJ090 | 7.5 | 3750 | 85 | 72 | 105 | 97.8 | 0.737 | 17.8 | 72.1 | 7.4 | 33
KJ090 | 7.5 | 3750 | 90 | 72 | 105 | 97.8 | 0.938 | 22.64 | 91.7 | 7.4 | 33
KJ090 | 7.5 | 3750 | 65 | 57 | 115 | 87.9 | 0.496 | 10.77 | 43.6 | 8.4 | 34
KJ090 | 7.5 | 3750 | 70 | 57 | 115 | 87.9 | 0.741 | 16.07 | 65.1 | 8.4 | 34
KJ090 | 7.5 | 3750 | 75 | 57 | 115 | 87.9 | 0.985 | 21.38 | 86.6 | 8.4 | 34
KJ090 | 7.5 | 3750 | 80 | 57 | 115 | 87.9 | 0.992 | 21.53 | 87.2 | 8.4 | 34
KJ090 | 7.5 | 3750 | 85 | 57 | 115 | 87.9 | 0.992 | 21.53 | 87.2 | 8.4 | 34
KJ090 | 7.5 | 3750 | 90 | 57 | 115 | 87.9 | 0.992 | 21.53 | 87.2 | 8.4 | 34
KJ090 | 7.5 | 3750 | 65 | 62 | 115 | 88 | 0.297 | 6.44 | 26.1 | 8.4 | 34
KJ090 | 7.5 | 3750 | 70 | 62 | 115 | 88 | 0.532 | 11.56 | 46.8 | 8.4 | 34
KJ090 | 7.5 | 3750 | 75 | 62 | 115 | 88 | 0.766 | 16.64 | 67.4 | 8.4 | 34
KJ090 | 7.5 | 3750 | 80 | 62 | 115 | 88 | 0.995 | 21.63 | 87.6 | 8.4 | 34
KJ090 | 7.5 | 3750 | 85 | 62 | 115 | 88 | 0.995 | 21.63 | 87.6 | 8.4 | 34
KJ090 | 7.5 | 3750 | 90 | 62 | 115 | 88 | 0.995 | 21.63 | 87.6 | 8.4 | 34
KJ090 | 7.5 | 3750 | 70 | 67 | 115 | 88.2 | 0.322 | 7.01 | 28.4 | 8.4 | 34
KJ090 | 7.5 | 3750 | 75 | 67 | 115 | 88.2 | 0.548 | 11.93 | 48.3 | 8.4 | 34
KJ090 | 7.5 | 3750 | 80 | 67 | 115 | 88.2 | 0.772 | 16.81 | 68.1 | 8.4 | 34
KJ090 | 7.5 | 3750 | 85 | 67 | 115 | 88.2 | 0.885 | 19.28 | 78.1 | 8.4 | 34
KJ090 | 7.5 | 3750 | 90 | 67 | 115 | 88.2 | 0.998 | 21.73 | 88 | 8.4 | 34
KJ090 | 7.5 | 3750 | 75 | 72 | 115 | 90.2 | 0.323 | 7.19 | 29.1 | 8.5 | 34
KJ090 | 7.5 | 3750 | 80 | 72 | 115 | 90.2 | 0.533 | 11.88 | 48.1 | 8.5 | 34
KJ090 | 7.5 | 3750 | 85 | 72 | 115 | 90.2 | 0.744 | 16.57 | 67.1 | 8.5 | 34
KJ090 | 7.5 | 3750 | 90 | 72 | 115 | 90.2 | 0.955 | 21.26 | 86.1 | 8.5 | 34
KJ090 | 7.5 | 3750 | 65 | 57 | 125 | 79.8 | 0.461 | 9.09 | 36.8 | 9.5 | 34
KJ090 | 7.5 | 3750 | 70 | 57 | 125 | 79.8 | 0.739 | 14.57 | 59 | 9.5 | 34
KJ090 | 7.5 | 3750 | 75 | 57 | 125 | 79.8 | 0.997 | 19.65 | 79.6 | 9.5 | 34
KJ090 | 7.5 | 3750 | 80 | 57 | 125 | 79.8 | 0.997 | 19.65 | 79.6 | 9.5 | 34
KJ090 | 7.5 | 3750 | 85 | 57 | 125 | 79.8 | 0.997 | 19.65 | 79.6 | 9.5 | 34
KJ090 | 7.5 | 3750 | 90 | 57 | 125 | 79.8 | 0.997 | 19.65 | 79.6 | 9.5 | 34
KJ090 | 7.5 | 3750 | 65 | 62 | 125 | 80.6 | 0.257 | 5.11 | 20.7 | 9.5 | 34
KJ090 | 7.5 | 3750 | 70 | 62 | 125 | 80.6 | 0.516 | 10.27 | 41.6 | 9.5 | 34
KJ090 | 7.5 | 3750 | 75 | 62 | 125 | 80.6 | 0.777 | 15.46 | 62.6 | 9.5 | 34
KJ090 | 7.5 | 3750 | 80 | 62 | 125 | 80.6 | 0.994 | 19.78 | 80.1 | 9.5 | 34
KJ090 | 7.5 | 3750 | 85 | 62 | 125 | 80.6 | 0.994 | 19.78 | 80.1 | 9.5 | 34
KJ090 | 7.5 | 3750 | 90 | 62 | 125 | 80.6 | 0.994 | 19.78 | 80.1 | 9.5 | 34
KJ090 | 7.5 | 3750 | 70 | 67 | 125 | 81.4 | 0.299 | 6 | 24.3 | 9.5 | 34
KJ090 | 7.5 | 3750 | 75 | 67 | 125 | 81.4 | 0.539 | 10.84 | 43.9 | 9.5 | 34
KJ090 | 7.5 | 3750 | 80 | 67 | 125 | 81.4 | 0.781 | 15.7 | 63.6 | 9.5 | 34
KJ090 | 7.5 | 3750 | 85 | 67 | 125 | 81.4 | 0.887 | 17.83 | 72.2 | 9.5 | 34
KJ090 | 7.5 | 3750 | 90 | 67 | 125 | 81.4 | 0.991 | 19.93 | 80.7 | 9.5 | 34
KJ090 | 7.5 | 3750 | 75 | 72 | 125 | 82.6 | 0.306 | 6.25 | 25.3 | 9.5 | 34
KJ090 | 7.5 | 3750 | 80 | 72 | 125 | 82.6 | 0.529 | 10.79 | 43.7 | 9.5 | 34
KJ090 | 7.5 | 3750 | 85 | 72 | 125 | 82.6 | 0.752 | 15.33 | 62.1 | 9.5 | 34
KJ090 | 7.5 | 3750 | 90 | 72 | 125 | 82.6 | 0.975 | 19.88 | 80.5 | 9.5 | 34
KJ102 | 8.5 | 2125 | 65 | 62 | 75 | 93.3 | 0.459 | 18.65 | 42.8 | 5.5 | 35
KJ102 | 8.5 | 2125 | 70 | 62 | 75 | 93.3 | 0.583 | 23.7 | 54.4 | 5.5 | 35
KJ102 | 8.5 | 2125 | 75 | 62 | 75 | 93.3 | 0.673 | 27.36 | 62.8 | 5.5 | 35
KJ102 | 8.5 | 2125 | 80 | 62 | 75 | 93.3 | 0.831 | 33.77 | 77.5 | 5.5 | 35
KJ102 | 8.5 | 2125 | 85 | 62 | 75 | 93.3 | 0.934 | 37.95 | 87.1 | 5.5 | 35
KJ102 | 8.5 | 2125 | 90 | 62 | 75 | 93.3 | 1 | 40.65 | 93.3 | 5.5 | 35
KJ102 | 8.5 | 2125 | 70 | 67 | 75 | 104.4 | 0.414 | 18.82 | 43.2 | 5.4 | 35
KJ102 | 8.5 | 2125 | 75 | 67 | 75 | 104.4 | 0.516 | 23.49 | 53.9 | 5.4 | 35
KJ102 | 8.5 | 2125 | 80 | 67 | 75 | 104.4 | 0.629 | 28.63 | 65.7 | 5.4 | 35
KJ102 | 8.5 | 2125 | 85 | 67 | 75 | 104.4 | 0.74 | 33.68 | 77.3 | 5.4 | 35
KJ102 | 8.5 | 2125 | 90 | 67 | 75 | 104.4 | 0.852 | 38.78 | 89 | 5.4 | 35
KJ102 | 8.5 | 2125 | 75 | 72 | 75 | 118.1 | 0.363 | 18.69 | 42.9 | 5.3 | 35
KJ102 | 8.5 | 2125 | 80 | 72 | 75 | 118.1 | 0.456 | 23.49 | 53.9 | 5.3 | 35
KJ102 | 8.5 | 2125 | 85 | 72 | 75 | 118.1 | 0.549 | 28.24 | 64.8 | 5.3 | 35
KJ102 | 8.5 | 2125 | 90 | 72 | 75 | 118.1 | 0.641 | 32.98 | 75.7 | 5.3 | 35
KJ102 | 8.5 | 2125 | 80 | 77 | 75 | 131.7 | 0.319 | 18.3 | 42 | 5.2 | 35
KJ102 | 8.5 | 2125 | 85 | 77 | 75 | 131.7 | 0.396 | 22.75 | 52.2 | 5.2 | 35
KJ102 | 8.5 | 2125 | 90 | 77 | 75 | 131.7 | 0.474 | 27.19 | 62.4 | 5.2 | 35
KJ102 | 8.5 | 2125 | 65 | 62 | 85 | 91.3 | 0.439 | 17.47 | 40.1 | 6.2 | 35
KJ102 | 8.5 | 2125 | 70 | 62 | 85 | 91.3 | 0.563 | 22.4 | 51.4 | 6.2 | 35
KJ102 | 8.5 | 2125 | 75 | 62 | 85 | 91.3 | 0.67 | 26.67 | 61.2 | 6.2 | 35
KJ102 | 8.5 | 2125 | 80 | 62 | 85 | 91.3 | 0.812 | 32.29 | 74.1 | 6.2 | 35
KJ102 | 8.5 | 2125 | 85 | 62 | 85 | 91.3 | 0.924 | 36.78 | 84.4 | 6.2 | 35
KJ102 | 8.5 | 2125 | 90 | 62 | 85 | 91.3 | 1 | 39.78 | 91.3 | 6.2 | 35
KJ102 | 8.5 | 2125 | 70 | 67 | 85 | 99.7 | 0.406 | 17.65 | 40.5 | 6.2 | 35
KJ102 | 8.5 | 2125 | 75 | 67 | 85 | 99.7 | 0.516 | 22.4 | 51.4 | 6.2 | 35
KJ102 | 8.5 | 2125 | 80 | 67 | 85 | 99.7 | 0.63 | 27.36 | 62.8 | 6.2 | 35
KJ102 | 8.5 | 2125 | 85 | 67 | 85 | 99.7 | 0.751 | 32.64 | 74.9 | 6.2 | 35
KJ102 | 8.5 | 2125 | 90 | 67 | 85 | 99.7 | 0.874 | 37.95 | 87.1 | 6.2 | 35
KJ102 | 8.5 | 2125 | 75 | 72 | 85 | 111.5 | 0.364 | 17.69 | 40.6 | 6.1 | 35
KJ102 | 8.5 | 2125 | 80 | 72 | 85 | 111.5 | 0.462 | 22.44 | 51.5 | 6.1 | 35
KJ102 | 8.5 | 2125 | 85 | 72 | 85 | 111.5 | 0.56 | 27.19 | 62.4 | 6.1 | 35
KJ102 | 8.5 | 2125 | 90 | 72 | 85 | 111.5 | 0.657 | 31.94 | 73.3 | 6.1 | 35
KJ102 | 8.5 | 2125 | 80 | 77 | 85 | 123.4 | 0.326 | 17.52 | 40.2 | 6.1 | 35
KJ102 | 8.5 | 2125 | 85 | 77 | 85 | 123.4 | 0.404 | 21.74 | 49.9 | 6.1 | 35
KJ102 | 8.5 | 2125 | 90 | 77 | 85 | 123.4 | 0.483 | 25.97 | 59.6 | 6.1 | 35
KJ102 | 8.5 | 2125 | 65 | 62 | 95 | 89.3 | 0.418 | 16.25 | 37.3 | 7 | 35
KJ102 | 8.5 | 2125 | 70 | 62 | 95 | 89.3 | 0.542 | 21.09 | 48.4 | 7 | 35
KJ102 | 8.5 | 2125 | 75 | 62 | 95 | 89.3 | 0.667 | 25.97 | 59.6 | 7 | 35
KJ102 | 8.5 | 2125 | 80 | 62 | 95 | 89.3 | 0.792 | 30.81 | 70.7 | 7 | 35
KJ102 | 8.5 | 2125 | 85 | 62 | 95 | 89.3 | 0.915 | 35.6 | 81.7 | 7 | 35
KJ102 | 8.5 | 2125 | 90 | 62 | 95 | 89.3 | 1 | 38.91 | 89.3 | 7 | 35
KJ102 | 8.5 | 2125 | 70 | 67 | 95 | 94.9 | 0.399 | 16.51 | 37.9 | 7 | 35
KJ102 | 8.5 | 2125 | 75 | 67 | 95 | 94.9 | 0.515 | 21.31 | 48.9 | 7 | 35
KJ102 | 8.5 | 2125 | 80 | 67 | 95 | 94.9 | 0.631 | 26.1 | 59.9 | 7 | 35
KJ102 | 8.5 | 2125 | 85 | 67 | 95 | 94.9 | 0.764 | 31.59 | 72.5 | 7 | 35
KJ102 | 8.5 | 2125 | 90 | 67 | 95 | 94.9 | 0.898 | 37.12 | 85.2 | 7 | 35
KJ102 | 8.5 | 2125 | 75 | 72 | 95 | 105 | 0.364 | 16.64 | 38.2 | 7 | 35
KJ102 | 8.5 | 2125 | 80 | 72 | 95 | 105 | 0.468 | 21.39 | 49.1 | 7 | 35
KJ102 | 8.5 | 2125 | 85 | 72 | 95 | 105 | 0.571 | 26.14 | 60 | 7 | 35
KJ102 | 8.5 | 2125 | 90 | 72 | 95 | 105 | 0.675 | 30.89 | 70.9 | 7 | 35
KJ102 | 8.5 | 2125 | 80 | 77 | 95 | 115.1 | 0.333 | 16.69 | 38.3 | 6.9 | 35
KJ102 | 8.5 | 2125 | 85 | 77 | 95 | 115.1 | 0.413 | 20.7 | 47.5 | 6.9 | 35
KJ102 | 8.5 | 2125 | 90 | 77 | 95 | 115.1 | 0.493 | 24.71 | 56.7 | 6.9 | 35
KJ102 | 8.5 | 2125 | 65 | 62 | 105 | 85.5 | 0.405 | 15.08 | 34.6 | 7.9 | 35
KJ102 | 8.5 | 2125 | 70 | 62 | 105 | 85.5 | 0.532 | 19.83 | 45.5 | 7.9 | 35
KJ102 | 8.5 | 2125 | 75 | 62 | 105 | 85.5 | 0.66 | 24.58 | 56.4 | 7.9 | 35
KJ102 | 8.5 | 2125 | 80 | 62 | 105 | 85.5 | 0.788 | 29.37 | 67.4 | 7.9 | 35
KJ102 | 8.5 | 2125 | 85 | 62 | 105 | 85.5 | 0.906 | 33.77 | 77.5 | 7.9 | 35
KJ102 | 8.5 | 2125 | 90 | 62 | 105 | 85.5 | 1 | 37.25 | 85.5 | 7.9 | 35
KJ102 | 8.5 | 2125 | 70 | 67 | 105 | 89.3 | 0.393 | 15.29 | 35.1 | 7.9 | 35
KJ102 | 8.5 | 2125 | 75 | 67 | 105 | 89.3 | 0.515 | 20.04 | 46 | 7.9 | 35
KJ102 | 8.5 | 2125 | 80 | 67 | 105 | 89.3 | 0.638 | 24.84 | 57 | 7.9 | 35
KJ102 | 8.5 | 2125 | 85 | 67 | 105 | 89.3 | 0.782 | 30.41 | 69.8 | 7.9 | 35
KJ102 | 8.5 | 2125 | 90 | 67 | 105 | 89.3 | 0.926 | 36.03 | 82.7 | 7.9 | 35
KJ102 | 8.5 | 2125 | 75 | 72 | 105 | 98.7 | 0.361 | 15.51 | 35.6 | 7.9 | 35
KJ102 | 8.5 | 2125 | 80 | 72 | 105 | 98.7 | 0.472 | 20.31 | 46.6 | 7.9 | 35
KJ102 | 8.5 | 2125 | 85 | 72 | 105 | 98.7 | 0.583 | 25.05 | 57.5 | 7.9 | 35
KJ102 | 8.5 | 2125 | 90 | 72 | 105 | 98.7 | 0.693 | 29.8 | 68.4 | 7.9 | 35
KJ102 | 8.5 | 2125 | 80 | 77 | 105 | 108 | 0.335 | 15.77 | 36.2 | 7.9 | 35
KJ102 | 8.5 | 2125 | 85 | 77 | 105 | 108 | 0.418 | 19.65 | 45.1 | 7.9 | 35
KJ102 | 8.5 | 2125 | 90 | 77 | 105 | 108 | 0.501 | 23.57 | 54.1 | 7.9 | 35
KJ102 | 8.5 | 2125 | 65 | 62 | 115 | 81.8 | 0.389 | 13.86 | 31.8 | 8.8 | 36
KJ102 | 8.5 | 2125 | 70 | 62 | 115 | 81.8 | 0.52 | 18.52 | 42.5 | 8.8 | 36
KJ102 | 8.5 | 2125 | 75 | 62 | 115 | 81.8 | 0.652 | 23.22 | 53.3 | 8.8 | 36
KJ102 | 8.5 | 2125 | 80 | 62 | 115 | 81.8 | 0.784 | 27.93 | 64.1 | 8.8 | 36
KJ102 | 8.5 | 2125 | 85 | 62 | 115 | 81.8 | 0.897 | 31.98 | 73.4 | 8.8 | 36
KJ102 | 8.5 | 2125 | 90 | 62 | 115 | 81.8 | 1 | 35.64 | 81.8 | 8.8 | 36
KJ102 | 8.5 | 2125 | 70 | 67 | 115 | 83.7 | 0.387 | 14.12 | 32.4 | 8.7 | 36
KJ102 | 8.5 | 2125 | 75 | 67 | 115 | 83.7 | 0.516 | 18.82 | 43.2 | 8.7 | 36
KJ102 | 8.5 | 2125 | 80 | 67 | 115 | 83.7 | 0.645 | 23.53 | 54 | 8.7 | 36
KJ102 | 8.5 | 2125 | 85 | 67 | 115 | 83.7 | 0.802 | 29.24 | 67.1 | 8.7 | 36
KJ102 | 8.5 | 2125 | 90 | 67 | 115 | 83.7 | 0.958 | 34.95 | 80.2 | 8.7 | 36
KJ102 | 8.5 | 2125 | 75 | 72 | 115 | 92.3 | 0.359 | 14.42 | 33.1 | 8.8 | 36
KJ102 | 8.5 | 2125 | 80 | 72 | 115 | 92.3 | 0.477 | 19.17 | 44 | 8.8 | 36
KJ102 | 8.5 | 2125 | 85 | 72 | 115 | 92.3 | 0.595 | 23.92 | 54.9 | 8.8 | 36
KJ102 | 8.5 | 2125 | 90 | 72 | 115 | 92.3 | 0.713 | 28.67 | 65.8 | 8.8 | 36
KJ102 | 8.5 | 2125 | 80 | 77 | 115 | 100.9 | 0.337 | 14.81 | 34 | 8.9 | 36
KJ102 | 8.5 | 2125 | 85 | 77 | 115 | 100.9 | 0.423 | 18.61 | 42.7 | 8.9 | 36
KJ102 | 8.5 | 2125 | 90 | 77 | 115 | 100.9 | 0.51 | 22.44 | 51.5 | 8.9 | 36
KJ102 | 8.5 | 2125 | 65 | 62 | 125 | 78.1 | 0.371 | 12.64 | 29 | 9.7 | 36
KJ102 | 8.5 | 2125 | 70 | 62 | 125 | 78.1 | 0.507 | 17.25 | 39.6 | 9.7 | 36
KJ102 | 8.5 | 2125 | 75 | 62 | 125 | 78.1 | 0.643 | 21.87 | 50.2 | 9.7 | 36
KJ102 | 8.5 | 2125 | 80 | 62 | 125 | 78.1 | 0.778 | 26.49 | 60.8 | 9.7 | 36
KJ102 | 8.5 | 2125 | 85 | 62 | 125 | 78.1 | 0.887 | 30.2 | 69.3 | 9.7 | 36
KJ102 | 8.5 | 2125 | 90 | 62 | 125 | 78.1 | 0.997 | 33.94 | 77.9 | 9.7 | 36
KJ102 | 8.5 | 2125 | 70 | 67 | 125 | 78.1 | 0.379 | 12.9 | 29.6 | 9.6 | 36
KJ102 | 8.5 | 2125 | 75 | 67 | 125 | 78.1 | 0.517 | 17.6 | 40.4 | 9.6 | 36
KJ102 | 8.5 | 2125 | 80 | 67 | 125 | 78.1 | 0.654 | 22.27 | 51.1 | 9.6 | 36
KJ102 | 8.5 | 2125 | 85 | 67 | 125 | 78.1 | 0.825 | 28.06 | 64.4 | 9.6 | 36
KJ102 | 8.5 | 2125 | 90 | 67 | 125 | 78.1 | 0.995 | 33.86 | 77.7 | 9.6 | 36
KJ102 | 8.5 | 2125 | 75 | 72 | 125 | 86 | 0.356 | 13.33 | 30.6 | 9.7 | 36
KJ102 | 8.5 | 2125 | 80 | 72 | 125 | 86 | 0.483 | 18.08 | 41.5 | 9.7 | 36
KJ102 | 8.5 | 2125 | 85 | 72 | 125 | 86 | 0.609 | 22.83 | 52.4 | 9.7 | 36
KJ102 | 8.5 | 2125 | 90 | 72 | 125 | 86 | 0.736 | 27.58 | 63.3 | 9.7 | 36
KJ102 | 8.5 | 2125 | 80 | 77 | 125 | 93.9 | 0.339 | 13.86 | 31.8 | 9.8 | 36
KJ102 | 8.5 | 2125 | 85 | 77 | 125 | 93.9 | 0.429 | 17.56 | 40.3 | 9.8 | 36
KJ102 | 8.5 | 2125 | 90 | 77 | 125 | 93.9 | 0.52 | 21.26 | 48.8 | 9.8 | 36
KJ102 | 8.5 | 2550 | 65 | 57 | 75 | 90.1 | 0.634 | 20.73 | 57.1 | 5.6 | 35
KJ102 | 8.5 | 2550 | 70 | 57 | 75 | 90.1 | 0.789 | 25.82 | 71.1 | 5.6 | 35
KJ102 | 8.5 | 2550 | 75 | 57 | 75 | 90.1 | 0.945 | 30.9 | 85.1 | 5.6 | 35
KJ102 | 8.5 | 2550 | 80 | 57 | 75 | 90.1 | 1 | 32.72 | 90.1 | 5.6 | 35
KJ102 | 8.5 | 2550 | 85 | 57 | 75 | 90.1 | 1 | 32.72 | 90.1 | 5.6 | 35
KJ102 | 8.5 | 2550 | 90 | 57 | 75 | 90.1 | 1 | 32.72 | 90.1 | 5.6 | 35
KJ102 | 8.5 | 2550 | 65 | 62 | 75 | 99.3 | 0.441 | 15.9 | 43.8 | 5.5 | 35
KJ102 | 8.5 | 2550 | 70 | 62 | 75 | 99.3 | 0.579 | 20.88 | 57.5 | 5.5 | 35
KJ102 | 8.5 | 2550 | 75 | 62 | 75 | 99.3 | 0.693 | 24.98 | 68.8 | 5.5 | 35
KJ102 | 8.5 | 2550 | 80 | 62 | 75 | 99.3 | 0.856 | 30.86 | 85 | 5.5 | 35
KJ102 | 8.5 | 2550 | 85 | 62 | 75 | 99.3 | 0.945 | 34.06 | 93.8 | 5.5 | 35
KJ102 | 8.5 | 2550 | 90 | 62 | 75 | 99.3 | 1 | 36.06 | 99.3 | 5.5 | 35
KJ102 | 8.5 | 2550 | 70 | 67 | 75 | 108.4 | 0.406 | 15.98 | 44 | 5.4 | 35
KJ102 | 8.5 | 2550 | 75 | 67 | 75 | 108.4 | 0.527 | 20.73 | 57.1 | 5.4 | 35
KJ102 | 8.5 | 2550 | 80 | 67 | 75 | 108.4 | 0.655 | 25.78 | 71 | 5.4 | 35
KJ102 | 8.5 | 2550 | 85 | 67 | 75 | 108.4 | 0.772 | 30.39 | 83.7 | 5.4 | 35
KJ102 | 8.5 | 2550 | 90 | 67 | 75 | 108.4 | 0.888 | 34.97 | 96.3 | 5.4 | 35
KJ102 | 8.5 | 2550 | 75 | 72 | 75 | 120.6 | 0.362 | 15.87 | 43.7 | 5.3 | 35
KJ102 | 8.5 | 2550 | 80 | 72 | 75 | 120.6 | 0.473 | 20.7 | 57 | 5.3 | 35
KJ102 | 8.5 | 2550 | 85 | 72 | 75 | 120.6 | 0.583 | 25.53 | 70.3 | 5.3 | 35
KJ102 | 8.5 | 2550 | 90 | 72 | 75 | 120.6 | 0.693 | 30.36 | 83.6 | 5.3 | 35
KJ102 | 8.5 | 2550 | 80 | 77 | 75 | 132.8 | 0.324 | 15.61 | 43 | 5.2 | 35
KJ102 | 8.5 | 2550 | 85 | 77 | 75 | 132.8 | 0.428 | 20.66 | 56.9 | 5.2 | 35
KJ102 | 8.5 | 2550 | 90 | 77 | 75 | 132.8 | 0.533 | 25.71 | 70.8 | 5.2 | 35
KJ102 | 8.5 | 2550 | 65 | 57 | 85 | 89.3 | 0.602 | 19.54 | 53.8 | 6.3 | 35
KJ102 | 8.5 | 2550 | 70 | 57 | 85 | 89.3 | 0.758 | 24.58 | 67.7 | 6.3 | 35
KJ102 | 8.5 | 2550 | 75 | 57 | 85 | 89.3 | 0.913 | 29.59 | 81.5 | 6.3 | 35
KJ102 | 8.5 | 2550 | 80 | 57 | 85 | 89.3 | 1 | 32.43 | 89.3 | 6.3 | 35
KJ102 | 8.5 | 2550 | 85 | 57 | 85 | 89.3 | 1 | 32.43 | 89.3 | 6.3 | 35
KJ102 | 8.5 | 2550 | 90 | 57 | 85 | 89.3 | 1 | 32.43 | 89.3 | 6.3 | 35
KJ102 | 8.5 | 2550 | 65 | 62 | 85 | 96.2 | 0.424 | 14.81 | 40.8 | 6.2 | 35
KJ102 | 8.5 | 2550 | 70 | 62 | 85 | 96.2 | 0.567 | 19.79 | 54.5 | 6.2 | 35
KJ102 | 8.5 | 2550 | 75 | 62 | 85 | 96.2 | 0.695 | 24.29 | 66.9 | 6.2 | 35
KJ102 | 8.5 | 2550 | 80 | 62 | 85 | 96.2 | 0.849 | 29.67 | 81.7 | 6.2 | 35
KJ102 | 8.5 | 2550 | 85 | 62 | 85 | 96.2 | 0.944 | 32.97 | 90.8 | 6.2 | 35
KJ102 | 8.5 | 2550 | 90 | 62 | 85 | 96.2 | 1 | 34.93 | 96.2 | 6.2 | 35
KJ102 | 8.5 | 2550 | 70 | 67 | 85 | 103.1 | 0.401 | 15 | 41.3 | 6.2 | 35
KJ102 | 8.5 | 2550 | 75 | 67 | 85 | 103.1 | 0.529 | 19.79 | 54.5 | 6.2 | 35
KJ102 | 8.5 | 2550 | 80 | 67 | 85 | 103.1 | 0.661 | 24.73 | 68.1 | 6.2 | 35
KJ102 | 8.5 | 2550 | 85 | 67 | 85 | 103.1 | 0.785 | 29.38 | 80.9 | 6.2 | 35
KJ102 | 8.5 | 2550 | 90 | 67 | 85 | 103.1 | 0.909 | 34.02 | 93.7 | 6.2 | 35
KJ102 | 8.5 | 2550 | 75 | 72 | 85 | 113.7 | 0.363 | 15 | 41.3 | 6.1 | 35
KJ102 | 8.5 | 2550 | 80 | 72 | 85 | 113.7 | 0.479 | 19.79 | 54.5 | 6.1 | 35
KJ102 | 8.5 | 2550 | 85 | 72 | 85 | 113.7 | 0.595 | 24.55 | 67.6 | 6.1 | 35
KJ102 | 8.5 | 2550 | 90 | 72 | 85 | 113.7 | 0.711 | 29.34 | 80.8 | 6.1 | 35
KJ102 | 8.5 | 2550 | 80 | 77 | 85 | 124.3 | 0.328 | 14.81 | 40.8 | 6.1 | 35
KJ102 | 8.5 | 2550 | 85 | 77 | 85 | 124.3 | 0.438 | 19.75 | 54.4 | 6.1 | 35
KJ102 | 8.5 | 2550 | 90 | 77 | 85 | 124.3 | 0.547 | 24.69 | 68 | 6.1 | 35
KJ102 | 8.5 | 2550 | 65 | 57 | 95 | 88.5 | 0.571 | 18.34 | 50.5 | 6.9 | 35
KJ102 | 8.5 | 2550 | 70 | 57 | 95 | 88.5 | 0.725 | 23.31 | 64.2 | 6.9 | 35
KJ102 | 8.5 | 2550 | 75 | 57 | 95 | 88.5 | 0.881 | 28.32 | 78 | 6.9 | 35
KJ102 | 8.5 | 2550 | 80 | 57 | 95 | 88.5 | 1 | 32.14 | 88.5 | 6.9 | 35
KJ102 | 8.5 | 2550 | 85 | 57 | 95 | 88.5 | 1 | 32.14 | 88.5 | 6.9 | 35
KJ102 | 8.5 | 2550 | 90 | 57 | 95 | 88.5 | 1 | 32.14 | 88.5 | 6.9 | 35
KJ102 | 8.5 | 2550 | 65 | 62 | 95 | 93.2 | 0.407 | 13.76 | 37.9 | 7 | 35
KJ102 | 8.5 | 2550 | 70 | 62 | 95 | 93.2 | 0.552 | 18.66 | 51.4 | 7 | 35
KJ102 | 8.5 | 2550 | 75 | 62 | 95 | 93.2 | 0.696 | 23.57 | 64.9 | 7 | 35
KJ102 | 8.5 | 2550 | 80 | 62 | 95 | 93.2 | 0.842 | 28.5 | 78.5 | 7 | 35
KJ102 | 8.5 | 2550 | 85 | 62 | 95 | 93.2 | 0.941 | 31.84 | 87.7 | 7 | 35
KJ102 | 8.5 | 2550 | 90 | 62 | 95 | 93.2 | 1 | 33.84 | 93.2 | 7 | 35
KJ102 | 8.5 | 2550 | 70 | 67 | 95 | 97.9 | 0.393 | 13.98 | 38.5 | 7 | 35
KJ102 | 8.5 | 2550 | 75 | 67 | 95 | 97.9 | 0.53 | 18.85 | 51.9 | 7 | 35
KJ102 | 8.5 | 2550 | 80 | 67 | 95 | 97.9 | 0.666 | 23.67 | 65.2 | 7 | 35
KJ102 | 8.5 | 2550 | 85 | 67 | 95 | 97.9 | 0.798 | 28.36 | 78.1 | 7 | 35
KJ102 | 8.5 | 2550 | 90 | 67 | 95 | 97.9 | 0.93 | 33.04 | 91 | 7 | 35
KJ102 | 8.5 | 2550 | 75 | 72 | 95 | 106.9 | 0.363 | 14.09 | 38.8 | 7 | 35
KJ102 | 8.5 | 2550 | 80 | 72 | 95 | 106.9 | 0.486 | 18.85 | 51.9 | 7 | 35
KJ102 | 8.5 | 2550 | 85 | 72 | 95 | 106.9 | 0.608 | 23.6 | 65 | 7 | 35
KJ102 | 8.5 | 2550 | 90 | 72 | 95 | 106.9 | 0.731 | 28.36 | 78.1 | 7 | 35
KJ102 | 8.5 | 2550 | 80 | 77 | 95 | 115.8 | 0.333 | 14.02 | 38.6 | 7 | 35
KJ102 | 8.5 | 2550 | 85 | 77 | 95 | 115.8 | 0.448 | 18.85 | 51.9 | 7 | 35
KJ102 | 8.5 | 2550 | 90 | 77 | 95 | 115.8 | 0.563 | 23.67 | 65.2 | 7 | 35
KJ102 | 8.5 | 2550 | 65 | 57 | 105 | 86.1 | 0.554 | 17.32 | 47.7 | 7.8 | 35
KJ102 | 8.5 | 2550 | 70 | 57 | 105 | 86.1 | 0.711 | 22.22 | 61.2 | 7.8 | 35
KJ102 | 8.5 | 2550 | 75 | 57 | 105 | 86.1 | 0.869 | 27.16 | 74.8 | 7.8 | 35
KJ102 | 8.5 | 2550 | 80 | 57 | 105 | 86.1 | 1 | 31.26 | 86.1 | 7.8 | 35
KJ102 | 8.5 | 2550 | 85 | 57 | 105 | 86.1 | 1 | 31.26 | 86.1 | 7.8 | 35
KJ102 | 8.5 | 2550 | 90 | 57 | 105 | 86.1 | 1 | 31.26 | 86.1 | 7.8 | 35
KJ102 | 8.5 | 2550 | 65 | 62 | 105 | 89.2 | 0.392 | 12.71 | 35 | 7.9 | 35
KJ102 | 8.5 | 2550 | 70 | 62 | 105 | 89.2 | 0.543 | 17.57 | 48.4 | 7.9 | 35
KJ102 | 8.5 | 2550 | 75 | 62 | 105 | 89.2 | 0.693 | 22.44 | 61.8 | 7.9 | 35
KJ102 | 8.5 | 2550 | 80 | 62 | 105 | 89.2 | 0.843 | 27.31 | 75.2 | 7.9 | 35
KJ102 | 8.5 | 2550 | 85 | 62 | 105 | 89.2 | 0.936 | 30.32 | 83.5 | 7.9 | 35
KJ102 | 8.5 | 2550 | 90 | 62 | 105 | 89.2 | 1 | 32.39 | 89.2 | 7.9 | 35
KJ102 | 8.5 | 2550 | 70 | 67 | 105 | 92.3 | 0.385 | 12.89 | 35.5 | 7.9 | 35
KJ102 | 8.5 | 2550 | 75 | 67 | 105 | 92.3 | 0.529 | 17.72 | 48.8 | 7.9 | 35
KJ102 | 8.5 | 2550 | 80 | 67 | 105 | 92.3 | 0.673 | 22.55 | 62.1 | 7.9 | 35
KJ102 | 8.5 | 2550 | 85 | 67 | 105 | 92.3 | 0.811 | 27.2 | 74.9 | 7.9 | 35
KJ102 | 8.5 | 2550 | 90 | 67 | 105 | 92.3 | 0.95 | 31.84 | 87.7 | 7.9 | 35
KJ102 | 8.5 | 2550 | 75 | 72 | 105 | 100.4 | 0.357 | 13 | 35.8 | 7.9 | 35
KJ102 | 8.5 | 2550 | 80 | 72 | 105 | 100.4 | 0.488 | 17.79 | 49 | 7.9 | 35
KJ102 | 8.5 | 2550 | 85 | 72 | 105 | 100.4 | 0.619 | 22.55 | 62.1 | 7.9 | 35
KJ102 | 8.5 | 2550 | 90 | 72 | 105 | 100.4 | 0.75 | 27.34 | 75.3 | 7.9 | 35
KJ102 | 8.5 | 2550 | 80 | 77 | 105 | 108.5 | 0.331 | 13.04 | 35.9 | 7.9 | 35
KJ102 | 8.5 | 2550 | 85 | 77 | 105 | 108.5 | 0.454 | 17.9 | 49.3 | 7.9 | 35
KJ102 | 8.5 | 2550 | 90 | 77 | 105 | 108.5 | 0.579 | 22.8 | 62.8 | 7.9 | 35
KJ102 | 8.5 | 2550 | 65 | 57 | 115 | 83.6 | 0.537 | 16.3 | 44.9 | 8.8 | 36
KJ102 | 8.5 | 2550 | 70 | 57 | 115 | 83.6 | 0.696 | 21.13 | 58.2 | 8.8 | 36
KJ102 | 8.5 | 2550 | 75 | 57 | 115 | 83.6 | 0.856 | 26 | 71.6 | 8.8 | 36
KJ102 | 8.5 | 2550 | 80 | 57 | 115 | 83.6 | 1 | 30.36 | 83.6 | 8.8 | 36
KJ102 | 8.5 | 2550 | 85 | 57 | 115 | 83.6 | 1 | 30.36 | 83.6 | 8.8 | 36
KJ102 | 8.5 | 2550 | 90 | 57 | 115 | 83.6 | 1 | 30.36 | 83.6 | 8.8 | 36
KJ102 | 8.5 | 2550 | 65 | 62 | 115 | 85.2 | 0.377 | 11.66 | 32.1 | 8.8 | 36
KJ102 | 8.5 | 2550 | 70 | 62 | 115 | 85.2 | 0.533 | 16.49 | 45.4 | 8.8 | 36
KJ102 | 8.5 | 2550 | 75 | 62 | 115 | 85.2 | 0.689 | 21.31 | 58.7 | 8.8 | 36
KJ102 | 8.5 | 2550 | 80 | 62 | 115 | 85.2 | 0.845 | 26.14 | 72 | 8.8 | 36
KJ102 | 8.5 | 2550 | 85 | 62 | 115 | 85.2 | 0.93 | 28.76 | 79.2 | 8.8 | 36
KJ102 | 8.5 | 2550 | 90 | 62 | 115 | 85.2 | 1 | 30.94 | 85.2 | 8.8 | 36
KJ102 | 8.5 | 2550 | 70 | 67 | 115 | 86.7 | 0.375 | 11.8 | 32.5 | 8.8 | 36
KJ102 | 8.5 | 2550 | 75 | 67 | 115 | 86.7 | 0.528 | 16.63 | 45.8 | 8.8 | 36
KJ102 | 8.5 | 2550 | 80 | 67 | 115 | 86.7 | 0.681 | 21.42 | 59 | 8.8 | 36
KJ102 | 8.5 | 2550 | 85 | 67 | 115 | 86.7 | 0.827 | 26.03 | 71.7 | 8.8 | 36
KJ102 | 8.5 | 2550 | 90 | 67 | 115 | 86.7 | 0.973 | 30.65 | 84.4 | 8.8 | 36
KJ102 | 8.5 | 2550 | 75 | 72 | 115 | 93.9 | 0.35 | 11.95 | 32.9 | 8.8 | 36
KJ102 | 8.5 | 2550 | 80 | 72 | 115 | 93.9 | 0.49 | 16.7 | 46 | 8.8 | 36
KJ102 | 8.5 | 2550 | 85 | 72 | 115 | 93.9 | 0.63 | 21.5 | 59.2 | 8.8 | 36
KJ102 | 8.5 | 2550 | 90 | 72 | 115 | 93.9 | 0.771 | 26.29 | 72.4 | 8.8 | 36
KJ102 | 8.5 | 2550 | 80 | 77 | 115 | 101.1 | 0.327 | 12.02 | 33.1 | 8.9 | 36
KJ102 | 8.5 | 2550 | 85 | 77 | 115 | 101.1 | 0.463 | 16.99 | 46.8 | 8.9 | 36
KJ102 | 8.5 | 2550 | 90 | 77 | 115 | 101.1 | 0.597 | 21.93 | 60.4 | 8.9 | 36
KJ102 | 8.5 | 2550 | 65 | 57 | 125 | 81.2 | 0.517 | 15.25 | 42 | 9.7 | 36
KJ102 | 8.5 | 2550 | 70 | 57 | 125 | 81.2 | 0.68 | 20.04 | 55.2 | 9.7 | 36
KJ102 | 8.5 | 2550 | 75 | 57 | 125 | 81.2 | 0.842 | 24.84 | 68.4 | 9.7 | 36
KJ102 | 8.5 | 2550 | 80 | 57 | 125 | 81.2 | 1 | 29.48 | 81.2 | 9.7 | 36
KJ102 | 8.5 | 2550 | 85 | 57 | 125 | 81.2 | 1 | 29.48 | 81.2 | 9.7 | 36
KJ102 | 8.5 | 2550 | 90 | 57 | 125 | 81.2 | 1 | 29.48 | 81.2 | 9.7 | 36
KJ102 | 8.5 | 2550 | 65 | 62 | 125 | 81.1 | 0.36 | 10.6 | 29.2 | 9.7 | 36
KJ102 | 8.5 | 2550 | 70 | 62 | 125 | 81.1 | 0.523 | 15.4 | 42.4 | 9.7 | 36
KJ102 | 8.5 | 2550 | 75 | 62 | 125 | 81.1 | 0.684 | 20.15 | 55.5 | 9.7 | 36
KJ102 | 8.5 | 2550 | 80 | 62 | 125 | 81.1 | 0.847 | 24.95 | 68.7 | 9.7 | 36
KJ102 | 8.5 | 2550 | 85 | 62 | 125 | 81.1 | 0.925 | 27.23 | 75 | 9.7 | 36
KJ102 | 8.5 | 2550 | 90 | 62 | 125 | 81.1 | 1 | 29.45 | 81.1 | 9.7 | 36
KJ102 | 8.5 | 2550 | 70 | 67 | 125 | 81.1 | 0.364 | 10.71 | 29.5 | 9.7 | 36
KJ102 | 8.5 | 2550 | 75 | 67 | 125 | 81.1 | 0.527 | 15.5 | 42.7 | 9.7 | 36
KJ102 | 8.5 | 2550 | 80 | 67 | 125 | 81.1 | 0.689 | 20.3 | 55.9 | 9.7 | 36
KJ102 | 8.5 | 2550 | 85 | 67 | 125 | 81.1 | 0.845 | 24.87 | 68.5 | 9.7 | 36
KJ102 | 8.5 | 2550 | 90 | 67 | 125 | 81.1 | 1 | 29.45 | 81.1 | 9.7 | 36
KJ102 | 8.5 | 2550 | 75 | 72 | 125 | 87.4 | 0.342 | 10.86 | 29.9 | 9.7 | 36
KJ102 | 8.5 | 2550 | 80 | 72 | 125 | 87.4 | 0.493 | 15.65 | 43.1 | 9.7 | 36
KJ102 | 8.5 | 2550 | 85 | 72 | 125 | 87.4 | 0.644 | 20.44 | 56.3 | 9.7 | 36
KJ102 | 8.5 | 2550 | 90 | 72 | 125 | 87.4 | 0.796 | 25.27 | 69.6 | 9.7 | 36
KJ102 | 8.5 | 2550 | 80 | 77 | 125 | 93.7 | 0.323 | 11 | 30.3 | 9.8 | 36
KJ102 | 8.5 | 2550 | 85 | 77 | 125 | 93.7 | 0.472 | 16.05 | 44.2 | 9.8 | 36
KJ102 | 8.5 | 2550 | 90 | 77 | 125 | 93.7 | 0.619 | 21.06 | 58 | 9.8 | 36
KJ102 | 8.5 | 2975 | 65 | 57 | 75 | 98.1 | 0.617 | 18.83 | 60.5 | 5.5 | 35
KJ102 | 8.5 | 2975 | 70 | 57 | 75 | 98.1 | 0.781 | 23.84 | 76.6 | 5.5 | 35
KJ102 | 8.5 | 2975 | 75 | 57 | 75 | 98.1 | 0.945 | 28.85 | 92.7 | 5.5 | 35
KJ102 | 8.5 | 2975 | 80 | 57 | 75 | 98.1 | 1 | 30.53 | 98.1 | 5.5 | 35
KJ102 | 8.5 | 2975 | 85 | 57 | 75 | 98.1 | 1 | 30.53 | 98.1 | 5.5 | 35
KJ102 | 8.5 | 2975 | 90 | 57 | 75 | 98.1 | 1 | 30.53 | 98.1 | 5.5 | 35
KJ102 | 8.5 | 2975 | 65 | 62 | 75 | 105.2 | 0.426 | 13.94 | 44.8 | 5.4 | 35
KJ102 | 8.5 | 2975 | 70 | 62 | 75 | 105.2 | 0.577 | 18.89 | 60.7 | 5.4 | 35
KJ102 | 8.5 | 2975 | 75 | 62 | 75 | 105.2 | 0.711 | 23.28 | 74.8 | 5.4 | 35
KJ102 | 8.5 | 2975 | 80 | 62 | 75 | 105.2 | 0.88 | 28.82 | 92.6 | 5.4 | 35
KJ102 | 8.5 | 2975 | 85 | 62 | 75 | 105.2 | 0.956 | 31.31 | 100.6 | 5.4 | 35
KJ102 | 8.5 | 2975 | 90 | 62 | 75 | 105.2 | 1 | 32.74 | 105.2 | 5.4 | 35
KJ102 | 8.5 | 2975 | 70 | 67 | 75 | 112.3 | 0.399 | 13.94 | 44.8 | 5.4 | 35
KJ102 | 8.5 | 2975 | 75 | 67 | 75 | 112.3 | 0.537 | 18.77 | 60.3 | 5.4 | 35
KJ102 | 8.5 | 2975 | 80 | 67 | 75 | 112.3 | 0.68 | 23.78 | 76.4 | 5.4 | 35
KJ102 | 8.5 | 2975 | 85 | 67 | 75 | 112.3 | 0.801 | 28.01 | 90 | 5.4 | 35
KJ102 | 8.5 | 2975 | 90 | 67 | 75 | 112.3 | 0.923 | 32.28 | 103.7 | 5.4 | 35
KJ102 | 8.5 | 2975 | 75 | 72 | 75 | 123.1 | 0.362 | 13.88 | 44.6 | 5.3 | 35
KJ102 | 8.5 | 2975 | 80 | 72 | 75 | 123.1 | 0.489 | 18.74 | 60.2 | 5.3 | 35
KJ102 | 8.5 | 2975 | 85 | 72 | 75 | 123.1 | 0.616 | 23.59 | 75.8 | 5.3 | 35
KJ102 | 8.5 | 2975 | 90 | 72 | 75 | 123.1 | 0.742 | 28.45 | 91.4 | 5.3 | 35
KJ102 | 8.5 | 2975 | 80 | 77 | 75 | 133.9 | 0.329 | 13.69 | 44 | 5.2 | 35
KJ102 | 8.5 | 2975 | 85 | 77 | 75 | 133.9 | 0.46 | 19.17 | 61.6 | 5.2 | 35
KJ102 | 8.5 | 2975 | 90 | 77 | 75 | 133.9 | 0.591 | 24.62 | 79.1 | 5.2 | 35
KJ102 | 8.5 | 2975 | 65 | 57 | 85 | 95.8 | 0.593 | 17.68 | 56.8 | 6.2 | 35
KJ102 | 8.5 | 2975 | 70 | 57 | 85 | 95.8 | 0.762 | 22.72 | 73 | 6.2 | 35
KJ102 | 8.5 | 2975 | 75 | 57 | 85 | 95.8 | 0.931 | 27.76 | 89.2 | 6.2 | 35
KJ102 | 8.5 | 2975 | 80 | 57 | 85 | 95.8 | 1 | 29.82 | 95.8 | 6.2 | 35
KJ102 | 8.5 | 2975 | 85 | 57 | 85 | 95.8 | 1 | 29.82 | 95.8 | 6.2 | 35
KJ102 | 8.5 | 2975 | 90 | 57 | 85 | 95.8 | 1 | 29.82 | 95.8 | 6.2 | 35
KJ102 | 8.5 | 2975 | 65 | 62 | 85 | 101.2 | 0.411 | 12.95 | 41.6 | 6.2 | 35
KJ102 | 8.5 | 2975 | 70 | 62 | 85 | 101.2 | 0.568 | 17.9 | 57.5 | 6.2 | 35
KJ102 | 8.5 | 2975 | 75 | 62 | 85 | 101.2 | 0.716 | 22.56 | 72.5 | 6.2 | 35
KJ102 | 8.5 | 2975 | 80 | 62 | 85 | 101.2 | 0.883 | 27.82 | 89.4 | 6.2 | 35
KJ102 | 8.5 | 2975 | 85 | 62 | 85 | 101.2 | 0.959 | 30.22 | 97.1 | 6.2 | 35
KJ102 | 8.5 | 2975 | 90 | 62 | 85 | 101.2 | 1 | 31.5 | 101.2 | 6.2 | 35
KJ102 | 8.5 | 2975 | 70 | 67 | 85 | 106.6 | 0.394 | 13.07 | 42 | 6.2 | 35
KJ102 | 8.5 | 2975 | 75 | 67 | 85 | 106.6 | 0.54 | 17.93 | 57.6 | 6.2 | 35
KJ102 | 8.5 | 2975 | 80 | 67 | 85 | 106.6 | 0.689 | 22.84 | 73.4 | 6.2 | 35
KJ102 | 8.5 | 2975 | 85 | 67 | 85 | 106.6 | 0.814 | 27.02 | 86.8 | 6.2 | 35
KJ102 | 8.5 | 2975 | 90 | 67 | 85 | 106.6 | 0.941 | 31.22 | 100.3 | 6.2 | 35
KJ102 | 8.5 | 2975 | 75 | 72 | 85 | 115.9 | 0.362 | 13.07 | 42 | 6.1 | 35
KJ102 | 8.5 | 2975 | 80 | 72 | 85 | 115.9 | 0.495 | 17.86 | 57.4 | 6.1 | 35
KJ102 | 8.5 | 2975 | 85 | 72 | 85 | 115.9 | 0.629 | 22.69 | 72.9 | 6.1 | 35
KJ102 | 8.5 | 2975 | 90 | 72 | 85 | 115.9 | 0.763 | 27.51 | 88.4 | 6.1 | 35
KJ102 | 8.5 | 2975 | 80 | 77 | 85 | 125.3 | 0.33 | 12.89 | 41.4 | 6.1 | 35
KJ102 | 8.5 | 2975 | 85 | 77 | 85 | 125.3 | 0.47 | 18.33 | 58.9 | 6.1 | 35
KJ102 | 8.5 | 2975 | 90 | 77 | 85 | 125.3 | 0.61 | 23.78 | 76.4 | 6.1 | 35
KJ102 | 8.5 | 2975 | 65 | 57 | 95 | 93.4 | 0.57 | 16.56 | 53.2 | 6.9 | 35
KJ102 | 8.5 | 2975 | 70 | 57 | 95 | 93.4 | 0.744 | 21.63 | 69.5 | 6.9 | 35
KJ102 | 8.5 | 2975 | 75 | 57 | 95 | 93.4 | 0.918 | 26.67 | 85.7 | 6.9 | 35
KJ102 | 8.5 | 2975 | 80 | 57 | 95 | 93.4 | 1 | 29.07 | 93.4 | 6.9 | 35
KJ102 | 8.5 | 2975 | 85 | 57 | 95 | 93.4 | 1 | 29.07 | 93.4 | 6.9 | 35
KJ102 | 8.5 | 2975 | 90 | 57 | 95 | 93.4 | 1 | 29.07 | 93.4 | 6.9 | 35
KJ102 | 8.5 | 2975 | 65 | 62 | 95 | 97.1 | 0.395 | 11.95 | 38.4 | 6.9 | 35
KJ102 | 8.5 | 2975 | 70 | 62 | 95 | 97.1 | 0.559 | 16.9 | 54.3 | 6.9 | 35
KJ102 | 8.5 | 2975 | 75 | 62 | 95 | 97.1 | 0.724 | 21.88 | 70.3 | 6.9 | 35
KJ102 | 8.5 | 2975 | 80 | 62 | 95 | 97.1 | 0.888 | 26.83 | 86.2 | 6.9 | 35
KJ102 | 8.5 | 2975 | 85 | 62 | 95 | 97.1 | 0.965 | 29.16 | 93.7 | 6.9 | 35
KJ102 | 8.5 | 2975 | 90 | 62 | 95 | 97.1 | 1 | 30.22 | 97.1 | 6.9 | 35
KJ102 | 8.5 | 2975 | 70 | 67 | 95 | 100.9 | 0.389 | 12.2 | 39.2 | 7 | 35
KJ102 | 8.5 | 2975 | 75 | 67 | 95 | 100.9 | 0.543 | 17.06 | 54.8 | 7 | 35
KJ102 | 8.5 | 2975 | 80 | 67 | 95 | 100.9 | 0.699 | 21.94 | 70.5 | 7 | 35
KJ102 | 8.5 | 2975 | 85 | 67 | 95 | 100.9 | 0.83 | 26.05 | 83.7 | 7 | 35
KJ102 | 8.5 | 2975 | 90 | 67 | 95 | 100.9 | 0.96 | 30.16 | 96.9 | 7 | 35
KJ102 | 8.5 | 2975 | 75 | 72 | 95 | 108.7 | 0.362 | 12.26 | 39.4 | 7 | 35
KJ102 | 8.5 | 2975 | 80 | 72 | 95 | 108.7 | 0.503 | 17.02 | 54.7 | 7 | 35
KJ102 | 8.5 | 2975 | 85 | 72 | 95 | 108.7 | 0.644 | 21.79 | 70 | 7 | 35
KJ102 | 8.5 | 2975 | 90 | 72 | 95 | 108.7 | 0.785 | 26.55 | 85.3 | 7 | 35
KJ102 | 8.5 | 2975 | 80 | 77 | 95 | 116.6 | 0.334 | 12.11 | 38.9 | 7 | 35
KJ102 | 8.5 | 2975 | 85 | 77 | 95 | 116.6 | 0.483 | 17.52 | 56.3 | 7 | 35
KJ102 | 8.5 | 2975 | 90 | 77 | 95 | 116.6 | 0.632 | 22.94 | 73.7 | 7 | 35
KJ102 | 8.5 | 2975 | 65 | 57 | 105 | 90.4 | 0.558 | 15.69 | 50.4 | 7.8 | 35
KJ102 | 8.5 | 2975 | 70 | 57 | 105 | 90.4 | 0.737 | 20.73 | 66.6 | 7.8 | 35
KJ102 | 8.5 | 2975 | 75 | 57 | 105 | 90.4 | 0.915 | 25.74 | 82.7 | 7.8 | 35
KJ102 | 8.5 | 2975 | 80 | 57 | 105 | 90.4 | 1 | 28.14 | 90.4 | 7.8 | 35
KJ102 | 8.5 | 2975 | 85 | 57 | 105 | 90.4 | 1 | 28.14 | 90.4 | 7.8 | 35
KJ102 | 8.5 | 2975 | 90 | 57 | 105 | 90.4 | 1 | 28.14 | 90.4 | 7.8 | 35
KJ102 | 8.5 | 2975 | 65 | 62 | 105 | 92.8 | 0.381 | 11.02 | 35.4 | 7.9 | 35
KJ102 | 8.5 | 2975 | 70 | 62 | 105 | 92.8 | 0.553 | 15.97 | 51.3 | 7.9 | 35
KJ102 | 8.5 | 2975 | 75 | 62 | 105 | 92.8 | 0.724 | 20.92 | 67.2 | 7.9 | 35
KJ102 | 8.5 | 2975 | 80 | 62 | 105 | 92.8 | 0.895 | 25.86 | 83.1 | 7.9 | 35
KJ102 | 8.5 | 2975 | 85 | 62 | 105 | 92.8 | 0.963 | 27.82 | 89.4 | 7.9 | 35
KJ102 | 8.5 | 2975 | 90 | 62 | 105 | 92.8 | 1 | 28.88 | 92.8 | 7.9 | 35
KJ102 | 8.5 | 2975 | 70 | 67 | 105 | 95.3 | 0.377 | 11.17 | 35.9 | 7.9 | 35
KJ102 | 8.5 | 2975 | 75 | 67 | 105 | 95.3 | 0.541 | 16.06 | 51.6 | 7.9 | 35
KJ102 | 8.5 | 2975 | 80 | 67 | 105 | 95.3 | 0.705 | 20.92 | 67.2 | 7.9 | 35
KJ102 | 8.5 | 2975 | 85 | 67 | 105 | 95.3 | 0.839 | 24.9 | 80 | 7.9 | 35
KJ102 | 8.5 | 2975 | 90 | 67 | 105 | 95.3 | 0.974 | 28.88 | 92.8 | 7.9 | 35
KJ102 | 8.5 | 2975 | 75 | 72 | 105 | 102.1 | 0.353 | 11.2 | 36 | 7.9 | 35
KJ102 | 8.5 | 2975 | 80 | 72 | 105 | 102.1 | 0.503 | 16 | 51.4 | 7.9 | 35
KJ102 | 8.5 | 2975 | 85 | 72 | 105 | 102.1 | 0.654 | 20.79 | 66.8 | 7.9 | 35
KJ102 | 8.5 | 2975 | 90 | 72 | 105 | 102.1 | 0.805 | 25.58 | 82.2 | 7.9 | 35
KJ102 | 8.5 | 2975 | 80 | 77 | 105 | 108.9 | 0.327 | 11.08 | 35.6 | 7.9 | 35
KJ102 | 8.5 | 2975 | 85 | 77 | 105 | 108.9 | 0.492 | 16.68 | 53.6 | 7.9 | 35
KJ102 | 8.5 | 2975 | 90 | 77 | 105 | 108.9 | 0.657 | 22.25 | 71.5 | 7.9 | 35
KJ102 | 8.5 | 2975 | 65 | 57 | 115 | 87.3 | 0.546 | 14.85 | 47.7 | 8.8 | 36
KJ102 | 8.5 | 2975 | 70 | 57 | 115 | 87.3 | 0.73 | 19.83 | 63.7 | 8.8 | 36
KJ102 | 8.5 | 2975 | 75 | 57 | 115 | 87.3 | 0.913 | 24.81 | 79.7 | 8.8 | 36
KJ102 | 8.5 | 2975 | 80 | 57 | 115 | 87.3 | 1 | 27.17 | 87.3 | 8.8 | 36
KJ102 | 8.5 | 2975 | 85 | 57 | 115 | 87.3 | 1 | 27.17 | 87.3 | 8.8 | 36
KJ102 | 8.5 | 2975 | 90 | 57 | 115 | 87.3 | 1 | 27.17 | 87.3 | 8.8 | 36
KJ102 | 8.5 | 2975 | 65 | 62 | 115 | 88.5 | 0.365 | 10.05 | 32.3 | 8.8 | 36
KJ102 | 8.5 | 2975 | 70 | 62 | 115 | 88.5 | 0.545 | 15 | 48.2 | 8.8 | 36
KJ102 | 8.5 | 2975 | 75 | 62 | 115 | 88.5 | 0.723 | 19.92 | 64 | 8.8 | 36
KJ102 | 8.5 | 2975 | 80 | 62 | 115 | 88.5 | 0.903 | 24.87 | 79.9 | 8.8 | 36
KJ102 | 8.5 | 2975 | 85 | 62 | 115 | 88.5 | 0.96 | 26.46 | 85 | 8.8 | 36
KJ102 | 8.5 | 2975 | 90 | 62 | 115 | 88.5 | 1 | 27.54 | 88.5 | 8.8 | 36
KJ102 | 8.5 | 2975 | 70 | 67 | 115 | 89.7 | 0.365 | 10.18 | 32.7 | 8.8 | 36
KJ102 | 8.5 | 2975 | 75 | 67 | 115 | 89.7 | 0.538 | 15.03 | 48.3 | 8.8 | 36
KJ102 | 8.5 | 2975 | 80 | 67 | 115 | 89.7 | 0.713 | 19.92 | 64 | 8.8 | 36
KJ102 | 8.5 | 2975 | 85 | 67 | 115 | 89.7 | 0.851 | 23.75 | 76.3 | 8.8 | 36
KJ102 | 8.5 | 2975 | 90 | 67 | 115 | 89.7 | 0.988 | 27.58 | 88.6 | 8.8 | 36
KJ102 | 8.5 | 2975 | 75 | 72 | 115 | 95.4 | 0.342 | 10.15 | 32.6 | 8.8 | 36
KJ102 | 8.5 | 2975 | 80 | 72 | 115 | 95.4 | 0.504 | 14.97 | 48.1 | 8.8 | 36
KJ102 | 8.5 | 2975 | 85 | 72 | 115 | 95.4 | 0.666 | 19.76 | 63.5 | 8.8 | 36
KJ102 | 8.5 | 2975 | 90 | 72 | 115 | 95.4 | 0.828 | 24.59 | 79 | 8.8 | 36
KJ102 | 8.5 | 2975 | 80 | 77 | 115 | 101.2 | 0.318 | 10.02 | 32.2 | 8.8 | 36
KJ102 | 8.5 | 2975 | 85 | 77 | 115 | 101.2 | 0.502 | 15.81 | 50.8 | 8.8 | 36
KJ102 | 8.5 | 2975 | 90 | 77 | 115 | 101.2 | 0.686 | 21.6 | 69.4 | 8.8 | 36
KJ102 | 8.5 | 2975 | 65 | 57 | 125 | 84.3 | 0.533 | 13.97 | 44.9 | 9.7 | 36
KJ102 | 8.5 | 2975 | 70 | 57 | 125 | 84.3 | 0.721 | 18.92 | 60.8 | 9.7 | 36
KJ102 | 8.5 | 2975 | 75 | 57 | 125 | 84.3 | 0.91 | 23.87 | 76.7 | 9.7 | 36
KJ102 | 8.5 | 2975 | 80 | 57 | 125 | 84.3 | 1 | 26.24 | 84.3 | 9.7 | 36
KJ102 | 8.5 | 2975 | 85 | 57 | 125 | 84.3 | 1 | 26.24 | 84.3 | 9.7 | 36
KJ102 | 8.5 | 2975 | 90 | 57 | 125 | 84.3 | 1 | 26.24 | 84.3 | 9.7 | 36
KJ102 | 8.5 | 2975 | 65 | 62 | 125 | 84.2 | 0.348 | 9.12 | 29.3 | 9.7 | 36
KJ102 | 8.5 | 2975 | 70 | 62 | 125 | 84.2 | 0.536 | 14.04 | 45.1 | 9.7 | 36
KJ102 | 8.5 | 2975 | 75 | 62 | 125 | 84.2 | 0.723 | 18.95 | 60.9 | 9.7 | 36
KJ102 | 8.5 | 2975 | 80 | 62 | 125 | 84.2 | 0.911 | 23.87 | 76.7 | 9.7 | 36
KJ102 | 8.5 | 2975 | 85 | 62 | 125 | 84.2 | 0.958 | 25.12 | 80.7 | 9.7 | 36
KJ102 | 8.5 | 2975 | 90 | 62 | 125 | 84.2 | 1 | 26.21 | 84.2 | 9.7 | 36
KJ102 | 8.5 | 2975 | 70 | 67 | 125 | 84.1 | 0.35 | 9.15 | 29.4 | 9.7 | 36
KJ102 | 8.5 | 2975 | 75 | 67 | 125 | 84.1 | 0.536 | 14.04 | 45.1 | 9.7 | 36
KJ102 | 8.5 | 2975 | 80 | 67 | 125 | 84.1 | 0.722 | 18.89 | 60.7 | 9.7 | 36
KJ102 | 8.5 | 2975 | 85 | 67 | 125 | 84.1 | 0.863 | 22.6 | 72.6 | 9.7 | 36
KJ102 | 8.5 | 2975 | 90 | 67 | 125 | 84.1 | 1 | 26.17 | 84.1 | 9.7 | 36
KJ102 | 8.5 | 2975 | 75 | 72 | 125 | 88.8 | 0.329 | 9.09 | 29.2 | 9.7 | 36
KJ102 | 8.5 | 2975 | 80 | 72 | 125 | 88.8 | 0.505 | 13.94 | 44.8 | 9.7 | 36
KJ102 | 8.5 | 2975 | 85 | 72 | 125 | 88.8 | 0.679 | 18.77 | 60.3 | 9.7 | 36
KJ102 | 8.5 | 2975 | 90 | 72 | 125 | 88.8 | 0.855 | 23.62 | 75.9 | 9.7 | 36
KJ102 | 8.5 | 2975 | 80 | 77 | 125 | 93.5 | 0.308 | 8.96 | 28.8 | 9.8 | 36
KJ102 | 8.5 | 2975 | 85 | 77 | 125 | 93.5 | 0.513 | 14.94 | 48 | 9.8 | 36
KJ102 | 8.5 | 2975 | 90 | 77 | 125 | 93.5 | 0.719 | 20.92 | 67.2 | 9.8 | 36
KJ102 | 8.5 | 3400 | 65 | 57 | 75 | 106.1 | 0.602 | 17.4 | 63.9 | 5.4 | 35
KJ102 | 8.5 | 3400 | 70 | 57 | 75 | 106.1 | 0.774 | 22.36 | 82.1 | 5.4 | 35
KJ102 | 8.5 | 3400 | 75 | 57 | 75 | 106.1 | 0.945 | 27.31 | 100.3 | 5.4 | 35
KJ102 | 8.5 | 3400 | 80 | 57 | 75 | 106.1 | 1 | 28.89 | 106.1 | 5.4 | 35
KJ102 | 8.5 | 3400 | 85 | 57 | 75 | 106.1 | 1 | 28.89 | 106.1 | 5.4 | 35
KJ102 | 8.5 | 3400 | 90 | 57 | 75 | 106.1 | 1 | 28.89 | 106.1 | 5.4 | 35
KJ102 | 8.5 | 3400 | 65 | 62 | 75 | 111.2 | 0.411 | 12.45 | 45.7 | 5.4 | 35
KJ102 | 8.5 | 3400 | 70 | 62 | 75 | 111.2 | 0.575 | 17.4 | 63.9 | 5.4 | 35
KJ102 | 8.5 | 3400 | 75 | 62 | 75 | 111.2 | 0.727 | 22 | 80.8 | 5.4 | 35
KJ102 | 8.5 | 3400 | 80 | 62 | 75 | 111.2 | 0.9 | 27.26 | 100.1 | 5.4 | 35
KJ102 | 8.5 | 3400 | 85 | 62 | 75 | 111.2 | 0.965 | 29.22 | 107.3 | 5.4 | 35
KJ102 | 8.5 | 3400 | 90 | 62 | 75 | 111.2 | 1 | 30.28 | 111.2 | 5.4 | 35
KJ102 | 8.5 | 3400 | 70 | 67 | 75 | 116.2 | 0.392 | 12.42 | 45.6 | 5.3 | 35
KJ102 | 8.5 | 3400 | 75 | 67 | 75 | 116.2 | 0.546 | 17.29 | 63.5 | 5.3 | 35
KJ102 | 8.5 | 3400 | 80 | 67 | 75 | 116.2 | 0.703 | 22.25 | 81.7 | 5.3 | 35
KJ102 | 8.5 | 3400 | 85 | 67 | 75 | 116.2 | 0.83 | 26.25 | 96.4 | 5.3 | 35
KJ102 | 8.5 | 3400 | 90 | 67 | 75 | 116.2 | 0.955 | 30.23 | 111 | 5.3 | 35
KJ102 | 8.5 | 3400 | 75 | 72 | 75 | 125.6 | 0.361 | 12.36 | 45.4 | 5.3 | 35
KJ102 | 8.5 | 3400 | 80 | 72 | 75 | 125.6 | 0.504 | 17.24 | 63.3 | 5.3 | 35
KJ102 | 8.5 | 3400 | 85 | 72 | 75 | 125.6 | 0.647 | 22.14 | 81.3 | 5.3 | 35
KJ102 | 8.5 | 3400 | 90 | 72 | 75 | 125.6 | 0.791 | 27.04 | 99.3 | 5.3 | 35
KJ102 | 8.5 | 3400 | 80 | 77 | 75 | 135 | 0.333 | 12.23 | 44.9 | 5.2 | 35
KJ102 | 8.5 | 3400 | 85 | 77 | 75 | 135 | 0.49 | 18.03 | 66.2 | 5.2 | 35
KJ102 | 8.5 | 3400 | 90 | 77 | 75 | 135 | 0.648 | 23.83 | 87.5 | 5.2 | 35
KJ102 | 8.5 | 3400 | 65 | 57 | 85 | 102.2 | 0.586 | 16.31 | 59.9 | 6.2 | 35
KJ102 | 8.5 | 3400 | 70 | 57 | 85 | 102.2 | 0.767 | 21.35 | 78.4 | 6.2 | 35
KJ102 | 8.5 | 3400 | 75 | 57 | 85 | 102.2 | 0.948 | 26.39 | 96.9 | 6.2 | 35
KJ102 | 8.5 | 3400 | 80 | 57 | 85 | 102.2 | 1 | 27.83 | 102.2 | 6.2 | 35
KJ102 | 8.5 | 3400 | 85 | 57 | 85 | 102.2 | 1 | 27.83 | 102.2 | 6.2 | 35
KJ102 | 8.5 | 3400 | 90 | 57 | 85 | 102.2 | 1 | 27.83 | 102.2 | 6.2 | 35
KJ102 | 8.5 | 3400 | 65 | 62 | 85 | 106.1 | 0.399 | 11.52 | 42.3 | 6.2 | 35
KJ102 | 8.5 | 3400 | 70 | 62 | 85 | 106.1 | 0.571 | 16.5 | 60.6 | 6.2 | 35
KJ102 | 8.5 | 3400 | 75 | 62 | 85 | 106.1 | 0.737 | 21.3 | 78.2 | 6.2 | 35
KJ102 | 8.5 | 3400 | 80 | 62 | 85 | 106.1 | 0.915 | 26.44 | 97.1 | 6.2 | 35
KJ102 | 8.5 | 3400 | 85 | 62 | 85 | 106.1 | 0.975 | 28.19 | 103.5 | 6.2 | 35
KJ102 | 8.5 | 3400 | 90 | 62 | 85 | 106.1 | 1 | 28.89 | 106.1 | 6.2 | 35
KJ102 | 8.5 | 3400 | 70 | 67 | 85 | 110 | 0.389 | 11.66 | 42.8 | 6.2 | 35
KJ102 | 8.5 | 3400 | 75 | 67 | 85 | 110 | 0.551 | 16.5 | 60.6 | 6.2 | 35
KJ102 | 8.5 | 3400 | 80 | 67 | 85 | 110 | 0.715 | 21.43 | 78.7 | 6.2 | 35
KJ102 | 8.5 | 3400 | 85 | 67 | 85 | 110 | 0.844 | 25.27 | 92.8 | 6.2 | 35
KJ102 | 8.5 | 3400 | 90 | 67 | 85 | 110 | 0.972 | 29.11 | 106.9 | 6.2 | 35
KJ102 | 8.5 | 3400 | 75 | 72 | 85 | 118.1 | 0.362 | 11.63 | 42.7 | 6.1 | 35
KJ102 | 8.5 | 3400 | 80 | 72 | 85 | 118.1 | 0.511 | 16.45 | 60.4 | 6.1 | 35
KJ102 | 8.5 | 3400 | 85 | 72 | 85 | 118.1 | 0.661 | 21.27 | 78.1 | 6.1 | 35
KJ102 | 8.5 | 3400 | 90 | 72 | 85 | 118.1 | 0.812 | 26.12 | 95.9 | 6.1 | 35
KJ102 | 8.5 | 3400 | 80 | 77 | 85 | 126.2 | 0.334 | 11.47 | 42.1 | 6.1 | 35
KJ102 | 8.5 | 3400 | 85 | 77 | 85 | 126.2 | 0.503 | 17.29 | 63.5 | 6.1 | 35
KJ102 | 8.5 | 3400 | 90 | 77 | 85 | 126.2 | 0.673 | 23.12 | 84.9 | 6.1 | 35
KJ102 | 8.5 | 3400 | 65 | 57 | 95 | 98.3 | 0.569 | 15.22 | 55.9 | 6.9 | 35
KJ102 | 8.5 | 3400 | 70 | 57 | 95 | 98.3 | 0.76 | 20.34 | 74.7 | 6.9 | 35
KJ102 | 8.5 | 3400 | 75 | 57 | 95 | 98.3 | 0.951 | 25.46 | 93.5 | 6.9 | 35
KJ102 | 8.5 | 3400 | 80 | 57 | 95 | 98.3 | 1 | 26.77 | 98.3 | 6.9 | 35
KJ102 | 8.5 | 3400 | 85 | 57 | 95 | 98.3 | 1 | 26.77 | 98.3 | 6.9 | 35
KJ102 | 8.5 | 3400 | 90 | 57 | 95 | 98.3 | 1 | 26.77 | 98.3 | 6.9 | 35
KJ102 | 8.5 | 3400 | 65 | 62 | 95 | 101.1 | 0.385 | 10.59 | 38.9 | 6.9 | 35
KJ102 | 8.5 | 3400 | 70 | 62 | 95 | 101.1 | 0.567 | 15.6 | 57.3 | 6.9 | 35
KJ102 | 8.5 | 3400 | 75 | 62 | 95 | 101.1 | 0.749 | 20.62 | 75.7 | 6.9 | 35
KJ102 | 8.5 | 3400 | 80 | 62 | 95 | 101.1 | 0.93 | 25.6 | 94 | 6.9 | 35
KJ102 | 8.5 | 3400 | 85 | 62 | 95 | 101.1 | 0.987 | 27.18 | 99.8 | 6.9 | 35
KJ102 | 8.5 | 3400 | 90 | 62 | 95 | 101.1 | 1 | 27.53 | 101.1 | 6.9 | 35
KJ102 | 8.5 | 3400 | 70 | 67 | 95 | 103.9 | 0.384 | 10.87 | 39.9 | 7 | 35
KJ102 | 8.5 | 3400 | 75 | 67 | 95 | 103.9 | 0.556 | 15.74 | 57.8 | 7 | 35
KJ102 | 8.5 | 3400 | 80 | 67 | 95 | 103.9 | 0.73 | 20.64 | 75.8 | 7 | 35
KJ102 | 8.5 | 3400 | 85 | 67 | 95 | 103.9 | 0.859 | 24.32 | 89.3 | 7 | 35
KJ102 | 8.5 | 3400 | 90 | 67 | 95 | 103.9 | 0.988 | 27.97 | 102.7 | 7 | 35
KJ102 | 8.5 | 3400 | 75 | 72 | 95 | 110.6 | 0.362 | 10.89 | 40 | 7 | 35
KJ102 | 8.5 | 3400 | 80 | 72 | 95 | 110.6 | 0.52 | 15.66 | 57.5 | 7 | 35
KJ102 | 8.5 | 3400 | 85 | 72 | 95 | 110.6 | 0.678 | 20.42 | 75 | 7 | 35
KJ102 | 8.5 | 3400 | 90 | 72 | 95 | 110.6 | 0.836 | 25.19 | 92.5 | 7 | 35
KJ102 | 8.5 | 3400 | 80 | 77 | 95 | 117.4 | 0.334 | 10.68 | 39.2 | 7 | 35
KJ102 | 8.5 | 3400 | 85 | 77 | 95 | 117.4 | 0.517 | 16.53 | 60.7 | 7 | 35
KJ102 | 8.5 | 3400 | 90 | 77 | 95 | 117.4 | 0.7 | 22.39 | 82.2 | 7 | 35
KJ102 | 8.5 | 3400 | 65 | 57 | 105 | 94.7 | 0.562 | 14.49 | 53.2 | 7.8 | 35
KJ102 | 8.5 | 3400 | 70 | 57 | 105 | 94.7 | 0.759 | 19.58 | 71.9 | 7.8 | 35
KJ102 | 8.5 | 3400 | 75 | 57 | 105 | 94.7 | 0.958 | 24.7 | 90.7 | 7.8 | 35
KJ102 | 8.5 | 3400 | 80 | 57 | 105 | 94.7 | 1 | 25.79 | 94.7 | 7.8 | 35
KJ102 | 8.5 | 3400 | 85 | 57 | 105 | 94.7 | 1 | 25.79 | 94.7 | 7.8 | 35
KJ102 | 8.5 | 3400 | 90 | 57 | 105 | 94.7 | 1 | 25.79 | 94.7 | 7.8 | 35
KJ102 | 8.5 | 3400 | 65 | 62 | 105 | 96.5 | 0.371 | 9.75 | 35.8 | 7.9 | 35
KJ102 | 8.5 | 3400 | 70 | 62 | 105 | 96.5 | 0.561 | 14.73 | 54.1 | 7.9 | 35
KJ102 | 8.5 | 3400 | 75 | 62 | 105 | 96.5 | 0.751 | 19.74 | 72.5 | 7.9 | 35
KJ102 | 8.5 | 3400 | 80 | 62 | 105 | 96.5 | 0.942 | 24.75 | 90.9 | 7.9 | 35
KJ102 | 8.5 | 3400 | 85 | 62 | 105 | 96.5 | 0.988 | 25.95 | 95.3 | 7.9 | 35
KJ102 | 8.5 | 3400 | 90 | 62 | 105 | 96.5 | 1 | 26.28 | 96.5 | 7.9 | 35
KJ102 | 8.5 | 3400 | 70 | 67 | 105 | 98.3 | 0.37 | 9.91 | 36.4 | 7.9 | 35
KJ102 | 8.5 | 3400 | 75 | 67 | 105 | 98.3 | 0.553 | 14.81 | 54.4 | 7.9 | 35
KJ102 | 8.5 | 3400 | 80 | 67 | 105 | 98.3 | 0.736 | 19.69 | 72.3 | 7.9 | 35
KJ102 | 8.5 | 3400 | 85 | 67 | 105 | 98.3 | 0.866 | 23.18 | 85.1 | 7.9 | 35
KJ102 | 8.5 | 3400 | 90 | 67 | 105 | 98.3 | 0.995 | 26.63 | 97.8 | 7.9 | 35
KJ102 | 8.5 | 3400 | 75 | 72 | 105 | 103.8 | 0.349 | 9.86 | 36.2 | 7.9 | 35
KJ102 | 8.5 | 3400 | 80 | 72 | 105 | 103.8 | 0.518 | 14.65 | 53.8 | 7.9 | 35
KJ102 | 8.5 | 3400 | 85 | 72 | 105 | 103.8 | 0.688 | 19.44 | 71.4 | 7.9 | 35
KJ102 | 8.5 | 3400 | 90 | 72 | 105 | 103.8 | 0.857 | 24.24 | 89 | 7.9 | 35
KJ102 | 8.5 | 3400 | 80 | 77 | 105 | 109.4 | 0.323 | 9.61 | 35.3 | 7.9 | 35
KJ102 | 8.5 | 3400 | 85 | 77 | 105 | 109.4 | 0.528 | 15.74 | 57.8 | 7.9 | 35
KJ102 | 8.5 | 3400 | 90 | 77 | 105 | 109.4 | 0.734 | 21.87 | 80.3 | 7.9 | 35
KJ102 | 8.5 | 3400 | 65 | 57 | 115 | 91.1 | 0.554 | 13.75 | 50.5 | 8.8 | 36
KJ102 | 8.5 | 3400 | 70 | 57 | 115 | 91.1 | 0.76 | 18.85 | 69.2 | 8.8 | 36
KJ102 | 8.5 | 3400 | 75 | 57 | 115 | 91.1 | 0.965 | 23.94 | 87.9 | 8.8 | 36
KJ102 | 8.5 | 3400 | 80 | 57 | 115 | 91.1 | 1 | 24.81 | 91.1 | 8.8 | 36
KJ102 | 8.5 | 3400 | 85 | 57 | 115 | 91.1 | 1 | 24.81 | 91.1 | 8.8 | 36
KJ102 | 8.5 | 3400 | 90 | 57 | 115 | 91.1 | 1 | 24.81 | 91.1 | 8.8 | 36
KJ102 | 8.5 | 3400 | 65 | 62 | 115 | 91.9 | 0.355 | 8.88 | 32.6 | 8.8 | 36
KJ102 | 8.5 | 3400 | 70 | 62 | 115 | 91.9 | 0.555 | 13.89 | 51 | 8.8 | 36
KJ102 | 8.5 | 3400 | 75 | 62 | 115 | 91.9 | 0.755 | 18.9 | 69.4 | 8.8 | 36
KJ102 | 8.5 | 3400 | 80 | 62 | 115 | 91.9 | 0.955 | 23.91 | 87.8 | 8.8 | 36
KJ102 | 8.5 | 3400 | 85 | 62 | 115 | 91.9 | 0.988 | 24.73 | 90.8 | 8.8 | 36
KJ102 | 8.5 | 3400 | 90 | 62 | 115 | 91.9 | 1 | 25.03 | 91.9 | 8.8 | 36
KJ102 | 8.5 | 3400 | 70 | 67 | 115 | 92.7 | 0.354 | 8.93 | 32.8 | 8.8 | 36
KJ102 | 8.5 | 3400 | 75 | 67 | 115 | 92.7 | 0.549 | 13.86 | 50.9 | 8.8 | 36
KJ102 | 8.5 | 3400 | 80 | 67 | 115 | 92.7 | 0.743 | 18.76 | 68.9 | 8.8 | 36
KJ102 | 8.5 | 3400 | 85 | 67 | 115 | 92.7 | 0.873 | 22.03 | 80.9 | 8.8 | 36
KJ102 | 8.5 | 3400 | 90 | 67 | 115 | 92.7 | 1 | 25.25 | 92.7 | 8.8 | 36
KJ102 | 8.5 | 3400 | 75 | 72 | 115 | 97 | 0.334 | 8.82 | 32.4 | 8.8 | 36
KJ102 | 8.5 | 3400 | 80 | 72 | 115 | 97 | 0.516 | 13.64 | 50.1 | 8.8 | 36
KJ102 | 8.5 | 3400 | 85 | 72 | 115 | 97 | 0.7 | 18.49 | 67.9 | 8.8 | 36
KJ102 | 8.5 | 3400 | 90 | 72 | 115 | 97 | 0.882 | 23.31 | 85.6 | 8.8 | 36
KJ102 | 8.5 | 3400 | 80 | 77 | 115 | 101.3 | 0.309 | 8.52 | 31.3 | 8.8 | 36
KJ102 | 8.5 | 3400 | 85 | 77 | 115 | 101.3 | 0.541 | 14.92 | 54.8 | 8.8 | 36
KJ102 | 8.5 | 3400 | 90 | 77 | 115 | 101.3 | 0.773 | 21.32 | 78.3 | 8.8 | 36
KJ102 | 8.5 | 3400 | 65 | 57 | 125 | 87.5 | 0.546 | 13.02 | 47.8 | 9.7 | 36
KJ102 | 8.5 | 3400 | 70 | 57 | 125 | 87.5 | 0.759 | 18.08 | 66.4 | 9.7 | 36
KJ102 | 8.5 | 3400 | 75 | 57 | 125 | 87.5 | 0.973 | 23.18 | 85.1 | 9.7 | 36
KJ102 | 8.5 | 3400 | 80 | 57 | 125 | 87.5 | 1 | 23.83 | 87.5 | 9.7 | 36
KJ102 | 8.5 | 3400 | 85 | 57 | 125 | 87.5 | 1 | 23.83 | 87.5 | 9.7 | 36
KJ102 | 8.5 | 3400 | 90 | 57 | 125 | 87.5 | 1 | 23.83 | 87.5 | 9.7 | 36
KJ102 | 8.5 | 3400 | 65 | 62 | 125 | 87.3 | 0.338 | 8.03 | 29.5 | 9.7 | 36
KJ102 | 8.5 | 3400 | 70 | 62 | 125 | 87.3 | 0.549 | 13.04 | 47.9 | 9.7 | 36
KJ102 | 8.5 | 3400 | 75 | 62 | 125 | 87.3 | 0.758 | 18.03 | 66.2 | 9.7 | 36
KJ102 | 8.5 | 3400 | 80 | 62 | 125 | 87.3 | 0.969 | 23.04 | 84.6 | 9.7 | 36
KJ102 | 8.5 | 3400 | 85 | 62 | 125 | 87.3 | 0.99 | 23.53 | 86.4 | 9.7 | 36
KJ102 | 8.5 | 3400 | 90 | 62 | 125 | 87.3 | 1 | 23.77 | 87.3 | 9.7 | 36
KJ102 | 8.5 | 3400 | 70 | 67 | 125 | 87.1 | 0.336 | 7.98 | 29.3 | 9.7 | 36
KJ102 | 8.5 | 3400 | 75 | 67 | 125 | 87.1 | 0.544 | 12.91 | 47.4 | 9.7 | 36
KJ102 | 8.5 | 3400 | 80 | 67 | 125 | 87.1 | 0.752 | 17.84 | 65.5 | 9.7 | 36
KJ102 | 8.5 | 3400 | 85 | 67 | 125 | 87.1 | 0.881 | 20.89 | 76.7 | 9.7 | 36
KJ102 | 8.5 | 3400 | 90 | 67 | 125 | 87.1 | 1 | 23.72 | 87.1 | 9.7 | 36
KJ102 | 8.5 | 3400 | 75 | 72 | 125 | 90.2 | 0.317 | 7.79 | 28.6 | 9.7 | 36
KJ102 | 8.5 | 3400 | 80 | 72 | 125 | 90.2 | 0.514 | 12.64 | 46.4 | 9.7 | 36
KJ102 | 8.5 | 3400 | 85 | 72 | 125 | 90.2 | 0.713 | 17.51 | 64.3 | 9.7 | 36
KJ102 | 8.5 | 3400 | 90 | 72 | 125 | 90.2 | 0.911 | 22.39 | 82.2 | 9.7 | 36
KJ102 | 8.5 | 3400 | 80 | 77 | 125 | 93.3 | 0.293 | 7.43 | 27.3 | 9.7 | 36
KJ102 | 8.5 | 3400 | 85 | 77 | 125 | 93.3 | 0.556 | 14.13 | 51.9 | 9.7 | 36
KJ102 | 8.5 | 3400 | 90 | 77 | 125 | 93.3 | 0.819 | 20.81 | 76.4 | 9.7 | 36
KJ102 | 8.5 | 3825 | 65 | 57 | 75 | 114.1 | 0.59 | 16.29 | 67.3 | 5.4 | 35
KJ102 | 8.5 | 3825 | 70 | 57 | 75 | 114.1 | 0.768 | 21.21 | 87.6 | 5.4 | 35
KJ102 | 8.5 | 3825 | 75 | 57 | 75 | 114.1 | 0.947 | 26.14 | 108 | 5.4 | 35
KJ102 | 8.5 | 3825 | 80 | 57 | 75 | 114.1 | 1 | 27.62 | 114.1 | 5.4 | 35
KJ102 | 8.5 | 3825 | 85 | 57 | 75 | 114.1 | 1 | 27.62 | 114.1 | 5.4 | 35
KJ102 | 8.5 | 3825 | 90 | 57 | 75 | 114.1 | 1 | 27.62 | 114.1 | 5.4 | 35
KJ102 | 8.5 | 3825 | 65 | 62 | 75 | 117.1 | 0.399 | 11.3 | 46.7 | 5.3 | 35
KJ102 | 8.5 | 3825 | 70 | 62 | 75 | 117.1 | 0.572 | 16.22 | 67 | 5.3 | 35
KJ102 | 8.5 | 3825 | 75 | 62 | 75 | 117.1 | 0.74 | 20.99 | 86.7 | 5.3 | 35
KJ102 | 8.5 | 3825 | 80 | 62 | 75 | 117.1 | 0.92 | 26.07 | 107.7 | 5.3 | 35
KJ102 | 8.5 | 3825 | 85 | 62 | 75 | 117.1 | 0.974 | 27.6 | 114 | 5.3 | 35
KJ102 | 8.5 | 3825 | 90 | 62 | 75 | 117.1 | 1 | 28.35 | 117.1 | 5.3 | 35
KJ102 | 8.5 | 3825 | 70 | 67 | 75 | 120.1 | 0.386 | 11.23 | 46.4 | 5.3 | 35
KJ102 | 8.5 | 3825 | 75 | 67 | 75 | 120.1 | 0.555 | 16.15 | 66.7 | 5.3 | 35
KJ102 | 8.5 | 3825 | 80 | 67 | 75 | 120.1 | 0.725 | 21.08 | 87.1 | 5.3 | 35
KJ102 | 8.5 | 3825 | 85 | 67 | 75 | 120.1 | 0.855 | 24.86 | 102.7 | 5.3 | 35
KJ102 | 8.5 | 3825 | 90 | 67 | 75 | 120.1 | 0.985 | 28.64 | 118.3 | 5.3 | 35
KJ102 | 8.5 | 3825 | 75 | 72 | 75 | 128.1 | 0.361 | 11.18 | 46.2 | 5.3 | 35
KJ102 | 8.5 | 3825 | 80 | 72 | 75 | 128.1 | 0.519 | 16.1 | 66.5 | 5.3 | 35
KJ102 | 8.5 | 3825 | 85 | 72 | 75 | 128.1 | 0.678 | 21.01 | 86.8 | 5.3 | 35
KJ102 | 8.5 | 3825 | 90 | 72 | 75 | 128.1 | 0.836 | 25.93 | 107.1 | 5.3 | 35
KJ102 | 8.5 | 3825 | 65 | 57 | 85 | 108.6 | 0.579 | 15.23 | 62.9 | 6.1 | 35
KJ102 | 8.5 | 3825 | 70 | 57 | 85 | 108.6 | 0.772 | 20.29 | 83.8 | 6.1 | 35
KJ102 | 8.5 | 3825 | 75 | 57 | 85 | 108.6 | 0.963 | 25.32 | 104.6 | 6.1 | 35
KJ102 | 8.5 | 3825 | 80 | 57 | 85 | 108.6 | 1 | 26.29 | 108.6 | 6.1 | 35
KJ102 | 8.5 | 3825 | 85 | 57 | 85 | 108.6 | 1 | 26.29 | 108.6 | 6.1 | 35
KJ102 | 8.5 | 3825 | 90 | 57 | 85 | 108.6 | 1 | 26.29 | 108.6 | 6.1 | 35
KJ102 | 8.5 | 3825 | 65 | 62 | 85 | 111.1 | 0.388 | 10.43 | 43.1 | 6.1 | 35
KJ102 | 8.5 | 3825 | 70 | 62 | 85 | 111.1 | 0.572 | 15.4 | 63.6 | 6.1 | 35
KJ102 | 8.5 | 3825 | 75 | 62 | 85 | 111.1 | 0.755 | 20.31 | 83.9 | 6.1 | 35
KJ102 | 8.5 | 3825 | 80 | 62 | 85 | 111.1 | 0.943 | 25.37 | 104.8 | 6.1 | 35
KJ102 | 8.5 | 3825 | 85 | 62 | 85 | 111.1 | 0.989 | 26.6 | 109.9 | 6.1 | 35
KJ102 | 8.5 | 3825 | 90 | 62 | 85 | 111.1 | 1 | 26.89 | 111.1 | 6.1 | 35
KJ102 | 8.5 | 3825 | 70 | 67 | 85 | 113.5 | 0.383 | 10.53 | 43.5 | 6.1 | 35
KJ102 | 8.5 | 3825 | 75 | 67 | 85 | 113.5 | 0.561 | 15.42 | 63.7 | 6.1 | 35
KJ102 | 8.5 | 3825 | 80 | 67 | 85 | 113.5 | 0.741 | 20.36 | 84.1 | 6.1 | 35
KJ102 | 8.5 | 3825 | 85 | 67 | 85 | 113.5 | 0.87 | 23.92 | 98.8 | 6.1 | 35
KJ102 | 8.5 | 3825 | 90 | 67 | 85 | 113.5 | 1 | 27.48 | 113.5 | 6.1 | 35
KJ102 | 8.5 | 3825 | 75 | 72 | 85 | 120.3 | 0.361 | 10.51 | 43.4 | 6.2 | 35
KJ102 | 8.5 | 3825 | 80 | 72 | 85 | 120.3 | 0.527 | 15.35 | 63.4 | 6.2 | 35
KJ102 | 8.5 | 3825 | 85 | 72 | 85 | 120.3 | 0.693 | 20.19 | 83.4 | 6.2 | 35
KJ102 | 8.5 | 3825 | 90 | 72 | 85 | 120.3 | 0.86 | 25.03 | 103.4 | 6.2 | 35
KJ102 | 8.5 | 3825 | 65 | 57 | 95 | 103.1 | 0.568 | 14.19 | 58.6 | 6.9 | 35
KJ102 | 8.5 | 3825 | 70 | 57 | 95 | 103.1 | 0.775 | 19.34 | 79.9 | 6.9 | 35
KJ102 | 8.5 | 3825 | 75 | 57 | 95 | 103.1 | 0.982 | 24.5 | 101.2 | 6.9 | 35
KJ102 | 8.5 | 3825 | 80 | 57 | 95 | 103.1 | 1 | 24.96 | 103.1 | 6.9 | 35
KJ102 | 8.5 | 3825 | 85 | 57 | 95 | 103.1 | 1 | 24.96 | 103.1 | 6.9 | 35
KJ102 | 8.5 | 3825 | 90 | 57 | 95 | 103.1 | 1 | 24.96 | 103.1 | 6.9 | 35
KJ102 | 8.5 | 3825 | 65 | 62 | 95 | 105 | 0.376 | 9.56 | 39.5 | 6.9 | 35
KJ102 | 8.5 | 3825 | 70 | 62 | 95 | 105 | 0.573 | 14.57 | 60.2 | 6.9 | 35
KJ102 | 8.5 | 3825 | 75 | 62 | 95 | 105 | 0.771 | 19.61 | 81 | 6.9 | 35
KJ102 | 8.5 | 3825 | 80 | 62 | 95 | 105 | 0.97 | 24.64 | 101.8 | 6.9 | 35
KJ102 | 8.5 | 3825 | 85 | 62 | 95 | 105 | 1 | 25.42 | 105 | 6.9 | 35
KJ102 | 8.5 | 3825 | 90 | 62 | 95 | 105 | 1 | 25.42 | 105 | 6.9 | 35
KJ102 | 8.5 | 3825 | 70 | 67 | 95 | 106.9 | 0.38 | 9.83 | 40.6 | 7 | 35
KJ102 | 8.5 | 3825 | 75 | 67 | 95 | 106.9 | 0.569 | 14.72 | 60.8 | 7 | 35
KJ102 | 8.5 | 3825 | 80 | 67 | 95 | 106.9 | 0.758 | 19.61 | 81 | 7 | 35
KJ102 | 8.5 | 3825 | 85 | 67 | 95 | 106.9 | 0.887 | 22.95 | 94.8 | 7 | 35
KJ102 | 8.5 | 3825 | 90 | 67 | 95 | 106.9 | 1 | 25.88 | 106.9 | 7 | 35
KJ102 | 8.5 | 3825 | 75 | 72 | 95 | 112.5 | 0.361 | 9.83 | 40.6 | 7 | 35
KJ102 | 8.5 | 3825 | 80 | 72 | 95 | 112.5 | 0.536 | 14.6 | 60.3 | 7 | 35
KJ102 | 8.5 | 3825 | 85 | 72 | 95 | 112.5 | 0.711 | 19.37 | 80 | 7 | 35
KJ102 | 8.5 | 3825 | 90 | 72 | 95 | 112.5 | 0.886 | 24.13 | 99.7 | 7 | 35
KJ102 | 8.5 | 3825 | 65 | 57 | 105 | 98.9 | 0.565 | 13.53 | 55.9 | 7.8 | 35
KJ102 | 8.5 | 3825 | 70 | 57 | 105 | 98.9 | 0.782 | 18.71 | 77.3 | 7.8 | 35
KJ102 | 8.5 | 3825 | 75 | 57 | 105 | 98.9 | 0.997 | 23.87 | 98.6 | 7.8 | 35
KJ102 | 8.5 | 3825 | 80 | 57 | 105 | 98.9 | 1 | 23.94 | 98.9 | 7.8 | 35
KJ102 | 8.5 | 3825 | 85 | 57 | 105 | 98.9 | 1 | 23.94 | 98.9 | 7.8 | 35
KJ102 | 8.5 | 3825 | 90 | 57 | 105 | 98.9 | 1 | 23.94 | 98.9 | 7.8 | 35
KJ102 | 8.5 | 3825 | 65 | 62 | 105 | 100.1 | 0.362 | 8.76 | 36.2 | 7.9 | 35
KJ102 | 8.5 | 3825 | 70 | 62 | 105 | 100.1 | 0.569 | 13.8 | 57 | 7.9 | 35
KJ102 | 8.5 | 3825 | 75 | 62 | 105 | 100.1 | 0.778 | 18.86 | 77.9 | 7.9 | 35
KJ102 | 8.5 | 3825 | 80 | 62 | 105 | 100.1 | 0.986 | 23.89 | 98.7 | 7.9 | 35
KJ102 | 8.5 | 3825 | 85 | 62 | 105 | 100.1 | 1 | 24.23 | 100.1 | 7.9 | 35
KJ102 | 8.5 | 3825 | 90 | 62 | 105 | 100.1 | 1 | 24.23 | 100.1 | 7.9 | 35
KJ102 | 8.5 | 3825 | 70 | 67 | 105 | 101.3 | 0.363 | 8.91 | 36.8 | 7.9 | 35
KJ102 | 8.5 | 3825 | 75 | 67 | 105 | 101.3 | 0.564 | 13.82 | 57.1 | 7.9 | 35
KJ102 | 8.5 | 3825 | 80 | 67 | 105 | 101.3 | 0.765 | 18.76 | 77.5 | 7.9 | 35
KJ102 | 8.5 | 3825 | 85 | 67 | 105 | 101.3 | 0.89 | 21.83 | 90.2 | 7.9 | 35
KJ102 | 8.5 | 3825 | 90 | 67 | 105 | 101.3 | 1 | 24.52 | 101.3 | 7.9 | 35
KJ102 | 8.5 | 3825 | 75 | 72 | 105 | 105.5 | 0.345 | 8.81 | 36.4 | 7.9 | 35
KJ102 | 8.5 | 3825 | 80 | 72 | 105 | 105.5 | 0.533 | 13.6 | 56.2 | 7.9 | 35
KJ102 | 8.5 | 3825 | 85 | 72 | 105 | 105.5 | 0.721 | 18.42 | 76.1 | 7.9 | 35
KJ102 | 8.5 | 3825 | 90 | 72 | 105 | 105.5 | 0.909 | 23.21 | 95.9 | 7.9 | 35
KJ102 | 8.5 | 3825 | 65 | 57 | 115 | 94.8 | 0.562 | 12.9 | 53.3 | 8.8 | 36
KJ102 | 8.5 | 3825 | 70 | 57 | 115 | 94.8 | 0.788 | 18.08 | 74.7 | 8.8 | 36
KJ102 | 8.5 | 3825 | 75 | 57 | 115 | 94.8 | 1 | 22.95 | 94.8 | 8.8 | 36
KJ102 | 8.5 | 3825 | 80 | 57 | 115 | 94.8 | 1 | 22.95 | 94.8 | 8.8 | 36
KJ102 | 8.5 | 3825 | 85 | 57 | 115 | 94.8 | 1 | 22.95 | 94.8 | 8.8 | 36
KJ102 | 8.5 | 3825 | 90 | 57 | 115 | 94.8 | 1 | 22.95 | 94.8 | 8.8 | 36
KJ102 | 8.5 | 3825 | 65 | 62 | 115 | 95.2 | 0.346 | 7.96 | 32.9 | 8.8 | 36
KJ102 | 8.5 | 3825 | 70 | 62 | 115 | 95.2 | 0.565 | 13.02 | 53.8 | 8.8 | 36
KJ102 | 8.5 | 3825 | 75 | 62 | 115 | 95.2 | 0.785 | 18.08 | 74.7 | 8.8 | 36
KJ102 | 8.5 | 3825 | 80 | 62 | 115 | 95.2 | 1 | 23.05 | 95.2 | 8.8 | 36
KJ102 | 8.5 | 3825 | 85 | 62 | 115 | 95.2 | 1 | 23.05 | 95.2 | 8.8 | 36
KJ102 | 8.5 | 3825 | 90 | 62 | 115 | 95.2 | 1 | 23.05 | 95.2 | 8.8 | 36
KJ102 | 8.5 | 3825 | 70 | 67 | 115 | 95.7 | 0.345 | 7.99 | 33 | 8.8 | 36
KJ102 | 8.5 | 3825 | 75 | 67 | 115 | 95.7 | 0.558 | 12.93 | 53.4 | 8.8 | 36
KJ102 | 8.5 | 3825 | 80 | 67 | 115 | 95.7 | 0.772 | 17.89 | 73.9 | 8.8 | 36
KJ102 | 8.5 | 3825 | 85 | 67 | 115 | 95.7 | 0.893 | 20.7 | 85.5 | 8.8 | 36
KJ102 | 8.5 | 3825 | 90 | 67 | 115 | 95.7 | 1 | 23.17 | 95.7 | 8.8 | 36
KJ102 | 8.5 | 3825 | 75 | 72 | 115 | 98.6 | 0.326 | 7.77 | 32.1 | 8.8 | 36
KJ102 | 8.5 | 3825 | 80 | 72 | 115 | 98.6 | 0.529 | 12.64 | 52.2 | 8.8 | 36
KJ102 | 8.5 | 3825 | 85 | 72 | 115 | 98.6 | 0.732 | 17.48 | 72.2 | 8.8 | 36
KJ102 | 8.5 | 3825 | 90 | 72 | 115 | 98.6 | 0.935 | 22.32 | 92.2 | 8.8 | 36
KJ102 | 8.5 | 3825 | 65 | 57 | 125 | 90.6 | 0.558 | 12.25 | 50.6 | 9.7 | 36
KJ102 | 8.5 | 3825 | 70 | 57 | 125 | 90.6 | 0.795 | 17.43 | 72 | 9.7 | 36
KJ102 | 8.5 | 3825 | 75 | 57 | 125 | 90.6 | 1 | 21.93 | 90.6 | 9.7 | 36
KJ102 | 8.5 | 3825 | 80 | 57 | 125 | 90.6 | 1 | 21.93 | 90.6 | 9.7 | 36
KJ102 | 8.5 | 3825 | 85 | 57 | 125 | 90.6 | 1 | 21.93 | 90.6 | 9.7 | 36
KJ102 | 8.5 | 3825 | 90 | 57 | 125 | 90.6 | 1 | 21.93 | 90.6 | 9.7 | 36
KJ102 | 8.5 | 3825 | 65 | 62 | 125 | 90.3 | 0.328 | 7.17 | 29.6 | 9.7 | 36
KJ102 | 8.5 | 3825 | 70 | 62 | 125 | 90.3 | 0.56 | 12.25 | 50.6 | 9.7 | 36
KJ102 | 8.5 | 3825 | 75 | 62 | 125 | 90.3 | 0.793 | 17.33 | 71.6 | 9.7 | 36
KJ102 | 8.5 | 3825 | 80 | 62 | 125 | 90.3 | 1 | 21.86 | 90.3 | 9.7 | 36
KJ102 | 8.5 | 3825 | 85 | 62 | 125 | 90.3 | 1 | 21.86 | 90.3 | 9.7 | 36
KJ102 | 8.5 | 3825 | 90 | 62 | 125 | 90.3 | 1 | 21.86 | 90.3 | 9.7 | 36
KJ102 | 8.5 | 3825 | 70 | 67 | 125 | 90.1 | 0.324 | 7.07 | 29.2 | 9.7 | 36
KJ102 | 8.5 | 3825 | 75 | 67 | 125 | 90.1 | 0.553 | 12.06 | 49.8 | 9.7 | 36
KJ102 | 8.5 | 3825 | 80 | 67 | 125 | 90.1 | 0.78 | 17.02 | 70.3 | 9.7 | 36
KJ102 | 8.5 | 3825 | 85 | 67 | 125 | 90.1 | 0.897 | 19.56 | 80.8 | 9.7 | 36
KJ102 | 8.5 | 3825 | 90 | 67 | 125 | 90.1 | 1 | 21.81 | 90.1 | 9.7 | 36
KJ102 | 8.5 | 3825 | 75 | 72 | 125 | 91.6 | 0.305 | 6.75 | 27.9 | 9.7 | 36
KJ102 | 8.5 | 3825 | 80 | 72 | 125 | 91.6 | 0.525 | 11.64 | 48.1 | 9.7 | 36
KJ102 | 8.5 | 3825 | 85 | 72 | 125 | 91.6 | 0.746 | 16.53 | 68.3 | 9.7 | 36
KJ102 | 8.5 | 3825 | 90 | 72 | 125 | 91.6 | 0.966 | 21.42 | 88.5 | 9.7 | 36
KJ102 | 8.5 | 4250 | 65 | 57 | 75 | 122.1 | 0.579 | 15.4 | 70.7 | 5.3 | 35
KJ102 | 8.5 | 4250 | 70 | 57 | 75 | 122.1 | 0.762 | 20.28 | 93.1 | 5.3 | 35
KJ102 | 8.5 | 4250 | 75 | 57 | 75 | 122.1 | 0.947 | 25.19 | 115.6 | 5.3 | 35
KJ102 | 8.5 | 4250 | 80 | 57 | 75 | 122.1 | 1 | 26.6 | 122.1 | 5.3 | 35
KJ102 | 8.5 | 4250 | 85 | 57 | 75 | 122.1 | 1 | 26.6 | 122.1 | 5.3 | 35
KJ102 | 8.5 | 4250 | 90 | 57 | 75 | 122.1 | 1 | 26.6 | 122.1 | 5.3 | 35
KJ102 | 8.5 | 4250 | 65 | 62 | 75 | 123.1 | 0.387 | 10.39 | 47.7 | 5.3 | 35
KJ102 | 8.5 | 4250 | 70 | 62 | 75 | 123.1 | 0.57 | 15.29 | 70.2 | 5.3 | 35
KJ102 | 8.5 | 4250 | 75 | 62 | 75 | 123.1 | 0.753 | 20.2 | 92.7 | 5.3 | 35
KJ102 | 8.5 | 4250 | 80 | 62 | 75 | 123.1 | 0.937 | 25.12 | 115.3 | 5.3 | 35
KJ102 | 8.5 | 4250 | 85 | 62 | 75 | 123.1 | 0.981 | 26.3 | 120.7 | 5.3 | 35
KJ102 | 8.5 | 4250 | 90 | 62 | 75 | 123.1 | 1 | 26.82 | 123.1 | 5.3 | 35
KJ102 | 8.5 | 4250 | 70 | 67 | 75 | 124.1 | 0.381 | 10.31 | 47.3 | 5.3 | 35
KJ102 | 8.5 | 4250 | 75 | 67 | 75 | 124.1 | 0.563 | 15.23 | 69.9 | 5.3 | 35
KJ102 | 8.5 | 4250 | 80 | 67 | 75 | 124.1 | 0.745 | 20.13 | 92.4 | 5.3 | 35
KJ102 | 8.5 | 4250 | 85 | 67 | 75 | 124.1 | 0.879 | 23.77 | 109.1 | 5.3 | 35
KJ102 | 8.5 | 4250 | 90 | 67 | 75 | 124.1 | 1 | 27.04 | 124.1 | 5.3 | 35
KJ102 | 8.5 | 4250 | 75 | 72 | 75 | 130.6 | 0.36 | 10.24 | 47 | 5.3 | 35
KJ102 | 8.5 | 4250 | 80 | 72 | 75 | 130.6 | 0.533 | 15.16 | 69.6 | 5.3 | 35
KJ102 | 8.5 | 4250 | 85 | 72 | 75 | 130.6 | 0.707 | 20.11 | 92.3 | 5.3 | 35
KJ102 | 8.5 | 4250 | 90 | 72 | 75 | 130.6 | 0.881 | 25.05 | 115 | 5.3 | 35
KJ102 | 8.5 | 4250 | 65 | 57 | 85 | 115.1 | 0.573 | 14.38 | 66 | 6.1 | 35
KJ102 | 8.5 | 4250 | 70 | 57 | 85 | 115.1 | 0.774 | 19.41 | 89.1 | 6.1 | 35
KJ102 | 8.5 | 4250 | 75 | 57 | 85 | 115.1 | 0.976 | 24.47 | 112.3 | 6.1 | 35
KJ102 | 8.5 | 4250 | 80 | 57 | 85 | 115.1 | 1 | 25.08 | 115.1 | 6.1 | 35
KJ102 | 8.5 | 4250 | 85 | 57 | 85 | 115.1 | 1 | 25.08 | 115.1 | 6.1 | 35
KJ102 | 8.5 | 4250 | 90 | 57 | 85 | 115.1 | 1 | 25.08 | 115.1 | 6.1 | 35
KJ102 | 8.5 | 4250 | 65 | 62 | 85 | 116 | 0.378 | 9.54 | 43.8 | 6.1 | 35
KJ102 | 8.5 | 4250 | 70 | 62 | 85 | 116 | 0.575 | 14.53 | 66.7 | 6.1 | 35
KJ102 | 8.5 | 4250 | 75 | 62 | 85 | 116 | 0.772 | 19.52 | 89.6 | 6.1 | 35
KJ102 | 8.5 | 4250 | 80 | 62 | 85 | 116 | 0.969 | 24.49 | 112.4 | 6.1 | 35
KJ102 | 8.5 | 4250 | 85 | 62 | 85 | 116 | 1 | 25.27 | 116 | 6.1 | 35
KJ102 | 8.5 | 4250 | 90 | 62 | 85 | 116 | 1 | 25.27 | 116 | 6.1 | 35
KJ102 | 8.5 | 4250 | 70 | 67 | 85 | 117 | 0.379 | 9.65 | 44.3 | 6.1 | 35
KJ102 | 8.5 | 4250 | 75 | 67 | 85 | 117 | 0.571 | 14.55 | 66.8 | 6.1 | 35
KJ102 | 8.5 | 4250 | 80 | 67 | 85 | 117 | 0.764 | 19.48 | 89.4 | 6.1 | 35
KJ102 | 8.5 | 4250 | 85 | 67 | 85 | 117 | 0.895 | 22.81 | 104.7 | 6.1 | 35
KJ102 | 8.5 | 4250 | 90 | 67 | 85 | 117 | 1 | 25.49 | 117 | 6.1 | 35
KJ102 | 8.5 | 4250 | 75 | 72 | 85 | 122.5 | 0.36 | 9.61 | 44.1 | 6.2 | 35
KJ102 | 8.5 | 4250 | 80 | 72 | 85 | 122.5 | 0.542 | 14.47 | 66.4 | 6.2 | 35
KJ102 | 8.5 | 4250 | 85 | 72 | 85 | 122.5 | 0.723 | 19.3 | 88.6 | 6.2 | 35
KJ102 | 8.5 | 4250 | 90 | 72 | 85 | 122.5 | 0.905 | 24.16 | 110.9 | 6.2 | 35
KJ102 | 8.5 | 4250 | 65 | 57 | 95 | 108 | 0.568 | 13.36 | 61.3 | 6.9 | 35
KJ102 | 8.5 | 4250 | 70 | 57 | 95 | 108 | 0.788 | 18.54 | 85.1 | 6.9 | 35
KJ102 | 8.5 | 4250 | 75 | 57 | 95 | 108 | 1 | 23.53 | 108 | 6.9 | 35
KJ102 | 8.5 | 4250 | 80 | 57 | 95 | 108 | 1 | 23.53 | 108 | 6.9 | 35
KJ102 | 8.5 | 4250 | 85 | 57 | 95 | 108 | 1 | 23.53 | 108 | 6.9 | 35
KJ102 | 8.5 | 4250 | 90 | 57 | 95 | 108 | 1 | 23.53 | 108 | 6.9 | 35
KJ102 | 8.5 | 4250 | 65 | 62 | 95 | 108.9 | 0.367 | 8.71 | 40 | 6.9 | 35
KJ102 | 8.5 | 4250 | 70 | 62 | 95 | 108.9 | 0.58 | 13.77 | 63.2 | 6.9 | 35
KJ102 | 8.5 | 4250 | 75 | 62 | 95 | 108.9 | 0.793 | 18.82 | 86.4 | 6.9 | 35
KJ102 | 8.5 | 4250 | 80 | 62 | 95 | 108.9 | 1 | 23.73 | 108.9 | 6.9 | 35
KJ102 | 8.5 | 4250 | 85 | 62 | 95 | 108.9 | 1 | 23.73 | 108.9 | 6.9 | 35
KJ102 | 8.5 | 4250 | 90 | 62 | 95 | 108.9 | 1 | 23.73 | 108.9 | 6.9 | 35
KJ102 | 8.5 | 4250 | 70 | 67 | 95 | 109.9 | 0.375 | 8.98 | 41.2 | 7 | 35
KJ102 | 8.5 | 4250 | 75 | 67 | 95 | 109.9 | 0.581 | 13.9 | 63.8 | 7 | 35
KJ102 | 8.5 | 4250 | 80 | 67 | 95 | 109.9 | 0.785 | 18.8 | 86.3 | 7 | 35
KJ102 | 8.5 | 4250 | 85 | 67 | 95 | 109.9 | 0.914 | 21.87 | 100.4 | 7 | 35
KJ102 | 8.5 | 4250 | 90 | 67 | 95 | 109.9 | 1 | 23.94 | 109.9 | 7 | 35
KJ102 | 8.5 | 4250 | 75 | 72 | 95 | 114.4 | 0.36 | 8.98 | 41.2 | 7 | 35
KJ102 | 8.5 | 4250 | 80 | 72 | 95 | 114.4 | 0.552 | 13.75 | 63.1 | 7 | 35
KJ102 | 8.5 | 4250 | 85 | 72 | 95 | 114.4 | 0.743 | 18.52 | 85 | 7 | 35
KJ102 | 8.5 | 4250 | 90 | 72 | 95 | 114.4 | 0.934 | 23.27 | 106.8 | 7 | 35
KJ102 | 8.5 | 4250 | 65 | 57 | 105 | 103.2 | 0.569 | 12.79 | 58.7 | 7.8 | 35
KJ102 | 8.5 | 4250 | 70 | 57 | 105 | 103.2 | 0.801 | 18.02 | 82.7 | 7.8 | 35
KJ102 | 8.5 | 4250 | 75 | 57 | 105 | 103.2 | 1 | 22.48 | 103.2 | 7.8 | 35
KJ102 | 8.5 | 4250 | 80 | 57 | 105 | 103.2 | 1 | 22.48 | 103.2 | 7.8 | 35
KJ102 | 8.5 | 4250 | 85 | 57 | 105 | 103.2 | 1 | 22.48 | 103.2 | 7.8 | 35
KJ102 | 8.5 | 4250 | 90 | 57 | 105 | 103.2 | 1 | 22.48 | 103.2 | 7.8 | 35
KJ102 | 8.5 | 4250 | 65 | 62 | 105 | 103.7 | 0.353 | 7.97 | 36.6 | 7.9 | 35
KJ102 | 8.5 | 4250 | 70 | 62 | 105 | 103.7 | 0.578 | 13.05 | 59.9 | 7.9 | 35
KJ102 | 8.5 | 4250 | 75 | 62 | 105 | 103.7 | 0.802 | 18.13 | 83.2 | 7.9 | 35
KJ102 | 8.5 | 4250 | 80 | 62 | 105 | 103.7 | 1 | 22.59 | 103.7 | 7.9 | 35
KJ102 | 8.5 | 4250 | 85 | 62 | 105 | 103.7 | 1 | 22.59 | 103.7 | 7.9 | 35
KJ102 | 8.5 | 4250 | 90 | 62 | 105 | 103.7 | 1 | 22.59 | 103.7 | 7.9 | 35
KJ102 | 8.5 | 4250 | 70 | 67 | 105 | 104.3 | 0.357 | 8.1 | 37.2 | 7.9 | 35
KJ102 | 8.5 | 4250 | 75 | 67 | 105 | 104.3 | 0.574 | 13.05 | 59.9 | 7.9 | 35
KJ102 | 8.5 | 4250 | 80 | 67 | 105 | 104.3 | 0.792 | 18 | 82.6 | 7.9 | 35
KJ102 | 8.5 | 4250 | 85 | 67 | 105 | 104.3 | 0.913 | 20.74 | 95.2 | 7.9 | 35
KJ102 | 8.5 | 4250 | 90 | 67 | 105 | 104.3 | 1 | 22.72 | 104.3 | 7.9 | 35
KJ102 | 8.5 | 4250 | 75 | 72 | 105 | 107.3 | 0.34 | 7.95 | 36.5 | 7.9 | 35
KJ102 | 8.5 | 4250 | 80 | 72 | 105 | 107.3 | 0.546 | 12.77 | 58.6 | 7.9 | 35
KJ102 | 8.5 | 4250 | 85 | 72 | 105 | 107.3 | 0.752 | 17.58 | 80.7 | 7.9 | 35
KJ102 | 8.5 | 4250 | 90 | 72 | 105 | 107.3 | 0.958 | 22.4 | 102.8 | 7.9 | 35
KJ102 | 8.5 | 4250 | 65 | 57 | 115 | 98.5 | 0.57 | 12.22 | 56.1 | 8.8 | 36
KJ102 | 8.5 | 4250 | 70 | 57 | 115 | 98.5 | 0.814 | 17.47 | 80.2 | 8.8 | 36
KJ102 | 8.5 | 4250 | 75 | 57 | 115 | 98.5 | 1 | 21.46 | 98.5 | 8.8 | 36
KJ102 | 8.5 | 4250 | 80 | 57 | 115 | 98.5 | 1 | 21.46 | 98.5 | 8.8 | 36
KJ102 | 8.5 | 4250 | 85 | 57 | 115 | 98.5 | 1 | 21.46 | 98.5 | 8.8 | 36
KJ102 | 8.5 | 4250 | 90 | 57 | 115 | 98.5 | 1 | 21.46 | 98.5 | 8.8 | 36
KJ102 | 8.5 | 4250 | 65 | 62 | 115 | 98.6 | 0.337 | 7.23 | 33.2 | 8.8 | 36
KJ102 | 8.5 | 4250 | 70 | 62 | 115 | 98.6 | 0.574 | 12.33 | 56.6 | 8.8 | 36
KJ102 | 8.5 | 4250 | 75 | 62 | 115 | 98.6 | 0.812 | 17.45 | 80.1 | 8.8 | 36
KJ102 | 8.5 | 4250 | 80 | 62 | 115 | 98.6 | 1 | 21.48 | 98.6 | 8.8 | 36
KJ102 | 8.5 | 4250 | 85 | 62 | 115 | 98.6 | 1 | 21.48 | 98.6 | 8.8 | 36
KJ102 | 8.5 | 4250 | 90 | 62 | 115 | 98.6 | 1 | 21.48 | 98.6 | 8.8 | 36
KJ102 | 8.5 | 4250 | 70 | 67 | 115 | 98.7 | 0.335 | 7.21 | 33.1 | 8.8 | 36
KJ102 | 8.5 | 4250 | 75 | 67 | 115 | 98.7 | 0.567 | 12.2 | 56 | 8.8 | 36
KJ102 | 8.5 | 4250 | 80 | 67 | 115 | 98.7 | 0.799 | 17.19 | 78.9 | 8.8 | 36
KJ102 | 8.5 | 4250 | 85 | 67 | 115 | 98.7 | 0.913 | 19.63 | 90.1 | 8.8 | 36
KJ102 | 8.5 | 4250 | 90 | 67 | 115 | 98.7 | 1 | 21.5 | 98.7 | 8.8 | 36
KJ102 | 8.5 | 4250 | 75 | 72 | 115 | 100.1 | 0.319 | 6.95 | 31.9 | 8.8 | 36
KJ102 | 8.5 | 4250 | 80 | 72 | 115 | 100.1 | 0.541 | 11.81 | 54.2 | 8.8 | 36
KJ102 | 8.5 | 4250 | 85 | 72 | 115 | 100.1 | 0.764 | 16.67 | 76.5 | 8.8 | 36
KJ102 | 8.5 | 4250 | 90 | 72 | 115 | 100.1 | 0.987 | 21.53 | 98.8 | 8.8 | 36
KJ102 | 8.5 | 4250 | 65 | 57 | 125 | 93.7 | 0.571 | 11.66 | 53.5 | 9.7 | 36
KJ102 | 8.5 | 4250 | 70 | 57 | 125 | 93.7 | 0.829 | 16.93 | 77.7 | 9.7 | 36
KJ102 | 8.5 | 4250 | 75 | 57 | 125 | 93.7 | 1 | 20.41 | 93.7 | 9.7 | 36
KJ102 | 8.5 | 4250 | 80 | 57 | 125 | 93.7 | 1 | 20.41 | 93.7 | 9.7 | 36
KJ102 | 8.5 | 4250 | 85 | 57 | 125 | 93.7 | 1 | 20.41 | 93.7 | 9.7 | 36
KJ102 | 8.5 | 4250 | 90 | 57 | 125 | 93.7 | 1 | 20.41 | 93.7 | 9.7 | 36
KJ102 | 8.5 | 4250 | 65 | 62 | 125 | 93.4 | 0.319 | 6.49 | 29.8 | 9.7 | 36
KJ102 | 8.5 | 4250 | 70 | 62 | 125 | 93.4 | 0.572 | 11.63 | 53.4 | 9.7 | 36
KJ102 | 8.5 | 4250 | 75 | 62 | 125 | 93.4 | 0.824 | 16.78 | 77 | 9.7 | 36
KJ102 | 8.5 | 4250 | 80 | 62 | 125 | 93.4 | 1 | 20.35 | 93.4 | 9.7 | 36
KJ102 | 8.5 | 4250 | 85 | 62 | 125 | 93.4 | 1 | 20.35 | 93.4 | 9.7 | 36
KJ102 | 8.5 | 4250 | 90 | 62 | 125 | 93.4 | 1 | 20.35 | 93.4 | 9.7 | 36
KJ102 | 8.5 | 4250 | 70 | 67 | 125 | 93.1 | 0.313 | 6.34 | 29.1 | 9.7 | 36
KJ102 | 8.5 | 4250 | 75 | 67 | 125 | 93.1 | 0.56 | 11.35 | 52.1 | 9.7 | 36
KJ102 | 8.5 | 4250 | 80 | 67 | 125 | 93.1 | 0.808 | 16.38 | 75.2 | 9.7 | 36
KJ102 | 8.5 | 4250 | 85 | 67 | 125 | 93.1 | 0.912 | 18.5 | 84.9 | 9.7 | 36
KJ102 | 8.5 | 4250 | 90 | 67 | 125 | 93.1 | 1 | 20.28 | 93.1 | 9.7 | 36
KJ102 | 8.5 | 4250 | 75 | 72 | 125 | 93 | 0.292 | 5.93 | 27.2 | 9.7 | 36
KJ102 | 8.5 | 4250 | 80 | 72 | 125 | 93 | 0.534 | 10.83 | 49.7 | 9.7 | 36
KJ102 | 8.5 | 4250 | 85 | 72 | 125 | 93 | 0.777 | 15.75 | 72.3 | 9.7 | 36
KJ102 | 8.5 | 4250 | 90 | 72 | 125 | 93 | 1 | 20.26 | 93 | 9.7 | 36
KJ120 | 10 | 2500 | 65 | 62 | 75 | 122.2 | 0.439 | 19.89 | 53.7 | 6.8 | 37
KJ120 | 10 | 2500 | 70 | 62 | 75 | 122.2 | 0.55 | 24.89 | 67.2 | 6.8 | 37
KJ120 | 10 | 2500 | 75 | 62 | 75 | 122.2 | 0.647 | 29.3 | 79.1 | 6.8 | 37
KJ120 | 10 | 2500 | 80 | 62 | 75 | 122.2 | 0.77 | 34.85 | 94.1 | 6.8 | 37
KJ120 | 10 | 2500 | 85 | 62 | 75 | 122.2 | 0.897 | 40.59 | 109.6 | 6.8 | 37
KJ120 | 10 | 2500 | 90 | 62 | 75 | 122.2 | 1 | 45.26 | 122.2 | 6.8 | 37
KJ120 | 10 | 2500 | 70 | 67 | 75 | 132.6 | 0.412 | 20.22 | 54.6 | 6.9 | 37
KJ120 | 10 | 2500 | 75 | 67 | 75 | 132.6 | 0.511 | 25.11 | 67.8 | 6.9 | 37
KJ120 | 10 | 2500 | 80 | 67 | 75 | 132.6 | 0.613 | 30.11 | 81.3 | 6.9 | 37
KJ120 | 10 | 2500 | 85 | 67 | 75 | 132.6 | 0.724 | 35.56 | 96 | 6.9 | 37
KJ120 | 10 | 2500 | 90 | 67 | 75 | 132.6 | 0.835 | 41 | 110.7 | 6.9 | 37
KJ120 | 10 | 2500 | 75 | 72 | 75 | 145.5 | 0.38 | 20.48 | 55.3 | 6.9 | 37
KJ120 | 10 | 2500 | 80 | 72 | 75 | 145.5 | 0.471 | 25.41 | 68.6 | 6.9 | 37
KJ120 | 10 | 2500 | 85 | 72 | 75 | 145.5 | 0.562 | 30.3 | 81.8 | 6.9 | 37
KJ120 | 10 | 2500 | 90 | 72 | 75 | 145.5 | 0.653 | 35.19 | 95 | 6.9 | 37
KJ120 | 10 | 2500 | 80 | 77 | 75 | 158.4 | 0.352 | 20.67 | 55.8 | 7 | 37
KJ120 | 10 | 2500 | 85 | 77 | 75 | 158.4 | 0.427 | 25.04 | 67.6 | 7 | 37
KJ120 | 10 | 2500 | 90 | 77 | 75 | 158.4 | 0.501 | 29.37 | 79.3 | 7 | 37
KJ120 | 10 | 2500 | 65 | 62 | 85 | 117.6 | 0.426 | 18.56 | 50.1 | 7.8 | 37
KJ120 | 10 | 2500 | 70 | 62 | 85 | 117.6 | 0.544 | 23.7 | 64 | 7.8 | 37
KJ120 | 10 | 2500 | 75 | 62 | 85 | 117.6 | 0.656 | 28.59 | 77.2 | 7.8 | 37
KJ120 | 10 | 2500 | 80 | 62 | 85 | 117.6 | 0.781 | 34.04 | 91.9 | 7.8 | 37
KJ120 | 10 | 2500 | 85 | 62 | 85 | 117.6 | 0.904 | 39.37 | 106.3 | 7.8 | 37
KJ120 | 10 | 2500 | 90 | 62 | 85 | 117.6 | 1 | 43.56 | 117.6 | 7.8 | 37
KJ120 | 10 | 2500 | 70 | 67 | 85 | 124.8 | 0.406 | 18.78 | 50.7 | 7.9 | 37
KJ120 | 10 | 2500 | 75 | 67 | 85 | 124.8 | 0.515 | 23.81 | 64.3 | 7.9 | 37
KJ120 | 10 | 2500 | 80 | 67 | 85 | 124.8 | 0.626 | 28.93 | 78.1 | 7.9 | 37
KJ120 | 10 | 2500 | 85 | 67 | 85 | 124.8 | 0.745 | 34.44 | 93 | 7.9 | 37
KJ120 | 10 | 2500 | 90 | 67 | 85 | 124.8 | 0.865 | 39.96 | 107.9 | 7.9 | 37
KJ120 | 10 | 2500 | 75 | 72 | 85 | 138.8 | 0.366 | 18.81 | 50.8 | 7.9 | 37
KJ120 | 10 | 2500 | 80 | 72 | 85 | 138.8 | 0.463 | 23.81 | 64.3 | 7.9 | 37
KJ120 | 10 | 2500 | 85 | 72 | 85 | 138.8 | 0.561 | 28.81 | 77.8 | 7.9 | 37
KJ120 | 10 | 2500 | 90 | 72 | 85 | 138.8 | 0.657 | 33.78 | 91.2 | 7.9 | 37
KJ120 | 10 | 2500 | 80 | 77 | 85 | 152.8 | 0.33 | 18.7 | 50.5 | 7.9 | 37
KJ120 | 10 | 2500 | 85 | 77 | 85 | 152.8 | 0.409 | 23.15 | 62.5 | 7.9 | 37
KJ120 | 10 | 2500 | 90 | 77 | 85 | 152.8 | 0.488 | 27.59 | 74.5 | 7.9 | 37
KJ120 | 10 | 2500 | 65 | 62 | 95 | 113 | 0.411 | 17.19 | 46.4 | 8.7 | 37
KJ120 | 10 | 2500 | 70 | 62 | 95 | 113 | 0.539 | 22.56 | 60.9 | 8.7 | 37
KJ120 | 10 | 2500 | 75 | 62 | 95 | 113 | 0.666 | 27.89 | 75.3 | 8.7 | 37
KJ120 | 10 | 2500 | 80 | 62 | 95 | 113 | 0.795 | 33.26 | 89.8 | 8.7 | 37
KJ120 | 10 | 2500 | 85 | 62 | 95 | 113 | 0.912 | 38.19 | 103.1 | 8.7 | 37
KJ120 | 10 | 2500 | 90 | 62 | 95 | 113 | 1 | 41.85 | 113 | 8.7 | 37
KJ120 | 10 | 2500 | 70 | 67 | 95 | 117 | 0.4 | 17.33 | 46.8 | 8.9 | 37
KJ120 | 10 | 2500 | 75 | 67 | 95 | 117 | 0.52 | 22.52 | 60.8 | 8.9 | 37
KJ120 | 10 | 2500 | 80 | 67 | 95 | 117 | 0.64 | 27.74 | 74.9 | 8.9 | 37
KJ120 | 10 | 2500 | 85 | 67 | 95 | 117 | 0.769 | 33.33 | 90 | 8.9 | 37
KJ120 | 10 | 2500 | 90 | 67 | 95 | 117 | 0.899 | 38.96 | 105.2 | 8.9 | 37
KJ120 | 10 | 2500 | 75 | 72 | 95 | 132.1 | 0.351 | 17.19 | 46.4 | 8.9 | 37
KJ120 | 10 | 2500 | 80 | 72 | 95 | 132.1 | 0.454 | 22.22 | 60 | 8.9 | 37
KJ120 | 10 | 2500 | 85 | 72 | 95 | 132.1 | 0.558 | 27.3 | 73.7 | 8.9 | 37
KJ120 | 10 | 2500 | 90 | 72 | 95 | 132.1 | 0.662 | 32.37 | 87.4 | 8.9 | 37
KJ120 | 10 | 2500 | 80 | 77 | 95 | 147.2 | 0.307 | 16.74 | 45.2 | 8.9 | 37
KJ120 | 10 | 2500 | 85 | 77 | 95 | 147.2 | 0.39 | 21.26 | 57.4 | 8.9 | 37
KJ120 | 10 | 2500 | 90 | 77 | 95 | 147.2 | 0.473 | 25.78 | 69.6 | 8.9 | 37
KJ120 | 10 | 2500 | 65 | 62 | 105 | 107.1 | 0.388 | 15.41 | 41.6 | 10 | 37
KJ120 | 10 | 2500 | 70 | 62 | 105 | 107.1 | 0.524 | 20.78 | 56.1 | 10 | 37
KJ120 | 10 | 2500 | 75 | 62 | 105 | 107.1 | 0.659 | 26.15 | 70.6 | 10 | 37
KJ120 | 10 | 2500 | 80 | 62 | 105 | 107.1 | 0.795 | 31.52 | 85.1 | 10 | 37
KJ120 | 10 | 2500 | 85 | 62 | 105 | 107.1 | 0.906 | 35.93 | 97 | 10 | 37
KJ120 | 10 | 2500 | 90 | 62 | 105 | 107.1 | 1 | 39.67 | 107.1 | 10 | 37
KJ120 | 10 | 2500 | 70 | 67 | 105 | 110.2 | 0.387 | 15.78 | 42.6 | 10.1 | 37
KJ120 | 10 | 2500 | 75 | 67 | 105 | 110.2 | 0.515 | 21 | 56.7 | 10.1 | 37
KJ120 | 10 | 2500 | 80 | 67 | 105 | 110.2 | 0.643 | 26.26 | 70.9 | 10.1 | 37
KJ120 | 10 | 2500 | 85 | 67 | 105 | 110.2 | 0.783 | 31.96 | 86.3 | 10.1 | 37
KJ120 | 10 | 2500 | 90 | 67 | 105 | 110.2 | 0.923 | 37.67 | 101.7 | 10.1 | 37
KJ120 | 10 | 2500 | 75 | 72 | 105 | 123.6 | 0.347 | 15.89 | 42.9 | 10.2 | 37
KJ120 | 10 | 2500 | 80 | 72 | 105 | 123.6 | 0.459 | 21 | 56.7 | 10.2 | 37
KJ120 | 10 | 2500 | 85 | 72 | 105 | 123.6 | 0.57 | 26.07 | 70.4 | 10.2 | 37
KJ120 | 10 | 2500 | 90 | 72 | 105 | 123.6 | 0.681 | 31.19 | 84.2 | 10.2 | 37
KJ120 | 10 | 2500 | 80 | 77 | 105 | 137.1 | 0.31 | 15.74 | 42.5 | 10.2 | 37
KJ120 | 10 | 2500 | 85 | 77 | 105 | 137.1 | 0.398 | 20.22 | 54.6 | 10.2 | 37
KJ120 | 10 | 2500 | 90 | 77 | 105 | 137.1 | 0.487 | 24.7 | 66.7 | 10.2 | 37
KJ120 | 10 | 2500 | 65 | 62 | 115 | 101.2 | 0.363 | 13.59 | 36.7 | 11.3 | 38
KJ120 | 10 | 2500 | 70 | 62 | 115 | 101.2 | 0.507 | 19 | 51.3 | 11.3 | 38
KJ120 | 10 | 2500 | 75 | 62 | 115 | 101.2 | 0.65 | 24.37 | 65.8 | 11.3 | 38
KJ120 | 10 | 2500 | 80 | 62 | 115 | 101.2 | 0.793 | 29.74 | 80.3 | 11.3 | 38
KJ120 | 10 | 2500 | 85 | 62 | 115 | 101.2 | 0.898 | 33.67 | 90.9 | 11.3 | 38
KJ120 | 10 | 2500 | 90 | 62 | 115 | 101.2 | 1 | 37.48 | 101.2 | 11.3 | 38
KJ120 | 10 | 2500 | 70 | 67 | 115 | 103.3 | 0.372 | 14.22 | 38.4 | 11.3 | 38
KJ120 | 10 | 2500 | 75 | 67 | 115 | 103.3 | 0.509 | 19.48 | 52.6 | 11.3 | 38
KJ120 | 10 | 2500 | 80 | 67 | 115 | 103.3 | 0.647 | 24.74 | 66.8 | 11.3 | 38
KJ120 | 10 | 2500 | 85 | 67 | 115 | 103.3 | 0.799 | 30.56 | 82.5 | 11.3 | 38
KJ120 | 10 | 2500 | 90 | 67 | 115 | 103.3 | 0.952 | 36.41 | 98.3 | 11.3 | 38
KJ120 | 10 | 2500 | 75 | 72 | 115 | 115.2 | 0.342 | 14.59 | 39.4 | 11.5 | 38
KJ120 | 10 | 2500 | 80 | 72 | 115 | 115.2 | 0.463 | 19.74 | 53.3 | 11.5 | 38
KJ120 | 10 | 2500 | 85 | 72 | 115 | 115.2 | 0.583 | 24.89 | 67.2 | 11.5 | 38
KJ120 | 10 | 2500 | 90 | 72 | 115 | 115.2 | 0.703 | 30 | 81 | 11.5 | 38
KJ120 | 10 | 2500 | 80 | 77 | 115 | 127 | 0.313 | 14.74 | 39.8 | 11.6 | 38
KJ120 | 10 | 2500 | 85 | 77 | 115 | 127 | 0.408 | 19.19 | 51.8 | 11.6 | 38
KJ120 | 10 | 2500 | 90 | 77 | 115 | 127 | 0.502 | 23.63 | 63.8 | 11.6 | 38
KJ120 | 10 | 2500 | 65 | 62 | 125 | 95.4 | 0.333 | 11.78 | 31.8 | 12.6 | 38
KJ120 | 10 | 2500 | 70 | 62 | 125 | 95.4 | 0.486 | 17.19 | 46.4 | 12.6 | 38
KJ120 | 10 | 2500 | 75 | 62 | 125 | 95.4 | 0.639 | 22.59 | 61 | 12.6 | 38
KJ120 | 10 | 2500 | 80 | 62 | 125 | 95.4 | 0.792 | 28 | 75.6 | 12.6 | 38
KJ120 | 10 | 2500 | 85 | 62 | 125 | 95.4 | 0.888 | 31.37 | 84.7 | 12.6 | 38
KJ120 | 10 | 2500 | 90 | 62 | 125 | 95.4 | 0.984 | 34.78 | 93.9 | 12.6 | 38
KJ120 | 10 | 2500 | 70 | 67 | 125 | 96.5 | 0.354 | 12.67 | 34.2 | 12.6 | 38
KJ120 | 10 | 2500 | 75 | 67 | 125 | 96.5 | 0.503 | 17.96 | 48.5 | 12.6 | 38
KJ120 | 10 | 2500 | 80 | 67 | 125 | 96.5 | 0.651 | 23.26 | 62.8 | 12.6 | 38
KJ120 | 10 | 2500 | 85 | 67 | 125 | 96.5 | 0.817 | 29.19 | 78.8 | 12.6 | 38
KJ120 | 10 | 2500 | 90 | 67 | 125 | 96.5 | 0.969 | 34.63 | 93.5 | 12.6 | 38
KJ120 | 10 | 2500 | 75 | 72 | 125 | 106.7 | 0.337 | 13.33 | 36 | 12.8 | 38
KJ120 | 10 | 2500 | 80 | 72 | 125 | 106.7 | 0.468 | 18.48 | 49.9 | 12.8 | 38
KJ120 | 10 | 2500 | 85 | 72 | 125 | 106.7 | 0.599 | 23.67 | 63.9 | 12.8 | 38
KJ120 | 10 | 2500 | 90 | 72 | 125 | 106.7 | 0.729 | 28.81 | 77.8 | 12.8 | 38
KJ120 | 10 | 2500 | 80 | 77 | 125 | 116.9 | 0.317 | 13.74 | 37.1 | 13 | 38
KJ120 | 10 | 2500 | 85 | 77 | 125 | 116.9 | 0.419 | 18.15 | 49 | 13 | 38
KJ120 | 10 | 2500 | 90 | 77 | 125 | 116.9 | 0.521 | 22.56 | 60.9 | 13 | 38
KJ120 | 10 | 3000 | 65 | 57 | 75 | 118.4 | 0.582 | 21.27 | 68.9 | 6.8 | 37
KJ120 | 10 | 3000 | 70 | 57 | 75 | 118.4 | 0.721 | 26.36 | 85.4 | 6.8 | 37
KJ120 | 10 | 3000 | 75 | 57 | 75 | 118.4 | 0.861 | 31.45 | 101.9 | 6.8 | 37
KJ120 | 10 | 3000 | 80 | 57 | 75 | 118.4 | 0.999 | 36.51 | 118.3 | 6.8 | 37
KJ120 | 10 | 3000 | 85 | 57 | 75 | 118.4 | 1 | 36.54 | 118.4 | 6.8 | 37
KJ120 | 10 | 3000 | 90 | 57 | 75 | 118.4 | 1 | 36.54 | 118.4 | 6.8 | 37
KJ120 | 10 | 3000 | 65 | 62 | 75 | 127 | 0.427 | 16.73 | 54.2 | 6.8 | 37
KJ120 | 10 | 3000 | 70 | 62 | 75 | 127 | 0.554 | 21.7 | 70.3 | 6.8 | 37
KJ120 | 10 | 3000 | 75 | 62 | 75 | 127 | 0.671 | 26.3 | 85.2 | 6.8 | 37
KJ120 | 10 | 3000 | 80 | 62 | 75 | 127 | 0.808 | 31.67 | 102.6 | 6.8 | 37
KJ120 | 10 | 3000 | 85 | 62 | 75 | 127 | 0.916 | 35.9 | 116.3 | 6.8 | 37
KJ120 | 10 | 3000 | 90 | 62 | 75 | 127 | 0.931 | 36.51 | 118.3 | 6.8 | 37
KJ120 | 10 | 3000 | 70 | 67 | 75 | 135.6 | 0.408 | 17.07 | 55.3 | 6.9 | 37
KJ120 | 10 | 3000 | 75 | 67 | 75 | 135.6 | 0.524 | 21.91 | 71 | 6.9 | 37
KJ120 | 10 | 3000 | 80 | 67 | 75 | 135.6 | 0.641 | 26.82 | 86.9 | 6.9 | 37
KJ120 | 10 | 3000 | 85 | 67 | 75 | 135.6 | 0.756 | 31.64 | 102.5 | 6.9 | 37
KJ120 | 10 | 3000 | 90 | 67 | 75 | 135.6 | 0.871 | 36.45 | 118.1 | 6.9 | 37
KJ120 | 10 | 3000 | 75 | 72 | 75 | 148.2 | 0.376 | 17.19 | 55.7 | 7 | 37
KJ120 | 10 | 3000 | 80 | 72 | 75 | 148.2 | 0.48 | 21.98 | 71.2 | 7 | 37
KJ120 | 10 | 3000 | 85 | 72 | 75 | 148.2 | 0.584 | 26.73 | 86.6 | 7 | 37
KJ120 | 10 | 3000 | 90 | 72 | 75 | 148.2 | 0.689 | 31.51 | 102.1 | 7 | 37
KJ120 | 10 | 3000 | 80 | 77 | 75 | 160.8 | 0.345 | 17.1 | 55.4 | 7 | 37
KJ120 | 10 | 3000 | 85 | 77 | 75 | 160.8 | 0.44 | 21.85 | 70.8 | 7 | 37
KJ120 | 10 | 3000 | 90 | 77 | 75 | 160.8 | 0.535 | 26.57 | 86.1 | 7 | 37
KJ120 | 10 | 3000 | 65 | 57 | 85 | 115.6 | 0.569 | 20.31 | 65.8 | 7.7 | 37
KJ120 | 10 | 3000 | 70 | 57 | 85 | 115.6 | 0.715 | 25.49 | 82.6 | 7.7 | 37
KJ120 | 10 | 3000 | 75 | 57 | 85 | 115.6 | 0.86 | 30.68 | 99.4 | 7.7 | 37
KJ120 | 10 | 3000 | 80 | 57 | 85 | 115.6 | 1 | 35.68 | 115.6 | 7.7 | 37
KJ120 | 10 | 3000 | 85 | 57 | 85 | 115.6 | 1 | 35.68 | 115.6 | 7.7 | 37
KJ120 | 10 | 3000 | 90 | 57 | 85 | 115.6 | 1 | 35.68 | 115.6 | 7.7 | 37
KJ120 | 10 | 3000 | 65 | 62 | 85 | 121.7 | 0.415 | 15.59 | 50.5 | 7.8 | 37
KJ120 | 10 | 3000 | 70 | 62 | 85 | 121.7 | 0.55 | 20.65 | 66.9 | 7.8 | 37
KJ120 | 10 | 3000 | 75 | 62 | 85 | 121.7 | 0.68 | 25.52 | 82.7 | 7.8 | 37
KJ120 | 10 | 3000 | 80 | 62 | 85 | 121.7 | 0.819 | 30.77 | 99.7 | 7.8 | 37
KJ120 | 10 | 3000 | 85 | 62 | 85 | 121.7 | 0.923 | 34.66 | 112.3 | 7.8 | 37
KJ120 | 10 | 3000 | 90 | 62 | 85 | 121.7 | 0.947 | 35.59 | 115.3 | 7.8 | 37
KJ120 | 10 | 3000 | 70 | 67 | 85 | 127.9 | 0.4 | 15.8 | 51.2 | 7.9 | 37
KJ120 | 10 | 3000 | 75 | 67 | 85 | 127.9 | 0.525 | 20.74 | 67.2 | 7.9 | 37
KJ120 | 10 | 3000 | 80 | 67 | 85 | 127.9 | 0.651 | 25.71 | 83.3 | 7.9 | 37
KJ120 | 10 | 3000 | 85 | 67 | 85 | 127.9 | 0.774 | 30.56 | 99 | 7.9 | 37
KJ120 | 10 | 3000 | 90 | 67 | 85 | 127.9 | 0.897 | 35.4 | 114.7 | 7.9 | 37
KJ120 | 10 | 3000 | 75 | 72 | 85 | 140.9 | 0.363 | 15.8 | 51.2 | 7.9 | 37
KJ120 | 10 | 3000 | 80 | 72 | 85 | 140.9 | 0.475 | 20.65 | 66.9 | 7.9 | 37
KJ120 | 10 | 3000 | 85 | 72 | 85 | 140.9 | 0.586 | 25.49 | 82.6 | 7.9 | 37
KJ120 | 10 | 3000 | 90 | 72 | 85 | 140.9 | 0.698 | 30.34 | 98.3 | 7.9 | 37
KJ120 | 10 | 3000 | 80 | 77 | 85 | 153.9 | 0.328 | 15.59 | 50.5 | 8 | 37
KJ120 | 10 | 3000 | 85 | 77 | 85 | 153.9 | 0.431 | 20.46 | 66.3 | 8 | 37
KJ120 | 10 | 3000 | 90 | 77 | 85 | 153.9 | 0.533 | 25.31 | 82 | 8 | 37
KJ120 | 10 | 3000 | 65 | 57 | 95 | 112.8 | 0.556 | 19.35 | 62.7 | 8.6 | 37
KJ120 | 10 | 3000 | 70 | 57 | 95 | 112.8 | 0.707 | 24.63 | 79.8 | 8.6 | 37
KJ120 | 10 | 3000 | 75 | 57 | 95 | 112.8 | 0.859 | 29.91 | 96.9 | 8.6 | 37
KJ120 | 10 | 3000 | 80 | 57 | 95 | 112.8 | 1 | 34.81 | 112.8 | 8.6 | 37
KJ120 | 10 | 3000 | 85 | 57 | 95 | 112.8 | 1 | 34.81 | 112.8 | 8.6 | 37
KJ120 | 10 | 3000 | 90 | 57 | 95 | 112.8 | 1 | 34.81 | 112.8 | 8.6 | 37
KJ120 | 10 | 3000 | 65 | 62 | 95 | 116.5 | 0.401 | 14.41 | 46.7 | 8.7 | 37
KJ120 | 10 | 3000 | 70 | 62 | 95 | 116.5 | 0.545 | 19.6 | 63.5 | 8.7 | 37
KJ120 | 10 | 3000 | 75 | 62 | 95 | 116.5 | 0.688 | 24.75 | 80.2 | 8.7 | 37
KJ120 | 10 | 3000 | 80 | 62 | 95 | 116.5 | 0.832 | 29.91 | 96.9 | 8.7 | 37
KJ120 | 10 | 3000 | 85 | 62 | 95 | 116.5 | 0.93 | 33.46 | 108.4 | 8.7 | 37
KJ120 | 10 | 3000 | 90 | 62 | 95 | 116.5 | 0.964 | 34.66 | 112.3 | 8.7 | 37
KJ120 | 10 | 3000 | 70 | 67 | 95 | 120.2 | 0.392 | 14.54 | 47.1 | 8.9 | 37
KJ120 | 10 | 3000 | 75 | 67 | 95 | 120.2 | 0.527 | 19.57 | 63.4 | 8.9 | 37
KJ120 | 10 | 3000 | 80 | 67 | 95 | 120.2 | 0.664 | 24.63 | 79.8 | 8.9 | 37
KJ120 | 10 | 3000 | 85 | 67 | 95 | 120.2 | 0.795 | 29.48 | 95.5 | 8.9 | 37
KJ120 | 10 | 3000 | 90 | 67 | 95 | 120.2 | 0.925 | 34.32 | 111.2 | 8.9 | 37
KJ120 | 10 | 3000 | 75 | 72 | 95 | 133.6 | 0.35 | 14.41 | 46.7 | 8.9 | 37
KJ120 | 10 | 3000 | 80 | 72 | 95 | 133.6 | 0.469 | 19.35 | 62.7 | 8.9 | 37
KJ120 | 10 | 3000 | 85 | 72 | 95 | 133.6 | 0.588 | 24.26 | 78.6 | 8.9 | 37
KJ120 | 10 | 3000 | 90 | 72 | 95 | 133.6 | 0.708 | 29.2 | 94.6 | 8.9 | 37
KJ120 | 10 | 3000 | 80 | 77 | 95 | 146.9 | 0.31 | 14.07 | 45.6 | 8.9 | 37
KJ120 | 10 | 3000 | 85 | 77 | 95 | 146.9 | 0.42 | 19.04 | 61.7 | 8.9 | 37
KJ120 | 10 | 3000 | 90 | 77 | 95 | 146.9 | 0.53 | 24.04 | 77.9 | 8.9 | 37
KJ120 | 10 | 3000 | 65 | 57 | 105 | 107.5 | 0.534 | 17.72 | 57.4 | 9.9 | 37
KJ120 | 10 | 3000 | 70 | 57 | 105 | 107.5 | 0.694 | 23.02 | 74.6 | 9.9 | 37
KJ120 | 10 | 3000 | 75 | 57 | 105 | 107.5 | 0.853 | 28.3 | 91.7 | 9.9 | 37
KJ120 | 10 | 3000 | 80 | 57 | 105 | 107.5 | 1 | 33.18 | 107.5 | 9.9 | 37
KJ120 | 10 | 3000 | 85 | 57 | 105 | 107.5 | 1 | 33.18 | 107.5 | 9.9 | 37
KJ120 | 10 | 3000 | 90 | 57 | 105 | 107.5 | 1 | 33.18 | 107.5 | 9.9 | 37
KJ120 | 10 | 3000 | 65 | 62 | 105 | 110.4 | 0.38 | 12.93 | 41.9 | 10 | 37
KJ120 | 10 | 3000 | 70 | 62 | 105 | 110.4 | 0.532 | 18.12 | 58.7 | 10 | 37
KJ120 | 10 | 3000 | 75 | 62 | 105 | 110.4 | 0.684 | 23.3 | 75.5 | 10 | 37
KJ120 | 10 | 3000 | 80 | 62 | 105 | 110.4 | 0.836 | 28.49 | 92.3 | 10 | 37
KJ120 | 10 | 3000 | 85 | 62 | 105 | 110.4 | 0.928 | 31.6 | 102.4 | 10 | 37
KJ120 | 10 | 3000 | 90 | 62 | 105 | 110.4 | 0.972 | 33.12 | 107.3 | 10 | 37
KJ120 | 10 | 3000 | 70 | 67 | 105 | 113.2 | 0.379 | 13.24 | 42.9 | 10.1 | 37
KJ120 | 10 | 3000 | 75 | 67 | 105 | 113.2 | 0.524 | 18.3 | 59.3 | 10.1 | 37
KJ120 | 10 | 3000 | 80 | 67 | 105 | 113.2 | 0.669 | 23.36 | 75.7 | 10.1 | 37
KJ120 | 10 | 3000 | 85 | 67 | 105 | 113.2 | 0.807 | 28.18 | 91.3 | 10.1 | 37
KJ120 | 10 | 3000 | 90 | 67 | 105 | 113.2 | 0.944 | 32.99 | 106.9 | 10.1 | 37
KJ120 | 10 | 3000 | 75 | 72 | 105 | 124.9 | 0.344 | 13.27 | 43 | 10.2 | 37
KJ120 | 10 | 3000 | 80 | 72 | 105 | 124.9 | 0.473 | 18.24 | 59.1 | 10.2 | 37
KJ120 | 10 | 3000 | 85 | 72 | 105 | 124.9 | 0.601 | 23.18 | 75.1 | 10.2 | 37
KJ120 | 10 | 3000 | 90 | 72 | 105 | 124.9 | 0.729 | 28.12 | 91.1 | 10.2 | 37
KJ120 | 10 | 3000 | 80 | 77 | 105 | 136.5 | 0.311 | 13.12 | 42.5 | 10.3 | 37
KJ120 | 10 | 3000 | 85 | 77 | 105 | 136.5 | 0.432 | 18.18 | 58.9 | 10.3 | 37
KJ120 | 10 | 3000 | 90 | 77 | 105 | 136.5 | 0.552 | 23.24 | 75.3 | 10.3 | 37
KJ120 | 10 | 3000 | 65 | 57 | 115 | 102.3 | 0.509 | 16.08 | 52.1 | 11.3 | 38
KJ120 | 10 | 3000 | 70 | 57 | 115 | 102.3 | 0.678 | 21.42 | 69.4 | 11.3 | 38
KJ120 | 10 | 3000 | 75 | 57 | 115 | 102.3 | 0.847 | 26.73 | 86.6 | 11.3 | 38
KJ120 | 10 | 3000 | 80 | 57 | 115 | 102.3 | 1 | 31.57 | 102.3 | 11.3 | 38
KJ120 | 10 | 3000 | 85 | 57 | 115 | 102.3 | 1 | 31.57 | 102.3 | 11.3 | 38
KJ120 | 10 | 3000 | 90 | 57 | 115 | 102.3 | 1 | 31.57 | 102.3 | 11.3 | 38
KJ120 | 10 | 3000 | 65 | 62 | 115 | 104.3 | 0.356 | 11.45 | 37.1 | 11.3 | 38
KJ120 | 10 | 3000 | 70 | 62 | 115 | 104.3 | 0.518 | 16.67 | 54 | 11.3 | 38
KJ120 | 10 | 3000 | 75 | 62 | 115 | 104.3 | 0.68 | 21.88 | 70.9 | 11.3 | 38
KJ120 | 10 | 3000 | 80 | 62 | 115 | 104.3 | 0.841 | 27.07 | 87.7 | 11.3 | 38
KJ120 | 10 | 3000 | 85 | 62 | 115 | 104.3 | 0.923 | 29.72 | 96.3 | 11.3 | 38
KJ120 | 10 | 3000 | 90 | 62 | 115 | 104.3 | 0.978 | 31.48 | 102 | 11.3 | 38
KJ120 | 10 | 3000 | 70 | 67 | 115 | 106.3 | 0.363 | 11.91 | 38.6 | 11.4 | 38
KJ120 | 10 | 3000 | 75 | 67 | 115 | 106.3 | 0.518 | 17.01 | 55.1 | 11.4 | 38
KJ120 | 10 | 3000 | 80 | 67 | 115 | 106.3 | 0.674 | 22.1 | 71.6 | 11.4 | 38
KJ120 | 10 | 3000 | 85 | 67 | 115 | 106.3 | 0.819 | 26.88 | 87.1 | 11.4 | 38
KJ120 | 10 | 3000 | 90 | 67 | 115 | 106.3 | 0.965 | 31.67 | 102.6 | 11.4 | 38
KJ120 | 10 | 3000 | 75 | 72 | 115 | 116.2 | 0.339 | 12.16 | 39.4 | 11.5 | 38
KJ120 | 10 | 3000 | 80 | 72 | 115 | 116.2 | 0.478 | 17.13 | 55.5 | 11.5 | 38
KJ120 | 10 | 3000 | 85 | 72 | 115 | 116.2 | 0.616 | 22.1 | 71.6 | 11.5 | 38
KJ120 | 10 | 3000 | 90 | 72 | 115 | 116.2 | 0.755 | 27.07 | 87.7 | 11.5 | 38
KJ120 | 10 | 3000 | 80 | 77 | 115 | 126 | 0.312 | 12.13 | 39.3 | 11.6 | 38
KJ120 | 10 | 3000 | 85 | 77 | 115 | 126 | 0.445 | 17.31 | 56.1 | 11.6 | 38
KJ120 | 10 | 3000 | 90 | 77 | 115 | 126 | 0.578 | 22.47 | 72.8 | 11.6 | 38
KJ120 | 10 | 3000 | 65 | 57 | 125 | 97.1 | 0.482 | 14.44 | 46.8 | 12.6 | 38
KJ120 | 10 | 3000 | 70 | 57 | 125 | 97.1 | 0.66 | 19.78 | 64.1 | 12.6 | 38
KJ120 | 10 | 3000 | 75 | 57 | 125 | 97.1 | 0.839 | 25.15 | 81.5 | 12.6 | 38
KJ120 | 10 | 3000 | 80 | 57 | 125 | 97.1 | 0.994 | 29.78 | 96.5 | 12.6 | 38
KJ120 | 10 | 3000 | 85 | 57 | 125 | 97.1 | 0.994 | 29.78 | 96.5 | 12.6 | 38
KJ120 | 10 | 3000 | 90 | 57 | 125 | 97.1 | 0.994 | 29.78 | 96.5 | 12.6 | 38
KJ120 | 10 | 3000 | 65 | 62 | 125 | 98.2 | 0.329 | 9.97 | 32.3 | 12.6 | 38
KJ120 | 10 | 3000 | 70 | 62 | 125 | 98.2 | 0.502 | 15.22 | 49.3 | 12.6 | 38
KJ120 | 10 | 3000 | 75 | 62 | 125 | 98.2 | 0.674 | 20.43 | 66.2 | 12.6 | 38
KJ120 | 10 | 3000 | 80 | 62 | 125 | 98.2 | 0.846 | 25.65 | 83.1 | 12.6 | 38
KJ120 | 10 | 3000 | 85 | 62 | 125 | 98.2 | 0.92 | 27.87 | 90.3 | 12.6 | 38
KJ120 | 10 | 3000 | 90 | 62 | 125 | 98.2 | 0.981 | 29.72 | 96.3 | 12.6 | 38
KJ120 | 10 | 3000 | 70 | 67 | 125 | 99.3 | 0.346 | 10.62 | 34.4 | 12.6 | 38
KJ120 | 10 | 3000 | 75 | 67 | 125 | 99.3 | 0.513 | 15.71 | 50.9 | 12.6 | 38
KJ120 | 10 | 3000 | 80 | 67 | 125 | 99.3 | 0.68 | 20.83 | 67.5 | 12.6 | 38
KJ120 | 10 | 3000 | 85 | 67 | 125 | 99.3 | 0.835 | 25.59 | 82.9 | 12.6 | 38
KJ120 | 10 | 3000 | 90 | 67 | 125 | 99.3 | 0.967 | 29.63 | 96 | 12.6 | 38
KJ120 | 10 | 3000 | 75 | 72 | 125 | 107.4 | 0.332 | 11.02 | 35.7 | 12.8 | 38
KJ120 | 10 | 3000 | 80 | 72 | 125 | 107.4 | 0.483 | 16.02 | 51.9 | 12.8 | 38
KJ120 | 10 | 3000 | 85 | 72 | 125 | 107.4 | 0.634 | 21.02 | 68.1 | 12.8 | 38
KJ120 | 10 | 3000 | 90 | 72 | 125 | 107.4 | 0.784 | 25.99 | 84.2 | 12.8 | 38
KJ120 | 10 | 3000 | 80 | 77 | 125 | 115.6 | 0.313 | 11.17 | 36.2 | 13 | 38
KJ120 | 10 | 3000 | 85 | 77 | 125 | 115.6 | 0.46 | 16.42 | 53.2 | 13 | 38
KJ120 | 10 | 3000 | 90 | 77 | 125 | 115.6 | 0.607 | 21.67 | 70.2 | 13 | 38
KJ120 | 10 | 3500 | 65 | 57 | 75 | 125 | 0.574 | 18.97 | 71.7 | 6.8 | 37
KJ120 | 10 | 3500 | 70 | 57 | 75 | 125 | 0.729 | 24.1 | 91.1 | 6.8 | 37
KJ120 | 10 | 3500 | 75 | 57 | 75 | 125 | 0.884 | 29.23 | 110.5 | 6.8 | 37
KJ120 | 10 | 3500 | 80 | 57 | 75 | 125 | 1 | 33.07 | 125 | 6.8 | 37
KJ120 | 10 | 3500 | 85 | 57 | 75 | 125 | 1 | 33.07 | 125 | 6.8 | 37
KJ120 | 10 | 3500 | 90 | 57 | 75 | 125 | 1 | 33.07 | 125 | 6.8 | 37
KJ120 | 10 | 3500 | 65 | 62 | 75 | 131.8 | 0.415 | 14.47 | 54.7 | 6.9 | 37
KJ120 | 10 | 3500 | 70 | 62 | 75 | 131.8 | 0.558 | 19.44 | 73.5 | 6.9 | 37
KJ120 | 10 | 3500 | 75 | 62 | 75 | 131.8 | 0.693 | 24.18 | 91.4 | 6.9 | 37
KJ120 | 10 | 3500 | 80 | 62 | 75 | 131.8 | 0.844 | 29.42 | 111.2 | 6.9 | 37
KJ120 | 10 | 3500 | 85 | 62 | 75 | 131.8 | 0.933 | 32.54 | 123 | 6.9 | 37
KJ120 | 10 | 3500 | 90 | 62 | 75 | 131.8 | 0.948 | 33.04 | 124.9 | 6.9 | 37
KJ120 | 10 | 3500 | 70 | 67 | 75 | 138.6 | 0.403 | 14.79 | 55.9 | 6.9 | 37
KJ120 | 10 | 3500 | 75 | 67 | 75 | 138.6 | 0.535 | 19.6 | 74.1 | 6.9 | 37
KJ120 | 10 | 3500 | 80 | 67 | 75 | 138.6 | 0.667 | 24.47 | 92.5 | 6.9 | 37
KJ120 | 10 | 3500 | 85 | 67 | 75 | 138.6 | 0.786 | 28.84 | 109 | 6.9 | 37
KJ120 | 10 | 3500 | 90 | 67 | 75 | 138.6 | 0.9 | 33.02 | 124.8 | 6.9 | 37
KJ120 | 10 | 3500 | 75 | 72 | 75 | 150.9 | 0.371 | 14.81 | 56 | 7 | 37
KJ120 | 10 | 3500 | 80 | 72 | 75 | 150.9 | 0.489 | 19.52 | 73.8 | 7 | 37
KJ120 | 10 | 3500 | 85 | 72 | 75 | 150.9 | 0.606 | 24.21 | 91.5 | 7 | 37
KJ120 | 10 | 3500 | 90 | 72 | 75 | 150.9 | 0.724 | 28.89 | 109.2 | 7 | 37
KJ120 | 10 | 3500 | 80 | 77 | 75 | 163.3 | 0.337 | 14.58 | 55.1 | 7 | 37
KJ120 | 10 | 3500 | 85 | 77 | 75 | 163.3 | 0.453 | 19.58 | 74 | 7 | 37
KJ120 | 10 | 3500 | 90 | 77 | 75 | 163.3 | 0.569 | 24.58 | 92.9 | 7 | 37
KJ120 | 10 | 3500 | 65 | 57 | 85 | 120.8 | 0.567 | 18.12 | 68.5 | 7.7 | 37
KJ120 | 10 | 3500 | 70 | 57 | 85 | 120.8 | 0.727 | 23.23 | 87.8 | 7.7 | 37
KJ120 | 10 | 3500 | 75 | 57 | 85 | 120.8 | 0.887 | 28.36 | 107.2 | 7.7 | 37
KJ120 | 10 | 3500 | 80 | 57 | 85 | 120.8 | 1 | 31.96 | 120.8 | 7.7 | 37
KJ120 | 10 | 3500 | 85 | 57 | 85 | 120.8 | 1 | 31.96 | 120.8 | 7.7 | 37
KJ120 | 10 | 3500 | 90 | 57 | 85 | 120.8 | 1 | 31.96 | 120.8 | 7.7 | 37
KJ120 | 10 | 3500 | 65 | 62 | 85 | 125.9 | 0.404 | 13.47 | 50.9 | 7.8 | 37
KJ120 | 10 | 3500 | 70 | 62 | 85 | 125.9 | 0.554 | 18.47 | 69.8 | 7.8 | 37
KJ120 | 10 | 3500 | 75 | 62 | 85 | 125.9 | 0.701 | 23.33 | 88.2 | 7.8 | 37
KJ120 | 10 | 3500 | 80 | 62 | 85 | 125.9 | 0.855 | 28.47 | 107.6 | 7.8 | 37
KJ120 | 10 | 3500 | 85 | 62 | 85 | 125.9 | 0.94 | 31.32 | 118.4 | 7.8 | 37
KJ120 | 10 | 3500 | 90 | 62 | 85 | 125.9 | 0.958 | 31.9 | 120.6 | 7.8 | 37
KJ120 | 10 | 3500 | 70 | 67 | 85 | 131 | 0.395 | 13.68 | 51.7 | 7.9 | 37
KJ120 | 10 | 3500 | 75 | 67 | 85 | 131 | 0.535 | 18.54 | 70.1 | 7.9 | 37
KJ120 | 10 | 3500 | 80 | 67 | 85 | 131 | 0.676 | 23.44 | 88.6 | 7.9 | 37
KJ120 | 10 | 3500 | 85 | 67 | 85 | 131 | 0.802 | 27.78 | 105 | 7.9 | 37
KJ120 | 10 | 3500 | 90 | 67 | 85 | 131 | 0.92 | 31.88 | 120.5 | 7.9 | 37
KJ120 | 10 | 3500 | 75 | 72 | 85 | 143 | 0.361 | 13.65 | 51.6 | 7.9 | 37
KJ120 | 10 | 3500 | 80 | 72 | 85 | 143 | 0.486 | 18.39 | 69.5 | 7.9 | 37
KJ120 | 10 | 3500 | 85 | 72 | 85 | 143 | 0.612 | 23.15 | 87.5 | 7.9 | 37
KJ120 | 10 | 3500 | 90 | 72 | 85 | 143 | 0.738 | 27.91 | 105.5 | 7.9 | 37
KJ120 | 10 | 3500 | 80 | 77 | 85 | 154.9 | 0.326 | 13.36 | 50.5 | 8 | 37
KJ120 | 10 | 3500 | 85 | 77 | 85 | 154.9 | 0.453 | 18.54 | 70.1 | 8 | 37
KJ120 | 10 | 3500 | 90 | 77 | 85 | 154.9 | 0.578 | 23.7 | 89.6 | 8 | 37
KJ120 | 10 | 3500 | 65 | 57 | 95 | 116.6 | 0.559 | 17.25 | 65.2 | 8.6 | 37
KJ120 | 10 | 3500 | 70 | 57 | 95 | 116.6 | 0.726 | 22.38 | 84.6 | 8.6 | 37
KJ120 | 10 | 3500 | 75 | 57 | 95 | 116.6 | 0.891 | 27.49 | 103.9 | 8.6 | 37
KJ120 | 10 | 3500 | 80 | 57 | 95 | 116.6 | 1 | 30.85 | 116.6 | 8.6 | 37
KJ120 | 10 | 3500 | 85 | 57 | 95 | 116.6 | 1 | 30.85 | 116.6 | 8.6 | 37
KJ120 | 10 | 3500 | 90 | 57 | 95 | 116.6 | 1 | 30.85 | 116.6 | 8.6 | 37
KJ120 | 10 | 3500 | 65 | 62 | 95 | 120 | 0.392 | 12.43 | 47 | 8.7 | 37
KJ120 | 10 | 3500 | 70 | 62 | 95 | 120 | 0.55 | 17.46 | 66 | 8.7 | 37
KJ120 | 10 | 3500 | 75 | 62 | 95 | 120 | 0.708 | 22.49 | 85 | 8.7 | 37
KJ120 | 10 | 3500 | 80 | 62 | 95 | 120 | 0.867 | 27.51 | 104 | 8.7 | 37
KJ120 | 10 | 3500 | 85 | 62 | 95 | 120 | 0.948 | 30.11 | 113.8 | 8.7 | 37
KJ120 | 10 | 3500 | 90 | 62 | 95 | 120 | 0.969 | 30.77 | 116.3 | 8.7 | 37
KJ120 | 10 | 3500 | 70 | 67 | 95 | 123.4 | 0.385 | 12.57 | 47.5 | 8.8 | 37
KJ120 | 10 | 3500 | 75 | 67 | 95 | 123.4 | 0.535 | 17.46 | 66 | 8.8 | 37
KJ120 | 10 | 3500 | 80 | 67 | 95 | 123.4 | 0.686 | 22.38 | 84.6 | 8.8 | 37
KJ120 | 10 | 3500 | 85 | 67 | 95 | 123.4 | 0.818 | 26.69 | 100.9 | 8.8 | 37
KJ120 | 10 | 3500 | 90 | 67 | 95 | 123.4 | 0.94 | 30.69 | 116 | 8.8 | 37
KJ120 | 10 | 3500 | 75 | 72 | 95 | 135 | 0.349 | 12.46 | 47.1 | 8.9 | 37
KJ120 | 10 | 3500 | 80 | 72 | 95 | 135 | 0.484 | 17.28 | 65.3 | 8.9 | 37
KJ120 | 10 | 3500 | 85 | 72 | 95 | 135 | 0.619 | 22.09 | 83.5 | 8.9 | 37
KJ120 | 10 | 3500 | 90 | 72 | 95 | 135 | 0.753 | 26.9 | 101.7 | 8.9 | 37
KJ120 | 10 | 3500 | 80 | 77 | 95 | 146.6 | 0.314 | 12.17 | 46 | 8.9 | 37
KJ120 | 10 | 3500 | 85 | 77 | 95 | 146.6 | 0.451 | 17.49 | 66.1 | 8.9 | 37
KJ120 | 10 | 3500 | 90 | 77 | 95 | 146.6 | 0.588 | 22.8 | 86.2 | 8.9 | 37
KJ120 | 10 | 3500 | 65 | 57 | 105 | 111 | 0.541 | 15.9 | 60.1 | 9.9 | 37
KJ120 | 10 | 3500 | 70 | 57 | 105 | 111 | 0.717 | 21.06 | 79.6 | 9.9 | 37
KJ120 | 10 | 3500 | 75 | 57 | 105 | 111 | 0.893 | 26.22 | 99.1 | 9.9 | 37
KJ120 | 10 | 3500 | 80 | 57 | 105 | 111 | 1 | 29.37 | 111 | 9.9 | 37
KJ120 | 10 | 3500 | 85 | 57 | 105 | 111 | 1 | 29.37 | 111 | 9.9 | 37
KJ120 | 10 | 3500 | 90 | 57 | 105 | 111 | 1 | 29.37 | 111 | 9.9 | 37
KJ120 | 10 | 3500 | 65 | 62 | 105 | 113.7 | 0.372 | 11.19 | 42.3 | 10 | 37
KJ120 | 10 | 3500 | 70 | 62 | 105 | 113.7 | 0.54 | 16.24 | 61.4 | 10 | 37
KJ120 | 10 | 3500 | 75 | 62 | 105 | 113.7 | 0.708 | 21.3 | 80.5 | 10 | 37
KJ120 | 10 | 3500 | 80 | 62 | 105 | 113.7 | 0.875 | 26.32 | 99.5 | 10 | 37
KJ120 | 10 | 3500 | 85 | 62 | 105 | 113.7 | 0.948 | 28.52 | 107.8 | 10 | 37
KJ120 | 10 | 3500 | 90 | 62 | 105 | 113.7 | 0.976 | 29.37 | 111 | 10 | 37
KJ120 | 10 | 3500 | 70 | 67 | 105 | 116.3 | 0.371 | 11.4 | 43.1 | 10.1 | 37
KJ120 | 10 | 3500 | 75 | 67 | 105 | 116.3 | 0.531 | 16.35 | 61.8 | 10.1 | 37
KJ120 | 10 | 3500 | 80 | 67 | 105 | 116.3 | 0.692 | 21.3 | 80.5 | 10.1 | 37
KJ120 | 10 | 3500 | 85 | 67 | 105 | 116.3 | 0.828 | 25.48 | 96.3 | 10.1 | 37
KJ120 | 10 | 3500 | 90 | 67 | 105 | 116.3 | 0.954 | 29.37 | 111 | 10.1 | 37
KJ120 | 10 | 3500 | 75 | 72 | 105 | 126.1 | 0.343 | 11.43 | 43.2 | 10.2 | 37
KJ120 | 10 | 3500 | 80 | 72 | 105 | 126.1 | 0.488 | 16.27 | 61.5 | 10.2 | 37
KJ120 | 10 | 3500 | 85 | 72 | 105 | 126.1 | 0.633 | 21.11 | 79.8 | 10.2 | 37
KJ120 | 10 | 3500 | 90 | 72 | 105 | 126.1 | 0.777 | 25.93 | 98 | 10.2 | 37
KJ120 | 10 | 3500 | 80 | 77 | 105 | 135.8 | 0.313 | 11.24 | 42.5 | 10.3 | 37
KJ120 | 10 | 3500 | 85 | 77 | 105 | 135.8 | 0.465 | 16.72 | 63.2 | 10.3 | 37
KJ120 | 10 | 3500 | 90 | 77 | 105 | 135.8 | 0.619 | 22.22 | 84 | 10.3 | 37
KJ120 | 10 | 3500 | 65 | 57 | 115 | 105.5 | 0.521 | 14.55 | 55 | 11.3 | 38
KJ120 | 10 | 3500 | 70 | 57 | 115 | 105.5 | 0.707 | 19.74 | 74.6 | 11.3 | 38
KJ120 | 10 | 3500 | 75 | 57 | 115 | 105.5 | 0.893 | 24.92 | 94.2 | 11.3 | 38
KJ120 | 10 | 3500 | 80 | 57 | 115 | 105.5 | 1 | 27.91 | 105.5 | 11.3 | 38
KJ120 | 10 | 3500 | 85 | 57 | 115 | 105.5 | 1 | 27.91 | 105.5 | 11.3 | 38
KJ120 | 10 | 3500 | 90 | 57 | 115 | 105.5 | 1 | 27.91 | 105.5 | 11.3 | 38
KJ120 | 10 | 3500 | 65 | 62 | 115 | 107.3 | 0.349 | 9.92 | 37.5 | 11.3 | 38
KJ120 | 10 | 3500 | 70 | 62 | 115 | 107.3 | 0.528 | 15 | 56.7 | 11.3 | 38
KJ120 | 10 | 3500 | 75 | 62 | 115 | 107.3 | 0.707 | 20.08 | 75.9 | 11.3 | 38
KJ120 | 10 | 3500 | 80 | 62 | 115 | 107.3 | 0.886 | 25.16 | 95.1 | 11.3 | 38
KJ120 | 10 | 3500 | 85 | 62 | 115 | 107.3 | 0.949 | 26.93 | 101.8 | 11.3 | 38
KJ120 | 10 | 3500 | 90 | 62 | 115 | 107.3 | 0.982 | 27.88 | 105.4 | 11.3 | 38
KJ120 | 10 | 3500 | 70 | 67 | 115 | 109.2 | 0.355 | 10.26 | 38.8 | 11.4 | 38
KJ120 | 10 | 3500 | 75 | 67 | 115 | 109.2 | 0.527 | 15.24 | 57.6 | 11.4 | 38
KJ120 | 10 | 3500 | 80 | 67 | 115 | 109.2 | 0.7 | 20.21 | 76.4 | 11.4 | 38
KJ120 | 10 | 3500 | 85 | 67 | 115 | 109.2 | 0.84 | 24.26 | 91.7 | 11.4 | 38
KJ120 | 10 | 3500 | 90 | 67 | 115 | 109.2 | 0.964 | 27.86 | 105.3 | 11.4 | 38
KJ120 | 10 | 3500 | 75 | 72 | 115 | 117.1 | 0.336 | 10.4 | 39.3 | 11.5 | 38
KJ120 | 10 | 3500 | 80 | 72 | 115 | 117.1 | 0.492 | 15.24 | 57.6 | 11.5 | 38
KJ120 | 10 | 3500 | 85 | 72 | 115 | 117.1 | 0.649 | 20.11 | 76 | 11.5 | 38
KJ120 | 10 | 3500 | 90 | 72 | 115 | 117.1 | 0.805 | 24.95 | 94.3 | 11.5 | 38
KJ120 | 10 | 3500 | 80 | 77 | 115 | 125.1 | 0.311 | 10.29 | 38.9 | 11.7 | 38
KJ120 | 10 | 3500 | 85 | 77 | 115 | 125.1 | 0.482 | 15.95 | 60.3 | 11.7 | 38
KJ120 | 10 | 3500 | 90 | 77 | 115 | 125.1 | 0.653 | 21.61 | 81.7 | 11.7 | 38
KJ120 | 10 | 3500 | 65 | 57 | 125 | 99.9 | 0.499 | 13.2 | 49.9 | 12.6 | 38
KJ120 | 10 | 3500 | 70 | 57 | 125 | 99.9 | 0.697 | 18.41 | 69.6 | 12.6 | 38
KJ120 | 10 | 3500 | 75 | 57 | 125 | 99.9 | 0.895 | 23.65 | 89.4 | 12.6 | 38
KJ120 | 10 | 3500 | 80 | 57 | 125 | 99.9 | 1 | 26.43 | 99.9 | 12.6 | 38
KJ120 | 10 | 3500 | 85 | 57 | 125 | 99.9 | 1 | 26.43 | 99.9 | 12.6 | 38
KJ120 | 10 | 3500 | 90 | 57 | 125 | 99.9 | 1 | 26.43 | 99.9 | 12.6 | 38
KJ120 | 10 | 3500 | 65 | 62 | 125 | 101 | 0.325 | 8.68 | 32.8 | 12.6 | 38
KJ120 | 10 | 3500 | 70 | 62 | 125 | 101 | 0.516 | 13.78 | 52.1 | 12.6 | 38
KJ120 | 10 | 3500 | 75 | 62 | 125 | 101 | 0.707 | 18.89 | 71.4 | 12.6 | 38
KJ120 | 10 | 3500 | 80 | 62 | 125 | 101 | 0.898 | 23.99 | 90.7 | 12.6 | 38
KJ120 | 10 | 3500 | 85 | 62 | 125 | 101 | 0.949 | 25.34 | 95.8 | 12.6 | 38
KJ120 | 10 | 3500 | 90 | 62 | 125 | 101 | 0.985 | 26.32 | 99.5 | 12.6 | 38
KJ120 | 10 | 3500 | 70 | 67 | 125 | 102.1 | 0.338 | 9.13 | 34.5 | 12.6 | 38
KJ120 | 10 | 3500 | 75 | 67 | 125 | 102.1 | 0.523 | 14.13 | 53.4 | 12.6 | 38
KJ120 | 10 | 3500 | 80 | 67 | 125 | 102.1 | 0.707 | 19.1 | 72.2 | 12.6 | 38
KJ120 | 10 | 3500 | 85 | 67 | 125 | 102.1 | 0.852 | 23.02 | 87 | 12.6 | 38
KJ120 | 10 | 3500 | 90 | 67 | 125 | 102.1 | 0.973 | 26.27 | 99.3 | 12.6 | 38
KJ120 | 10 | 3500 | 75 | 72 | 125 | 108.2 | 0.327 | 9.37 | 35.4 | 12.8 | 38
KJ120 | 10 | 3500 | 80 | 72 | 125 | 108.2 | 0.497 | 14.23 | 53.8 | 12.8 | 38
KJ120 | 10 | 3500 | 85 | 72 | 125 | 108.2 | 0.667 | 19.1 | 72.2 | 12.8 | 38
KJ120 | 10 | 3500 | 90 | 72 | 125 | 108.2 | 0.837 | 23.97 | 90.6 | 12.8 | 38
KJ120 | 10 | 3500 | 80 | 77 | 125 | 114.3 | 0.31 | 9.37 | 35.4 | 13 | 38
KJ120 | 10 | 3500 | 85 | 77 | 125 | 114.3 | 0.502 | 15.19 | 57.4 | 13 | 38
KJ120 | 10 | 3500 | 90 | 77 | 125 | 114.3 | 0.696 | 21.03 | 79.5 | 13 | 38
KJ120 | 10 | 4000 | 65 | 57 | 75 | 131.6 | 0.566 | 17.25 | 74.5 | 6.9 | 37
KJ120 | 10 | 4000 | 70 | 57 | 75 | 131.6 | 0.736 | 22.41 | 96.8 | 6.9 | 37
KJ120 | 10 | 4000 | 75 | 57 | 75 | 131.6 | 0.905 | 27.57 | 119.1 | 6.9 | 37
KJ120 | 10 | 4000 | 80 | 57 | 75 | 131.6 | 1 | 30.46 | 131.6 | 6.9 | 37
KJ120 | 10 | 4000 | 85 | 57 | 75 | 131.6 | 1 | 30.46 | 131.6 | 6.9 | 37
KJ120 | 10 | 4000 | 90 | 57 | 75 | 131.6 | 1 | 30.46 | 131.6 | 6.9 | 37
KJ120 | 10 | 4000 | 65 | 62 | 75 | 136.6 | 0.403 | 12.75 | 55.1 | 6.9 | 37
KJ120 | 10 | 4000 | 70 | 62 | 75 | 136.6 | 0.561 | 17.75 | 76.7 | 6.9 | 37
KJ120 | 10 | 4000 | 75 | 62 | 75 | 136.6 | 0.714 | 22.59 | 97.6 | 6.9 | 37
KJ120 | 10 | 4000 | 80 | 62 | 75 | 136.6 | 0.876 | 27.71 | 119.7 | 6.9 | 37
KJ120 | 10 | 4000 | 85 | 62 | 75 | 136.6 | 0.949 | 30 | 129.6 | 6.9 | 37
KJ120 | 10 | 4000 | 90 | 62 | 75 | 136.6 | 0.963 | 30.44 | 131.5 | 6.9 | 37
KJ120 | 10 | 4000 | 70 | 67 | 75 | 141.6 | 0.4 | 13.1 | 56.6 | 6.9 | 37
KJ120 | 10 | 4000 | 75 | 67 | 75 | 141.6 | 0.546 | 17.89 | 77.3 | 6.9 | 37
KJ120 | 10 | 4000 | 80 | 67 | 75 | 141.6 | 0.692 | 22.69 | 98 | 6.9 | 37
KJ120 | 10 | 4000 | 85 | 67 | 75 | 141.6 | 0.815 | 26.71 | 115.4 | 6.9 | 37
KJ120 | 10 | 4000 | 90 | 67 | 75 | 141.6 | 0.927 | 30.39 | 131.3 | 6.9 | 37
KJ120 | 10 | 4000 | 75 | 72 | 75 | 153.7 | 0.367 | 13.06 | 56.4 | 7 | 37
KJ120 | 10 | 4000 | 80 | 72 | 75 | 153.7 | 0.497 | 17.69 | 76.4 | 7 | 37
KJ120 | 10 | 4000 | 85 | 72 | 75 | 153.7 | 0.627 | 22.29 | 96.3 | 7 | 37
KJ120 | 10 | 4000 | 90 | 72 | 75 | 153.7 | 0.757 | 26.92 | 116.3 | 7 | 37
KJ120 | 10 | 4000 | 80 | 77 | 75 | 165.7 | 0.33 | 12.66 | 54.7 | 7.1 | 37
KJ120 | 10 | 4000 | 85 | 77 | 75 | 165.7 | 0.466 | 17.87 | 77.2 | 7.1 | 37
KJ120 | 10 | 4000 | 90 | 77 | 75 | 165.7 | 0.602 | 23.08 | 99.7 | 7.1 | 37
KJ120 | 10 | 4000 | 65 | 57 | 85 | 126 | 0.564 | 16.46 | 71.1 | 7.8 | 37
KJ120 | 10 | 4000 | 70 | 57 | 85 | 126 | 0.739 | 21.55 | 93.1 | 7.8 | 37
KJ120 | 10 | 4000 | 75 | 57 | 85 | 126 | 0.913 | 26.62 | 115 | 7.8 | 37
KJ120 | 10 | 4000 | 80 | 57 | 85 | 126 | 1 | 29.17 | 126 | 7.8 | 37
KJ120 | 10 | 4000 | 85 | 57 | 85 | 126 | 1 | 29.17 | 126 | 7.8 | 37
KJ120 | 10 | 4000 | 90 | 57 | 85 | 126 | 1 | 29.17 | 126 | 7.8 | 37
KJ120 | 10 | 4000 | 65 | 62 | 85 | 130.1 | 0.394 | 11.85 | 51.2 | 7.8 | 37
KJ120 | 10 | 4000 | 70 | 62 | 85 | 130.1 | 0.558 | 16.81 | 72.6 | 7.8 | 37
KJ120 | 10 | 4000 | 75 | 62 | 85 | 130.1 | 0.72 | 21.69 | 93.7 | 7.8 | 37
KJ120 | 10 | 4000 | 80 | 62 | 85 | 130.1 | 0.887 | 26.71 | 115.4 | 7.8 | 37
KJ120 | 10 | 4000 | 85 | 62 | 85 | 130.1 | 0.956 | 28.8 | 124.4 | 7.8 | 37
KJ120 | 10 | 4000 | 90 | 62 | 85 | 130.1 | 0.967 | 29.12 | 125.8 | 7.8 | 37
KJ120 | 10 | 4000 | 70 | 67 | 85 | 134.1 | 0.389 | 12.08 | 52.2 | 7.9 | 37
KJ120 | 10 | 4000 | 75 | 67 | 85 | 134.1 | 0.544 | 16.9 | 73 | 7.9 | 37
KJ120 | 10 | 4000 | 80 | 67 | 85 | 134.1 | 0.699 | 21.71 | 93.8 | 7.9 | 37
KJ120 | 10 | 4000 | 85 | 67 | 85 | 134.1 | 0.827 | 25.67 | 110.9 | 7.9 | 37
KJ120 | 10 | 4000 | 90 | 67 | 85 | 134.1 | 0.935 | 29.03 | 125.4 | 7.9 | 37
KJ120 | 10 | 4000 | 75 | 72 | 85 | 145.1 | 0.358 | 12.01 | 51.9 | 7.9 | 37
KJ120 | 10 | 4000 | 80 | 72 | 85 | 145.1 | 0.498 | 16.71 | 72.2 | 7.9 | 37
KJ120 | 10 | 4000 | 85 | 72 | 85 | 145.1 | 0.637 | 21.39 | 92.4 | 7.9 | 37
KJ120 | 10 | 4000 | 90 | 72 | 85 | 145.1 | 0.776 | 26.06 | 112.6 | 7.9 | 37
KJ120 | 10 | 4000 | 80 | 77 | 85 | 156 | 0.324 | 11.71 | 50.6 | 8 | 37
KJ120 | 10 | 4000 | 85 | 77 | 85 | 156 | 0.473 | 17.08 | 73.8 | 8 | 37
KJ120 | 10 | 4000 | 90 | 77 | 85 | 156 | 0.622 | 22.48 | 97.1 | 8 | 37
KJ120 | 10 | 4000 | 65 | 57 | 95 | 120.5 | 0.562 | 15.67 | 67.7 | 8.6 | 37
KJ120 | 10 | 4000 | 70 | 57 | 95 | 120.5 | 0.742 | 20.69 | 89.4 | 8.6 | 37
KJ120 | 10 | 4000 | 75 | 57 | 95 | 120.5 | 0.921 | 25.69 | 111 | 8.6 | 37
KJ120 | 10 | 4000 | 80 | 57 | 95 | 120.5 | 1 | 27.89 | 120.5 | 8.6 | 37
KJ120 | 10 | 4000 | 85 | 57 | 95 | 120.5 | 1 | 27.89 | 120.5 | 8.6 | 37
KJ120 | 10 | 4000 | 90 | 57 | 95 | 120.5 | 1 | 27.89 | 120.5 | 8.6 | 37
KJ120 | 10 | 4000 | 65 | 62 | 95 | 123.6 | 0.383 | 10.95 | 47.3 | 8.7 | 37
KJ120 | 10 | 4000 | 70 | 62 | 95 | 123.6 | 0.555 | 15.88 | 68.6 | 8.7 | 37
KJ120 | 10 | 4000 | 75 | 62 | 95 | 123.6 | 0.727 | 20.79 | 89.8 | 8.7 | 37
KJ120 | 10 | 4000 | 80 | 62 | 95 | 123.6 | 0.899 | 25.72 | 111.1 | 8.7 | 37
KJ120 | 10 | 4000 | 85 | 62 | 95 | 123.6 | 0.964 | 27.57 | 119.1 | 8.7 | 37
KJ120 | 10 | 4000 | 90 | 62 | 95 | 123.6 | 0.973 | 27.85 | 120.3 | 8.7 | 37
KJ120 | 10 | 4000 | 70 | 67 | 95 | 126.7 | 0.377 | 11.06 | 47.8 | 8.8 | 37
KJ120 | 10 | 4000 | 75 | 67 | 95 | 126.7 | 0.542 | 15.9 | 68.7 | 8.8 | 37
KJ120 | 10 | 4000 | 80 | 67 | 95 | 126.7 | 0.706 | 20.72 | 89.5 | 8.8 | 37
KJ120 | 10 | 4000 | 85 | 67 | 95 | 126.7 | 0.84 | 24.63 | 106.4 | 8.8 | 37
KJ120 | 10 | 4000 | 90 | 67 | 95 | 126.7 | 0.947 | 27.78 | 120 | 8.8 | 37
KJ120 | 10 | 4000 | 75 | 72 | 95 | 136.5 | 0.348 | 11 | 47.5 | 8.9 | 37
KJ120 | 10 | 4000 | 80 | 72 | 95 | 136.5 | 0.498 | 15.74 | 68 | 8.9 | 37
KJ120 | 10 | 4000 | 85 | 72 | 95 | 136.5 | 0.648 | 20.46 | 88.4 | 8.9 | 37
KJ120 | 10 | 4000 | 90 | 72 | 95 | 136.5 | 0.798 | 25.21 | 108.9 | 8.9 | 37
KJ120 | 10 | 4000 | 80 | 77 | 95 | 146.3 | 0.317 | 10.74 | 46.4 | 9 | 37
KJ120 | 10 | 4000 | 85 | 77 | 95 | 146.3 | 0.481 | 16.3 | 70.4 | 9 | 37
KJ120 | 10 | 4000 | 90 | 77 | 95 | 146.3 | 0.646 | 21.88 | 94.5 | 9 | 37
KJ120 | 10 | 4000 | 65 | 57 | 105 | 114.6 | 0.548 | 14.54 | 62.8 | 9.9 | 37
KJ120 | 10 | 4000 | 70 | 57 | 105 | 114.6 | 0.738 | 19.58 | 84.6 | 9.9 | 37
KJ120 | 10 | 4000 | 75 | 57 | 105 | 114.6 | 0.928 | 24.63 | 106.4 | 9.9 | 37
KJ120 | 10 | 4000 | 80 | 57 | 105 | 114.6 | 1 | 26.53 | 114.6 | 9.9 | 37
KJ120 | 10 | 4000 | 85 | 57 | 105 | 114.6 | 1 | 26.53 | 114.6 | 9.9 | 37
KJ120 | 10 | 4000 | 90 | 57 | 105 | 114.6 | 1 | 26.53 | 114.6 | 9.9 | 37
KJ120 | 10 | 4000 | 65 | 62 | 105 | 117 | 0.364 | 9.86 | 42.6 | 10 | 37
KJ120 | 10 | 4000 | 70 | 62 | 105 | 117 | 0.547 | 14.81 | 64 | 10 | 37
KJ120 | 10 | 4000 | 75 | 62 | 105 | 117 | 0.73 | 19.77 | 85.4 | 10 | 37
KJ120 | 10 | 4000 | 80 | 62 | 105 | 117 | 0.913 | 24.72 | 106.8 | 10 | 37
KJ120 | 10 | 4000 | 85 | 62 | 105 | 117 | 0.968 | 26.2 | 113.2 | 10 | 37
KJ120 | 10 | 4000 | 90 | 62 | 105 | 117 | 0.979 | 26.5 | 114.5 | 10 | 37
KJ120 | 10 | 4000 | 70 | 67 | 105 | 119.4 | 0.363 | 10.05 | 43.4 | 10.1 | 37
KJ120 | 10 | 4000 | 75 | 67 | 105 | 119.4 | 0.539 | 14.91 | 64.4 | 10.1 | 37
KJ120 | 10 | 4000 | 80 | 67 | 105 | 119.4 | 0.714 | 19.75 | 85.3 | 10.1 | 37
KJ120 | 10 | 4000 | 85 | 67 | 105 | 119.4 | 0.848 | 23.45 | 101.3 | 10.1 | 37
KJ120 | 10 | 4000 | 90 | 67 | 105 | 119.4 | 0.957 | 26.46 | 114.3 | 10.1 | 37
KJ120 | 10 | 4000 | 75 | 72 | 105 | 127.3 | 0.341 | 10.05 | 43.4 | 10.2 | 37
KJ120 | 10 | 4000 | 80 | 72 | 105 | 127.3 | 0.502 | 14.79 | 63.9 | 10.2 | 37
KJ120 | 10 | 4000 | 85 | 72 | 105 | 127.3 | 0.663 | 19.54 | 84.4 | 10.2 | 37
KJ120 | 10 | 4000 | 90 | 72 | 105 | 127.3 | 0.824 | 24.28 | 104.9 | 10.2 | 37
KJ120 | 10 | 4000 | 80 | 77 | 105 | 135.2 | 0.314 | 9.81 | 42.4 | 10.3 | 37
KJ120 | 10 | 4000 | 85 | 77 | 105 | 135.2 | 0.499 | 15.62 | 67.5 | 10.3 | 37
KJ120 | 10 | 4000 | 90 | 77 | 105 | 135.2 | 0.685 | 21.44 | 92.6 | 10.3 | 37
KJ120 | 10 | 4000 | 65 | 57 | 115 | 108.6 | 0.533 | 13.4 | 57.9 | 11.3 | 38
KJ120 | 10 | 4000 | 70 | 57 | 115 | 108.6 | 0.736 | 18.5 | 79.9 | 11.3 | 38
KJ120 | 10 | 4000 | 75 | 57 | 115 | 108.6 | 0.937 | 23.56 | 101.8 | 11.3 | 38
KJ120 | 10 | 4000 | 80 | 57 | 115 | 108.6 | 1 | 25.14 | 108.6 | 11.3 | 38
KJ120 | 10 | 4000 | 85 | 57 | 115 | 108.6 | 1 | 25.14 | 108.6 | 11.3 | 38
KJ120 | 10 | 4000 | 90 | 57 | 115 | 108.6 | 1 | 25.14 | 108.6 | 11.3 | 38
KJ120 | 10 | 4000 | 65 | 62 | 115 | 110.4 | 0.343 | 8.77 | 37.9 | 11.3 | 38
KJ120 | 10 | 4000 | 70 | 62 | 115 | 110.4 | 0.539 | 13.77 | 59.5 | 11.3 | 38
KJ120 | 10 | 4000 | 75 | 62 | 115 | 110.4 | 0.734 | 18.75 | 81 | 11.3 | 38
KJ120 | 10 | 4000 | 80 | 62 | 115 | 110.4 | 0.928 | 23.73 | 102.5 | 11.3 | 38
KJ120 | 10 | 4000 | 85 | 62 | 115 | 110.4 | 0.971 | 24.81 | 107.2 | 11.3 | 38
KJ120 | 10 | 4000 | 90 | 62 | 115 | 110.4 | 0.983 | 25.12 | 108.5 | 11.3 | 38
KJ120 | 10 | 4000 | 70 | 67 | 115 | 112.1 | 0.349 | 9.05 | 39.1 | 11.4 | 38
KJ120 | 10 | 4000 | 75 | 67 | 115 | 112.1 | 0.536 | 13.91 | 60.1 | 11.4 | 38
KJ120 | 10 | 4000 | 80 | 67 | 115 | 112.1 | 0.723 | 18.77 | 81.1 | 11.4 | 38
KJ120 | 10 | 4000 | 85 | 67 | 115 | 112.1 | 0.858 | 22.27 | 96.2 | 11.4 | 38
KJ120 | 10 | 4000 | 90 | 67 | 115 | 112.1 | 0.967 | 25.09 | 108.4 | 11.4 | 38
KJ120 | 10 | 4000 | 75 | 72 | 115 | 118.1 | 0.332 | 9.07 | 39.2 | 11.5 | 38
KJ120 | 10 | 4000 | 80 | 72 | 115 | 118.1 | 0.506 | 13.84 | 59.8 | 11.5 | 38
KJ120 | 10 | 4000 | 85 | 72 | 115 | 118.1 | 0.681 | 18.61 | 80.4 | 11.5 | 38
KJ120 | 10 | 4000 | 90 | 72 | 115 | 118.1 | 0.855 | 23.38 | 101 | 11.5 | 38
KJ120 | 10 | 4000 | 80 | 77 | 115 | 124.1 | 0.31 | 8.91 | 38.5 | 11.7 | 38
KJ120 | 10 | 4000 | 85 | 77 | 115 | 124.1 | 0.521 | 14.95 | 64.6 | 11.7 | 38
KJ120 | 10 | 4000 | 90 | 77 | 115 | 124.1 | 0.731 | 21 | 90.7 | 11.7 | 38
KJ120 | 10 | 4000 | 65 | 57 | 125 | 102.7 | 0.516 | 12.27 | 53 | 12.6 | 38
KJ120 | 10 | 4000 | 70 | 57 | 125 | 102.7 | 0.731 | 17.38 | 75.1 | 12.6 | 38
KJ120 | 10 | 4000 | 75 | 57 | 125 | 102.7 | 0.947 | 22.52 | 97.3 | 12.6 | 38
KJ120 | 10 | 4000 | 80 | 57 | 125 | 102.7 | 1 | 23.77 | 102.7 | 12.6 | 38
KJ120 | 10 | 4000 | 85 | 57 | 125 | 102.7 | 1 | 23.77 | 102.7 | 12.6 | 38
KJ120 | 10 | 4000 | 90 | 57 | 125 | 102.7 | 1 | 23.77 | 102.7 | 12.6 | 38
KJ120 | 10 | 4000 | 65 | 62 | 125 | 103.8 | 0.32 | 7.69 | 33.2 | 12.6 | 38
KJ120 | 10 | 4000 | 70 | 62 | 125 | 103.8 | 0.529 | 12.71 | 54.9 | 12.6 | 38
KJ120 | 10 | 4000 | 75 | 62 | 125 | 103.8 | 0.737 | 17.71 | 76.5 | 12.6 | 38
KJ120 | 10 | 4000 | 80 | 62 | 125 | 103.8 | 0.946 | 22.73 | 98.2 | 12.6 | 38
KJ120 | 10 | 4000 | 85 | 62 | 125 | 103.8 | 0.976 | 23.45 | 101.3 | 12.6 | 38
KJ120 | 10 | 4000 | 90 | 62 | 125 | 103.8 | 0.987 | 23.73 | 102.5 | 12.6 | 38
KJ120 | 10 | 4000 | 70 | 67 | 125 | 104.9 | 0.331 | 8.03 | 34.7 | 12.7 | 38
KJ120 | 10 | 4000 | 75 | 67 | 125 | 104.9 | 0.532 | 12.92 | 55.8 | 12.7 | 38
KJ120 | 10 | 4000 | 80 | 67 | 125 | 104.9 | 0.734 | 17.82 | 77 | 12.7 | 38
KJ120 | 10 | 4000 | 85 | 67 | 125 | 104.9 | 0.868 | 21.09 | 91.1 | 12.7 | 38
KJ120 | 10 | 4000 | 90 | 67 | 125 | 104.9 | 0.976 | 23.7 | 102.4 | 12.7 | 38
KJ120 | 10 | 4000 | 75 | 72 | 125 | 109 | 0.322 | 8.12 | 35.1 | 12.9 | 38
KJ120 | 10 | 4000 | 80 | 72 | 125 | 109 | 0.511 | 12.89 | 55.7 | 12.9 | 38
KJ120 | 10 | 4000 | 85 | 72 | 125 | 109 | 0.701 | 17.69 | 76.4 | 12.9 | 38
KJ120 | 10 | 4000 | 90 | 72 | 125 | 109 | 0.89 | 22.45 | 97 | 12.9 | 38
KJ120 | 10 | 4000 | 80 | 77 | 125 | 113 | 0.305 | 7.99 | 34.5 | 13 | 38
KJ120 | 10 | 4000 | 85 | 77 | 125 | 113 | 0.546 | 14.28 | 61.7 | 13 | 38
KJ120 | 10 | 4000 | 90 | 77 | 125 | 113 | 0.786 | 20.56 | 88.8 | 13 | 38
KJ120 | 10 | 4500 | 65 | 57 | 75 | 138.2 | 0.559 | 15.91 | 77.3 | 6.9 | 37
KJ120 | 10 | 4500 | 70 | 57 | 75 | 138.2 | 0.742 | 21.09 | 102.5 | 6.9 | 37
KJ120 | 10 | 4500 | 75 | 57 | 75 | 138.2 | 0.924 | 26.28 | 127.7 | 6.9 | 37
KJ120 | 10 | 4500 | 80 | 57 | 75 | 138.2 | 1 | 28.44 | 138.2 | 6.9 | 37
KJ120 | 10 | 4500 | 85 | 57 | 75 | 138.2 | 1 | 28.44 | 138.2 | 6.9 | 37
KJ120 | 10 | 4500 | 90 | 57 | 75 | 138.2 | 1 | 28.44 | 138.2 | 6.9 | 37
KJ120 | 10 | 4500 | 65 | 62 | 75 | 141.4 | 0.393 | 11.44 | 55.6 | 6.9 | 37
KJ120 | 10 | 4500 | 70 | 62 | 75 | 141.4 | 0.564 | 16.42 | 79.8 | 6.9 | 37
KJ120 | 10 | 4500 | 75 | 62 | 75 | 141.4 | 0.733 | 21.34 | 103.7 | 6.9 | 37
KJ120 | 10 | 4500 | 80 | 62 | 75 | 141.4 | 0.907 | 26.4 | 128.3 | 6.9 | 37
KJ120 | 10 | 4500 | 85 | 62 | 75 | 141.4 | 0.964 | 28.05 | 136.3 | 6.9 | 37
KJ120 | 10 | 4500 | 90 | 62 | 75 | 141.4 | 0.977 | 28.42 | 138.1 | 6.9 | 37
KJ120 | 10 | 4500 | 70 | 67 | 75 | 144.6 | 0.396 | 11.77 | 57.2 | 6.9 | 37
KJ120 | 10 | 4500 | 75 | 67 | 75 | 144.6 | 0.556 | 16.54 | 80.4 | 6.9 | 37
KJ120 | 10 | 4500 | 80 | 67 | 75 | 144.6 | 0.716 | 21.32 | 103.6 | 6.9 | 37
KJ120 | 10 | 4500 | 85 | 67 | 75 | 144.6 | 0.843 | 25.08 | 121.9 | 6.9 | 37
KJ120 | 10 | 4500 | 90 | 67 | 75 | 144.6 | 0.954 | 28.4 | 138 | 6.9 | 37
KJ120 | 10 | 4500 | 75 | 72 | 75 | 156.4 | 0.363 | 11.69 | 56.8 | 7 | 37
KJ120 | 10 | 4500 | 80 | 72 | 75 | 156.4 | 0.505 | 16.26 | 79 | 7 | 37
KJ120 | 10 | 4500 | 85 | 72 | 75 | 156.4 | 0.647 | 20.82 | 101.2 | 7 | 37
KJ120 | 10 | 4500 | 90 | 72 | 75 | 156.4 | 0.789 | 25.39 | 123.4 | 7 | 37
KJ120 | 10 | 4500 | 65 | 57 | 85 | 131.2 | 0.562 | 15.19 | 73.8 | 7.8 | 37
KJ120 | 10 | 4500 | 70 | 57 | 85 | 131.2 | 0.749 | 20.23 | 98.3 | 7.8 | 37
KJ120 | 10 | 4500 | 75 | 57 | 85 | 131.2 | 0.937 | 25.29 | 122.9 | 7.8 | 37
KJ120 | 10 | 4500 | 80 | 57 | 85 | 131.2 | 1 | 27 | 131.2 | 7.8 | 37
KJ120 | 10 | 4500 | 85 | 57 | 85 | 131.2 | 1 | 27 | 131.2 | 7.8 | 37
KJ120 | 10 | 4500 | 90 | 57 | 85 | 131.2 | 1 | 27 | 131.2 | 7.8 | 37
KJ120 | 10 | 4500 | 65 | 62 | 85 | 134.2 | 0.385 | 10.62 | 51.6 | 7.8 | 37
KJ120 | 10 | 4500 | 70 | 62 | 85 | 134.2 | 0.563 | 15.53 | 75.5 | 7.8 | 37
KJ120 | 10 | 4500 | 75 | 62 | 85 | 134.2 | 0.739 | 20.41 | 99.2 | 7.8 | 37
KJ120 | 10 | 4500 | 80 | 62 | 85 | 134.2 | 0.918 | 25.35 | 123.2 | 7.8 | 37
KJ120 | 10 | 4500 | 85 | 62 | 85 | 134.2 | 0.972 | 26.83 | 130.4 | 7.8 | 37
KJ120 | 10 | 4500 | 90 | 62 | 85 | 134.2 | 0.977 | 26.98 | 131.1 | 7.8 | 37
KJ120 | 10 | 4500 | 70 | 67 | 85 | 137.2 | 0.384 | 10.84 | 52.7 | 7.9 | 37
KJ120 | 10 | 4500 | 75 | 67 | 85 | 137.2 | 0.552 | 15.6 | 75.8 | 7.9 | 37
KJ120 | 10 | 4500 | 80 | 67 | 85 | 137.2 | 0.722 | 20.37 | 99 | 7.9 | 37
KJ120 | 10 | 4500 | 85 | 67 | 85 | 137.2 | 0.852 | 24.05 | 116.9 | 7.9 | 37
KJ120 | 10 | 4500 | 90 | 67 | 85 | 137.2 | 0.955 | 26.95 | 131 | 7.9 | 37
KJ120 | 10 | 4500 | 75 | 72 | 85 | 147.2 | 0.355 | 10.76 | 52.3 | 8 | 37
KJ120 | 10 | 4500 | 80 | 72 | 85 | 147.2 | 0.508 | 15.39 | 74.8 | 8 | 37
KJ120 | 10 | 4500 | 85 | 72 | 85 | 147.2 | 0.661 | 20.02 | 97.3 | 8 | 37
KJ120 | 10 | 4500 | 90 | 72 | 85 | 147.2 | 0.813 | 24.63 | 119.7 | 8 | 37
KJ120 | 10 | 4500 | 65 | 57 | 95 | 124.3 | 0.565 | 14.44 | 70.2 | 8.7 | 37
KJ120 | 10 | 4500 | 70 | 57 | 95 | 124.3 | 0.757 | 19.36 | 94.1 | 8.7 | 37
KJ120 | 10 | 4500 | 75 | 57 | 95 | 124.3 | 0.949 | 24.28 | 118 | 8.7 | 37
KJ120 | 10 | 4500 | 80 | 57 | 95 | 124.3 | 1 | 25.58 | 124.3 | 8.7 | 37
KJ120 | 10 | 4500 | 85 | 57 | 95 | 124.3 | 1 | 25.58 | 124.3 | 8.7 | 37
KJ120 | 10 | 4500 | 90 | 57 | 95 | 124.3 | 1 | 25.58 | 124.3 | 8.7 | 37
KJ120 | 10 | 4500 | 65 | 62 | 95 | 127.1 | 0.375 | 9.79 | 47.6 | 8.7 | 37
KJ120 | 10 | 4500 | 70 | 62 | 95 | 127.1 | 0.559 | 14.63 | 71.1 | 8.7 | 37
KJ120 | 10 | 4500 | 75 | 62 | 95 | 127.1 | 0.744 | 19.47 | 94.6 | 8.7 | 37
KJ120 | 10 | 4500 | 80 | 62 | 95 | 127.1 | 0.93 | 24.32 | 118.2 | 8.7 | 37
KJ120 | 10 | 4500 | 85 | 62 | 95 | 127.1 | 0.977 | 25.56 | 124.2 | 8.7 | 37
KJ120 | 10 | 4500 | 90 | 62 | 95 | 127.1 | 0.977 | 25.56 | 124.2 | 8.7 | 37
KJ120 | 10 | 4500 | 70 | 67 | 95 | 129.9 | 0.37 | 9.9 | 48.1 | 8.8 | 37
KJ120 | 10 | 4500 | 75 | 67 | 95 | 129.9 | 0.549 | 14.67 | 71.3 | 8.8 | 37
KJ120 | 10 | 4500 | 80 | 67 | 95 | 129.9 | 0.727 | 19.42 | 94.4 | 8.8 | 37
KJ120 | 10 | 4500 | 85 | 67 | 95 | 129.9 | 0.861 | 23.02 | 111.9 | 8.8 | 37
KJ120 | 10 | 4500 | 90 | 67 | 95 | 129.9 | 0.955 | 25.51 | 124 | 8.8 | 37
KJ120 | 10 | 4500 | 75 | 72 | 95 | 137.9 | 0.347 | 9.86 | 47.9 | 8.9 | 37
KJ120 | 10 | 4500 | 80 | 72 | 95 | 137.9 | 0.512 | 14.53 | 70.6 | 8.9 | 37
KJ120 | 10 | 4500 | 85 | 72 | 95 | 137.9 | 0.677 | 19.2 | 93.3 | 8.9 | 37
KJ120 | 10 | 4500 | 90 | 72 | 95 | 137.9 | 0.842 | 23.89 | 116.1 | 8.9 | 37
KJ120 | 10 | 4500 | 65 | 57 | 105 | 118.1 | 0.555 | 13.48 | 65.5 | 10 | 37
KJ120 | 10 | 4500 | 70 | 57 | 105 | 118.1 | 0.759 | 18.44 | 89.6 | 10 | 37
KJ120 | 10 | 4500 | 75 | 57 | 105 | 118.1 | 0.963 | 23.4 | 113.7 | 10 | 37
KJ120 | 10 | 4500 | 80 | 57 | 105 | 118.1 | 1 | 24.3 | 118.1 | 10 | 37
KJ120 | 10 | 4500 | 85 | 57 | 105 | 118.1 | 1 | 24.3 | 118.1 | 10 | 37
KJ120 | 10 | 4500 | 90 | 57 | 105 | 118.1 | 1 | 24.3 | 118.1 | 10 | 37
KJ120 | 10 | 4500 | 65 | 62 | 105 | 120.3 | 0.357 | 8.85 | 43 | 10 | 37
KJ120 | 10 | 4500 | 70 | 62 | 105 | 120.3 | 0.554 | 13.72 | 66.7 | 10 | 37
KJ120 | 10 | 4500 | 75 | 62 | 105 | 120.3 | 0.751 | 18.58 | 90.3 | 10 | 37
KJ120 | 10 | 4500 | 80 | 62 | 105 | 120.3 | 0.948 | 23.46 | 114 | 10 | 37
KJ120 | 10 | 4500 | 85 | 62 | 105 | 120.3 | 0.982 | 24.3 | 118.1 | 10 | 37
KJ120 | 10 | 4500 | 90 | 62 | 105 | 120.3 | 0.982 | 24.3 | 118.1 | 10 | 37
KJ120 | 10 | 4500 | 70 | 67 | 105 | 122.5 | 0.357 | 8.99 | 43.7 | 10.1 | 37
KJ120 | 10 | 4500 | 75 | 67 | 105 | 122.5 | 0.546 | 13.77 | 66.9 | 10.1 | 37
KJ120 | 10 | 4500 | 80 | 67 | 105 | 122.5 | 0.736 | 18.54 | 90.1 | 10.1 | 37
KJ120 | 10 | 4500 | 85 | 67 | 105 | 122.5 | 0.868 | 21.87 | 106.3 | 10.1 | 37
KJ120 | 10 | 4500 | 90 | 67 | 105 | 122.5 | 0.963 | 24.28 | 118 | 10.1 | 37
KJ120 | 10 | 4500 | 75 | 72 | 105 | 128.5 | 0.339 | 8.95 | 43.5 | 10.2 | 37
KJ120 | 10 | 4500 | 80 | 72 | 105 | 128.5 | 0.516 | 13.64 | 66.3 | 10.2 | 37
KJ120 | 10 | 4500 | 85 | 72 | 105 | 128.5 | 0.693 | 18.33 | 89.1 | 10.2 | 37
KJ120 | 10 | 4500 | 90 | 72 | 105 | 128.5 | 0.87 | 23 | 111.8 | 10.2 | 37
KJ120 | 10 | 4500 | 65 | 57 | 115 | 111.8 | 0.544 | 12.51 | 60.8 | 11.2 | 38
KJ120 | 10 | 4500 | 70 | 57 | 115 | 111.8 | 0.761 | 17.51 | 85.1 | 11.2 | 38
KJ120 | 10 | 4500 | 75 | 57 | 115 | 111.8 | 0.979 | 22.53 | 109.5 | 11.2 | 38
KJ120 | 10 | 4500 | 80 | 57 | 115 | 111.8 | 1 | 23 | 111.8 | 11.2 | 38
KJ120 | 10 | 4500 | 85 | 57 | 115 | 111.8 | 1 | 23 | 111.8 | 11.2 | 38
KJ120 | 10 | 4500 | 90 | 57 | 115 | 111.8 | 1 | 23 | 111.8 | 11.2 | 38
KJ120 | 10 | 4500 | 65 | 62 | 115 | 113.4 | 0.339 | 7.9 | 38.4 | 11.3 | 38
KJ120 | 10 | 4500 | 70 | 62 | 115 | 113.4 | 0.549 | 12.8 | 62.2 | 11.3 | 38
KJ120 | 10 | 4500 | 75 | 62 | 115 | 113.4 | 0.758 | 17.7 | 86 | 11.3 | 38
KJ120 | 10 | 4500 | 80 | 62 | 115 | 113.4 | 0.969 | 22.61 | 109.9 | 11.3 | 38
KJ120 | 10 | 4500 | 85 | 62 | 115 | 113.4 | 0.984 | 22.96 | 111.6 | 11.3 | 38
KJ120 | 10 | 4500 | 90 | 62 | 115 | 113.4 | 0.984 | 22.96 | 111.6 | 11.3 | 38
KJ120 | 10 | 4500 | 70 | 67 | 115 | 115.1 | 0.341 | 8.09 | 39.3 | 11.4 | 38
KJ120 | 10 | 4500 | 75 | 67 | 115 | 115.1 | 0.544 | 12.88 | 62.6 | 11.4 | 38
KJ120 | 10 | 4500 | 80 | 67 | 115 | 115.1 | 0.746 | 17.67 | 85.9 | 11.4 | 38
KJ120 | 10 | 4500 | 85 | 67 | 115 | 115.1 | 0.876 | 20.74 | 100.8 | 11.4 | 38
KJ120 | 10 | 4500 | 90 | 67 | 115 | 115.1 | 0.967 | 22.9 | 111.3 | 11.4 | 38
KJ120 | 10 | 4500 | 75 | 72 | 115 | 119.1 | 0.329 | 8.07 | 39.2 | 11.6 | 38
KJ120 | 10 | 4500 | 80 | 72 | 115 | 119.1 | 0.521 | 12.76 | 62 | 11.6 | 38
KJ120 | 10 | 4500 | 85 | 72 | 115 | 119.1 | 0.712 | 17.45 | 84.8 | 11.6 | 38
KJ120 | 10 | 4500 | 90 | 72 | 115 | 119.1 | 0.903 | 22.14 | 107.6 | 11.6 | 38
KJ120 | 10 | 4500 | 65 | 57 | 125 | 105.5 | 0.531 | 11.52 | 56 | 12.5 | 38
KJ120 | 10 | 4500 | 70 | 57 | 125 | 105.5 | 0.764 | 16.58 | 80.6 | 12.5 | 38
KJ120 | 10 | 4500 | 75 | 57 | 125 | 105.5 | 0.997 | 21.65 | 105.2 | 12.5 | 38
KJ120 | 10 | 4500 | 80 | 57 | 125 | 105.5 | 1 | 21.71 | 105.5 | 12.5 | 38
KJ120 | 10 | 4500 | 85 | 57 | 125 | 105.5 | 1 | 21.71 | 105.5 | 12.5 | 38
KJ120 | 10 | 4500 | 90 | 57 | 125 | 105.5 | 1 | 21.71 | 105.5 | 12.5 | 38
KJ120 | 10 | 4500 | 65 | 62 | 125 | 106.6 | 0.316 | 6.93 | 33.7 | 12.6 | 38
KJ120 | 10 | 4500 | 70 | 62 | 125 | 106.6 | 0.541 | 11.87 | 57.7 | 12.6 | 38
KJ120 | 10 | 4500 | 75 | 62 | 125 | 106.6 | 0.766 | 16.81 | 81.7 | 12.6 | 38
KJ120 | 10 | 4500 | 80 | 62 | 125 | 106.6 | 0.988 | 21.67 | 105.3 | 12.6 | 38
KJ120 | 10 | 4500 | 85 | 62 | 125 | 106.6 | 0.988 | 21.67 | 105.3 | 12.6 | 38
KJ120 | 10 | 4500 | 90 | 62 | 125 | 106.6 | 0.988 | 21.67 | 105.3 | 12.6 | 38
KJ120 | 10 | 4500 | 70 | 67 | 125 | 107.7 | 0.323 | 7.16 | 34.8 | 12.7 | 38
KJ120 | 10 | 4500 | 75 | 67 | 125 | 107.7 | 0.541 | 12 | 58.3 | 12.7 | 38
KJ120 | 10 | 4500 | 80 | 67 | 125 | 107.7 | 0.759 | 16.81 | 81.7 | 12.7 | 38
KJ120 | 10 | 4500 | 85 | 67 | 125 | 107.7 | 0.884 | 19.59 | 95.2 | 12.7 | 38
KJ120 | 10 | 4500 | 90 | 67 | 125 | 107.7 | 0.977 | 21.65 | 105.2 | 12.7 | 38
KJ120 | 10 | 4500 | 75 | 72 | 125 | 109.7 | 0.317 | 7.16 | 34.8 | 12.9 | 38
KJ120 | 10 | 4500 | 80 | 72 | 125 | 109.7 | 0.526 | 11.87 | 57.7 | 12.9 | 38
KJ120 | 10 | 4500 | 85 | 72 | 125 | 109.7 | 0.734 | 16.56 | 80.5 | 12.9 | 38
KJ120 | 10 | 4500 | 90 | 72 | 125 | 109.7 | 0.943 | 21.28 | 103.4 | 12.9 | 38
KJ120 | 10 | 5000 | 65 | 57 | 75 | 144.7 | 0.553 | 14.81 | 80 | 6.9 | 37
KJ120 | 10 | 5000 | 70 | 57 | 75 | 144.7 | 0.748 | 20.04 | 108.2 | 6.9 | 37
KJ120 | 10 | 5000 | 75 | 57 | 75 | 144.7 | 0.942 | 25.24 | 136.3 | 6.9 | 37
KJ120 | 10 | 5000 | 80 | 57 | 75 | 144.7 | 1 | 26.8 | 144.7 | 6.9 | 37
KJ120 | 10 | 5000 | 85 | 57 | 75 | 144.7 | 1 | 26.8 | 144.7 | 6.9 | 37
KJ120 | 10 | 5000 | 90 | 57 | 75 | 144.7 | 1 | 26.8 | 144.7 | 6.9 | 37
KJ120 | 10 | 5000 | 65 | 62 | 75 | 146.2 | 0.384 | 10.39 | 56.1 | 7 | 37
KJ120 | 10 | 5000 | 70 | 62 | 75 | 146.2 | 0.568 | 15.37 | 83 | 7 | 37
KJ120 | 10 | 5000 | 75 | 62 | 75 | 146.2 | 0.752 | 20.35 | 109.9 | 7 | 37
KJ120 | 10 | 5000 | 80 | 62 | 75 | 146.2 | 0.936 | 25.33 | 136.8 | 7 | 37
KJ120 | 10 | 5000 | 85 | 62 | 75 | 146.2 | 0.978 | 26.48 | 143 | 7 | 37
KJ120 | 10 | 5000 | 90 | 62 | 75 | 146.2 | 0.989 | 26.78 | 144.6 | 7 | 37
KJ120 | 10 | 5000 | 70 | 67 | 75 | 147.6 | 0.392 | 10.72 | 57.9 | 7 | 37
KJ120 | 10 | 5000 | 75 | 67 | 75 | 147.6 | 0.566 | 15.46 | 83.5 | 7 | 37
KJ120 | 10 | 5000 | 80 | 67 | 75 | 147.6 | 0.74 | 20.22 | 109.2 | 7 | 37
KJ120 | 10 | 5000 | 85 | 67 | 75 | 147.6 | 0.87 | 23.78 | 128.4 | 7 | 37
KJ120 | 10 | 5000 | 90 | 67 | 75 | 147.6 | 0.979 | 26.76 | 144.5 | 7 | 37
KJ120 | 10 | 5000 | 75 | 72 | 75 | 159.1 | 0.359 | 10.57 | 57.1 | 7 | 37
KJ120 | 10 | 5000 | 80 | 72 | 75 | 159.1 | 0.513 | 15.11 | 81.6 | 7 | 37
KJ120 | 10 | 5000 | 85 | 72 | 75 | 159.1 | 0.666 | 19.63 | 106 | 7 | 37
KJ120 | 10 | 5000 | 90 | 72 | 75 | 159.1 | 0.82 | 24.17 | 130.5 | 7 | 37
KJ120 | 10 | 5000 | 65 | 57 | 85 | 136.5 | 0.56 | 14.15 | 76.4 | 7.8 | 37
KJ120 | 10 | 5000 | 70 | 57 | 85 | 136.5 | 0.758 | 19.17 | 103.5 | 7.8 | 37
KJ120 | 10 | 5000 | 75 | 57 | 85 | 136.5 | 0.958 | 24.2 | 130.7 | 7.8 | 37
KJ120 | 10 | 5000 | 80 | 57 | 85 | 136.5 | 1 | 25.28 | 136.5 | 7.8 | 37
KJ120 | 10 | 5000 | 85 | 57 | 85 | 136.5 | 1 | 25.28 | 136.5 | 7.8 | 37
KJ120 | 10 | 5000 | 90 | 57 | 85 | 136.5 | 1 | 25.28 | 136.5 | 7.8 | 37
KJ120 | 10 | 5000 | 65 | 62 | 85 | 138.4 | 0.376 | 9.63 | 52 | 7.8 | 37
KJ120 | 10 | 5000 | 70 | 62 | 85 | 138.4 | 0.566 | 14.52 | 78.4 | 7.8 | 37
KJ120 | 10 | 5000 | 75 | 62 | 85 | 138.4 | 0.757 | 19.39 | 104.7 | 7.8 | 37
KJ120 | 10 | 5000 | 80 | 62 | 85 | 138.4 | 0.947 | 24.26 | 131 | 7.8 | 37
KJ120 | 10 | 5000 | 85 | 62 | 85 | 138.4 | 0.985 | 25.24 | 136.3 | 7.8 | 37
KJ120 | 10 | 5000 | 90 | 62 | 85 | 138.4 | 0.985 | 25.24 | 136.3 | 7.8 | 37
KJ120 | 10 | 5000 | 70 | 67 | 85 | 140.4 | 0.379 | 9.85 | 53.2 | 7.9 | 37
KJ120 | 10 | 5000 | 75 | 67 | 85 | 140.4 | 0.561 | 14.57 | 78.7 | 7.9 | 37
KJ120 | 10 | 5000 | 80 | 67 | 85 | 140.4 | 0.742 | 19.3 | 104.2 | 7.9 | 37
KJ120 | 10 | 5000 | 85 | 67 | 85 | 140.4 | 0.875 | 22.76 | 122.9 | 7.9 | 37
KJ120 | 10 | 5000 | 90 | 67 | 85 | 140.4 | 0.969 | 25.19 | 136 | 7.9 | 37
KJ120 | 10 | 5000 | 75 | 72 | 85 | 149.3 | 0.353 | 9.76 | 52.7 | 8 | 37
KJ120 | 10 | 5000 | 80 | 72 | 85 | 149.3 | 0.518 | 14.33 | 77.4 | 8 | 37
KJ120 | 10 | 5000 | 85 | 72 | 85 | 149.3 | 0.684 | 18.91 | 102.1 | 8 | 37
KJ120 | 10 | 5000 | 90 | 72 | 85 | 149.3 | 0.85 | 23.5 | 126.9 | 8 | 37
KJ120 | 10 | 5000 | 65 | 57 | 95 | 128.2 | 0.568 | 13.48 | 72.8 | 8.7 | 37
KJ120 | 10 | 5000 | 70 | 57 | 95 | 128.2 | 0.771 | 18.31 | 98.9 | 8.7 | 37
KJ120 | 10 | 5000 | 75 | 57 | 95 | 128.2 | 0.976 | 23.17 | 125.1 | 8.7 | 37
KJ120 | 10 | 5000 | 80 | 57 | 95 | 128.2 | 1 | 23.74 | 128.2 | 8.7 | 37
KJ120 | 10 | 5000 | 85 | 57 | 95 | 128.2 | 1 | 23.74 | 128.2 | 8.7 | 37
KJ120 | 10 | 5000 | 90 | 57 | 95 | 128.2 | 1 | 23.74 | 128.2 | 8.7 | 37
KJ120 | 10 | 5000 | 65 | 62 | 95 | 130.6 | 0.367 | 8.87 | 47.9 | 8.7 | 37
KJ120 | 10 | 5000 | 70 | 62 | 95 | 130.6 | 0.564 | 13.65 | 73.7 | 8.7 | 37
KJ120 | 10 | 5000 | 75 | 62 | 95 | 130.6 | 0.762 | 18.43 | 99.5 | 8.7 | 37
KJ120 | 10 | 5000 | 80 | 62 | 95 | 130.6 | 0.959 | 23.19 | 125.2 | 8.7 | 37
KJ120 | 10 | 5000 | 85 | 62 | 95 | 130.6 | 0.981 | 23.72 | 128.1 | 8.7 | 37
KJ120 | 10 | 5000 | 90 | 62 | 95 | 130.6 | 0.981 | 23.72 | 128.1 | 8.7 | 37
KJ120 | 10 | 5000 | 70 | 67 | 95 | 133.1 | 0.364 | 8.98 | 48.5 | 8.8 | 37
KJ120 | 10 | 5000 | 75 | 67 | 95 | 133.1 | 0.555 | 13.69 | 73.9 | 8.8 | 37
KJ120 | 10 | 5000 | 80 | 67 | 95 | 133.1 | 0.745 | 18.37 | 99.2 | 8.8 | 37
KJ120 | 10 | 5000 | 85 | 67 | 95 | 133.1 | 0.881 | 21.72 | 117.3 | 8.8 | 37
KJ120 | 10 | 5000 | 90 | 67 | 95 | 133.1 | 0.962 | 23.7 | 128 | 8.8 | 37
KJ120 | 10 | 5000 | 75 | 72 | 95 | 139.4 | 0.346 | 8.93 | 48.2 | 8.9 | 37
KJ120 | 10 | 5000 | 80 | 72 | 95 | 139.4 | 0.525 | 13.56 | 73.2 | 8.9 | 37
KJ120 | 10 | 5000 | 85 | 72 | 95 | 139.4 | 0.704 | 18.19 | 98.2 | 8.9 | 37
KJ120 | 10 | 5000 | 90 | 72 | 95 | 139.4 | 0.884 | 22.81 | 123.2 | 8.9 | 37
KJ120 | 10 | 5000 | 65 | 57 | 105 | 121.6 | 0.561 | 12.63 | 68.2 | 10 | 37
KJ120 | 10 | 5000 | 70 | 57 | 105 | 121.6 | 0.778 | 17.52 | 94.6 | 10 | 37
KJ120 | 10 | 5000 | 75 | 57 | 105 | 121.6 | 0.996 | 22.43 | 121.1 | 10 | 37
KJ120 | 10 | 5000 | 80 | 57 | 105 | 121.6 | 1 | 22.52 | 121.6 | 10 | 37
KJ120 | 10 | 5000 | 85 | 57 | 105 | 121.6 | 1 | 22.52 | 121.6 | 10 | 37
KJ120 | 10 | 5000 | 90 | 57 | 105 | 121.6 | 1 | 22.52 | 121.6 | 10 | 37
KJ120 | 10 | 5000 | 65 | 62 | 105 | 123.6 | 0.35 | 8.02 | 43.3 | 10 | 37
KJ120 | 10 | 5000 | 70 | 62 | 105 | 123.6 | 0.561 | 12.83 | 69.3 | 10 | 37
KJ120 | 10 | 5000 | 75 | 62 | 105 | 123.6 | 0.771 | 17.65 | 95.3 | 10 | 37
KJ120 | 10 | 5000 | 80 | 62 | 105 | 123.6 | 0.981 | 22.44 | 121.2 | 10 | 37
KJ120 | 10 | 5000 | 85 | 62 | 105 | 123.6 | 0.982 | 22.48 | 121.4 | 10 | 37
KJ120 | 10 | 5000 | 90 | 62 | 105 | 123.6 | 0.982 | 22.48 | 121.4 | 10 | 37
KJ120 | 10 | 5000 | 70 | 67 | 105 | 125.6 | 0.35 | 8.15 | 44 | 10.1 | 37
KJ120 | 10 | 5000 | 75 | 67 | 105 | 125.6 | 0.553 | 12.87 | 69.5 | 10.1 | 37
KJ120 | 10 | 5000 | 80 | 67 | 105 | 125.6 | 0.756 | 17.59 | 95 | 10.1 | 37
KJ120 | 10 | 5000 | 85 | 67 | 105 | 125.6 | 0.886 | 20.61 | 111.3 | 10.1 | 37
KJ120 | 10 | 5000 | 90 | 67 | 105 | 125.6 | 0.966 | 22.46 | 121.3 | 10.1 | 37
KJ120 | 10 | 5000 | 75 | 72 | 105 | 129.8 | 0.337 | 8.09 | 43.7 | 10.2 | 37
KJ120 | 10 | 5000 | 80 | 72 | 105 | 129.8 | 0.529 | 12.72 | 68.7 | 10.2 | 37
KJ120 | 10 | 5000 | 85 | 72 | 105 | 129.8 | 0.722 | 17.35 | 93.7 | 10.2 | 37
KJ120 | 10 | 5000 | 90 | 72 | 105 | 129.8 | 0.915 | 22 | 118.8 | 10.2 | 37
KJ120 | 10 | 5000 | 65 | 57 | 115 | 115 | 0.554 | 11.8 | 63.7 | 11.2 | 38
KJ120 | 10 | 5000 | 70 | 57 | 115 | 115 | 0.786 | 16.74 | 90.4 | 11.2 | 38
KJ120 | 10 | 5000 | 75 | 57 | 115 | 115 | 1 | 21.3 | 115 | 11.2 | 38
KJ120 | 10 | 5000 | 80 | 57 | 115 | 115 | 1 | 21.3 | 115 | 11.2 | 38
KJ120 | 10 | 5000 | 85 | 57 | 115 | 115 | 1 | 21.3 | 115 | 11.2 | 38
KJ120 | 10 | 5000 | 90 | 57 | 115 | 115 | 1 | 21.3 | 115 | 11.2 | 38
KJ120 | 10 | 5000 | 65 | 62 | 115 | 116.5 | 0.333 | 7.19 | 38.8 | 11.3 | 38
KJ120 | 10 | 5000 | 70 | 62 | 115 | 116.5 | 0.557 | 12.02 | 64.9 | 11.3 | 38
KJ120 | 10 | 5000 | 75 | 62 | 115 | 116.5 | 0.782 | 16.87 | 91.1 | 11.3 | 38
KJ120 | 10 | 5000 | 80 | 62 | 115 | 116.5 | 0.987 | 21.3 | 115 | 11.3 | 38
KJ120 | 10 | 5000 | 85 | 62 | 115 | 116.5 | 0.987 | 21.3 | 115 | 11.3 | 38
KJ120 | 10 | 5000 | 90 | 62 | 115 | 116.5 | 0.987 | 21.3 | 115 | 11.3 | 38
KJ120 | 10 | 5000 | 70 | 67 | 115 | 118 | 0.335 | 7.31 | 39.5 | 11.4 | 38
KJ120 | 10 | 5000 | 75 | 67 | 115 | 118 | 0.552 | 12.06 | 65.1 | 11.4 | 38
KJ120 | 10 | 5000 | 80 | 67 | 115 | 118 | 0.769 | 16.8 | 90.7 | 11.4 | 38
KJ120 | 10 | 5000 | 85 | 67 | 115 | 118 | 0.892 | 19.5 | 105.3 | 11.4 | 38
KJ120 | 10 | 5000 | 90 | 67 | 115 | 118 | 0.974 | 21.28 | 114.9 | 11.4 | 38
KJ120 | 10 | 5000 | 75 | 72 | 115 | 120.1 | 0.326 | 7.24 | 39.1 | 11.6 | 38
KJ120 | 10 | 5000 | 80 | 72 | 115 | 120.1 | 0.535 | 11.89 | 64.2 | 11.6 | 38
KJ120 | 10 | 5000 | 85 | 72 | 115 | 120.1 | 0.743 | 16.52 | 89.2 | 11.6 | 38
KJ120 | 10 | 5000 | 90 | 72 | 115 | 120.1 | 0.952 | 21.17 | 114.3 | 11.6 | 38
KJ120 | 10 | 5000 | 65 | 57 | 125 | 108.3 | 0.546 | 10.94 | 59.1 | 12.5 | 38
KJ120 | 10 | 5000 | 70 | 57 | 125 | 108.3 | 0.795 | 15.94 | 86.1 | 12.5 | 38
KJ120 | 10 | 5000 | 75 | 57 | 125 | 108.3 | 1 | 20.06 | 108.3 | 12.5 | 38
KJ120 | 10 | 5000 | 80 | 57 | 125 | 108.3 | 1 | 20.06 | 108.3 | 12.5 | 38
KJ120 | 10 | 5000 | 85 | 57 | 125 | 108.3 | 1 | 20.06 | 108.3 | 12.5 | 38
KJ120 | 10 | 5000 | 90 | 57 | 125 | 108.3 | 1 | 20.06 | 108.3 | 12.5 | 38
KJ120 | 10 | 5000 | 65 | 62 | 125 | 109.4 | 0.313 | 6.33 | 34.2 | 12.6 | 38
KJ120 | 10 | 5000 | 70 | 62 | 125 | 109.4 | 0.553 | 11.2 | 60.5 | 12.6 | 38
KJ120 | 10 | 5000 | 75 | 62 | 125 | 109.4 | 0.794 | 16.09 | 86.9 | 12.6 | 38
KJ120 | 10 | 5000 | 80 | 62 | 125 | 109.4 | 0.989 | 20.04 | 108.2 | 12.6 | 38
KJ120 | 10 | 5000 | 85 | 62 | 125 | 109.4 | 0.989 | 20.04 | 108.2 | 12.6 | 38
KJ120 | 10 | 5000 | 90 | 62 | 125 | 109.4 | 0.989 | 20.04 | 108.2 | 12.6 | 38
KJ120 | 10 | 5000 | 70 | 67 | 125 | 110.5 | 0.317 | 6.48 | 35 | 12.7 | 38
KJ120 | 10 | 5000 | 75 | 67 | 125 | 110.5 | 0.549 | 11.24 | 60.7 | 12.7 | 38
KJ120 | 10 | 5000 | 80 | 67 | 125 | 110.5 | 0.782 | 16 | 86.4 | 12.7 | 38
KJ120 | 10 | 5000 | 85 | 67 | 125 | 110.5 | 0.899 | 18.39 | 99.3 | 12.7 | 38
KJ120 | 10 | 5000 | 90 | 67 | 125 | 110.5 | 0.977 | 20 | 108 | 12.7 | 38
KJ120 | 10 | 5000 | 75 | 72 | 125 | 110.5 | 0.312 | 6.39 | 34.5 | 12.9 | 38
KJ120 | 10 | 5000 | 80 | 72 | 125 | 110.5 | 0.539 | 11.04 | 59.6 | 12.9 | 38
KJ120 | 10 | 5000 | 85 | 72 | 125 | 110.5 | 0.767 | 15.69 | 84.7 | 12.9 | 38
KJ120 | 10 | 5000 | 90 | 72 | 125 | 110.5 | 0.994 | 20.33 | 109.8 | 12.9 | 38
KJ150 | 12.5 | 3125 | 65 | 62 | 75 | 150.4 | 0.449 | 20.03 | 67.6 | 8.5 | 39
KJ150 | 12.5 | 3125 | 70 | 62 | 75 | 150.4 | 0.559 | 24.92 | 84.1 | 8.5 | 39
KJ150 | 12.5 | 3125 | 75 | 62 | 75 | 150.4 | 0.662 | 29.48 | 99.5 | 8.5 | 39
KJ150 | 12.5 | 3125 | 80 | 62 | 75 | 150.4 | 0.778 | 34.67 | 117 | 8.5 | 39
KJ150 | 12.5 | 3125 | 85 | 62 | 75 | 150.4 | 0.908 | 40.44 | 136.5 | 8.5 | 39
KJ150 | 12.5 | 3125 | 90 | 62 | 75 | 150.4 | 1 | 44.56 | 150.4 | 8.5 | 39
KJ150 | 12.5 | 3125 | 70 | 67 | 75 | 168.9 | 0.413 | 20.68 | 69.8 | 8.5 | 39
KJ150 | 12.5 | 3125 | 75 | 67 | 75 | 168.9 | 0.507 | 25.36 | 85.6 | 8.5 | 39
KJ150 | 12.5 | 3125 | 80 | 67 | 75 | 168.9 | 0.602 | 30.13 | 101.7 | 8.5 | 39
KJ150 | 12.5 | 3125 | 85 | 67 | 75 | 168.9 | 0.699 | 34.96 | 118 | 8.5 | 39
KJ150 | 12.5 | 3125 | 90 | 67 | 75 | 168.9 | 0.795 | 39.79 | 134.3 | 8.5 | 39
KJ150 | 12.5 | 3125 | 75 | 72 | 75 | 187.5 | 0.378 | 21.01 | 70.9 | 8.5 | 39
KJ150 | 12.5 | 3125 | 80 | 72 | 75 | 187.5 | 0.461 | 25.6 | 86.4 | 8.5 | 39
KJ150 | 12.5 | 3125 | 85 | 72 | 75 | 187.5 | 0.543 | 30.16 | 101.8 | 8.5 | 39
KJ150 | 12.5 | 3125 | 90 | 72 | 75 | 187.5 | 0.626 | 34.76 | 117.3 | 8.5 | 39
KJ150 | 12.5 | 3125 | 80 | 77 | 75 | 206.1 | 0.345 | 21.07 | 71.1 | 8.5 | 39
KJ150 | 12.5 | 3125 | 85 | 77 | 75 | 206.1 | 0.416 | 25.39 | 85.7 | 8.5 | 39
KJ150 | 12.5 | 3125 | 90 | 77 | 75 | 206.1 | 0.487 | 29.72 | 100.3 | 8.5 | 39
KJ150 | 12.5 | 3125 | 65 | 62 | 85 | 147.6 | 0.434 | 18.99 | 64.1 | 9.8 | 39
KJ150 | 12.5 | 3125 | 70 | 62 | 85 | 147.6 | 0.541 | 23.67 | 79.9 | 9.8 | 39
KJ150 | 12.5 | 3125 | 75 | 62 | 85 | 147.6 | 0.644 | 28.18 | 95.1 | 9.8 | 39
KJ150 | 12.5 | 3125 | 80 | 62 | 85 | 147.6 | 0.755 | 33.01 | 111.4 | 9.8 | 39
KJ150 | 12.5 | 3125 | 85 | 62 | 85 | 147.6 | 0.886 | 38.76 | 130.8 | 9.8 | 39
KJ150 | 12.5 | 3125 | 90 | 62 | 85 | 147.6 | 1 | 43.73 | 147.6 | 9.8 | 39
KJ150 | 12.5 | 3125 | 70 | 67 | 85 | 160.3 | 0.405 | 19.23 | 64.9 | 9.9 | 39
KJ150 | 12.5 | 3125 | 75 | 67 | 85 | 160.3 | 0.503 | 23.91 | 80.7 | 9.9 | 39
KJ150 | 12.5 | 3125 | 80 | 67 | 85 | 160.3 | 0.603 | 28.65 | 96.7 | 9.9 | 39
KJ150 | 12.5 | 3125 | 85 | 67 | 85 | 160.3 | 0.716 | 34.01 | 114.8 | 9.9 | 39
KJ150 | 12.5 | 3125 | 90 | 67 | 85 | 160.3 | 0.83 | 39.41 | 133 | 9.9 | 39
KJ150 | 12.5 | 3125 | 75 | 72 | 85 | 179.4 | 0.368 | 19.56 | 66 | 9.9 | 39
KJ150 | 12.5 | 3125 | 80 | 72 | 85 | 179.4 | 0.457 | 24.3 | 82 | 9.9 | 39
KJ150 | 12.5 | 3125 | 85 | 72 | 85 | 179.4 | 0.546 | 29.04 | 98 | 9.9 | 39
KJ150 | 12.5 | 3125 | 90 | 72 | 85 | 179.4 | 0.635 | 33.78 | 114 | 9.9 | 39
KJ150 | 12.5 | 3125 | 80 | 77 | 85 | 198.6 | 0.339 | 19.94 | 67.3 | 9.9 | 39
KJ150 | 12.5 | 3125 | 85 | 77 | 85 | 198.6 | 0.409 | 24.06 | 81.2 | 9.9 | 39
KJ150 | 12.5 | 3125 | 90 | 77 | 85 | 198.6 | 0.479 | 28.18 | 95.1 | 9.9 | 39
KJ150 | 12.5 | 3125 | 65 | 62 | 95 | 144.8 | 0.419 | 17.96 | 60.6 | 11.2 | 39
KJ150 | 12.5 | 3125 | 70 | 62 | 95 | 144.8 | 0.523 | 22.43 | 75.7 | 11.2 | 39
KJ150 | 12.5 | 3125 | 75 | 62 | 95 | 144.8 | 0.627 | 26.9 | 90.8 | 11.2 | 39
KJ150 | 12.5 | 3125 | 80 | 62 | 95 | 144.8 | 0.731 | 31.35 | 105.8 | 11.2 | 39
KJ150 | 12.5 | 3125 | 85 | 62 | 95 | 144.8 | 0.863 | 37.04 | 125 | 11.2 | 39
KJ150 | 12.5 | 3125 | 90 | 62 | 95 | 144.8 | 0.996 | 42.73 | 144.2 | 11.2 | 39
KJ150 | 12.5 | 3125 | 70 | 67 | 95 | 151.6 | 0.396 | 17.81 | 60.1 | 11.2 | 39
KJ150 | 12.5 | 3125 | 75 | 67 | 95 | 151.6 | 0.501 | 22.49 | 75.9 | 11.2 | 39
KJ150 | 12.5 | 3125 | 80 | 67 | 95 | 151.6 | 0.605 | 27.17 | 91.7 | 11.2 | 39
KJ150 | 12.5 | 3125 | 85 | 67 | 95 | 151.6 | 0.737 | 33.1 | 111.7 | 11.2 | 39
KJ150 | 12.5 | 3125 | 90 | 67 | 95 | 151.6 | 0.868 | 38.99 | 131.6 | 11.2 | 39
KJ150 | 12.5 | 3125 | 75 | 72 | 95 | 171.4 | 0.356 | 18.1 | 61.1 | 11.3 | 39
KJ150 | 12.5 | 3125 | 80 | 72 | 95 | 171.4 | 0.453 | 22.99 | 77.6 | 11.3 | 39
KJ150 | 12.5 | 3125 | 85 | 72 | 95 | 171.4 | 0.55 | 27.91 | 94.2 | 11.3 | 39
KJ150 | 12.5 | 3125 | 90 | 72 | 95 | 171.4 | 0.646 | 32.83 | 110.8 | 11.3 | 39
KJ150 | 12.5 | 3125 | 80 | 77 | 95 | 191.2 | 0.333 | 18.84 | 63.6 | 11.4 | 39
KJ150 | 12.5 | 3125 | 85 | 77 | 95 | 191.2 | 0.401 | 22.73 | 76.7 | 11.4 | 39
KJ150 | 12.5 | 3125 | 90 | 77 | 95 | 191.2 | 0.47 | 26.64 | 89.9 | 11.4 | 39
KJ150 | 12.5 | 3125 | 65 | 62 | 105 | 137.6 | 0.409 | 16.68 | 56.3 | 12.8 | 39
KJ150 | 12.5 | 3125 | 70 | 62 | 105 | 137.6 | 0.52 | 21.19 | 71.5 | 12.8 | 39
KJ150 | 12.5 | 3125 | 75 | 62 | 105 | 137.6 | 0.631 | 25.72 | 86.8 | 12.8 | 39
KJ150 | 12.5 | 3125 | 80 | 62 | 105 | 137.6 | 0.741 | 30.22 | 102 | 12.8 | 39
KJ150 | 12.5 | 3125 | 85 | 62 | 105 | 137.6 | 0.872 | 35.56 | 120 | 12.8 | 39
KJ150 | 12.5 | 3125 | 90 | 62 | 105 | 137.6 | 1 | 40.77 | 137.6 | 12.8 | 39
KJ150 | 12.5 | 3125 | 70 | 67 | 105 | 141.7 | 0.393 | 16.5 | 55.7 | 12.8 | 39
KJ150 | 12.5 | 3125 | 75 | 67 | 105 | 141.7 | 0.505 | 21.21 | 71.6 | 12.8 | 39
KJ150 | 12.5 | 3125 | 80 | 67 | 105 | 141.7 | 0.618 | 25.93 | 87.5 | 12.8 | 39
KJ150 | 12.5 | 3125 | 85 | 67 | 105 | 141.7 | 0.759 | 31.85 | 107.5 | 12.8 | 39
KJ150 | 12.5 | 3125 | 90 | 67 | 105 | 141.7 | 0.9 | 37.78 | 127.5 | 12.8 | 39
KJ150 | 12.5 | 3125 | 75 | 72 | 105 | 160.3 | 0.352 | 16.74 | 56.5 | 13 | 39
KJ150 | 12.5 | 3125 | 80 | 72 | 105 | 160.3 | 0.455 | 21.63 | 73 | 13 | 39
KJ150 | 12.5 | 3125 | 85 | 72 | 105 | 160.3 | 0.559 | 26.55 | 89.6 | 13 | 39
KJ150 | 12.5 | 3125 | 90 | 72 | 105 | 160.3 | 0.662 | 31.44 | 106.1 | 13 | 39
KJ150 | 12.5 | 3125 | 80 | 77 | 105 | 178.8 | 0.327 | 17.33 | 58.5 | 13.1 | 39
KJ150 | 12.5 | 3125 | 85 | 77 | 105 | 178.8 | 0.401 | 21.24 | 71.7 | 13.1 | 39
KJ150 | 12.5 | 3125 | 90 | 77 | 105 | 178.8 | 0.474 | 25.13 | 84.8 | 13.1 | 39
KJ150 | 12.5 | 3125 | 65 | 62 | 115 | 130.5 | 0.398 | 15.41 | 52 | 14.4 | 40
KJ150 | 12.5 | 3125 | 70 | 62 | 115 | 130.5 | 0.516 | 19.97 | 67.4 | 14.4 | 40
KJ150 | 12.5 | 3125 | 75 | 62 | 115 | 130.5 | 0.634 | 24.53 | 82.8 | 14.4 | 40
KJ150 | 12.5 | 3125 | 80 | 62 | 115 | 130.5 | 0.752 | 29.1 | 98.2 | 14.4 | 40
KJ150 | 12.5 | 3125 | 85 | 62 | 115 | 130.5 | 0.881 | 34.07 | 115 | 14.4 | 40
KJ150 | 12.5 | 3125 | 90 | 62 | 115 | 130.5 | 1 | 38.67 | 130.5 | 14.4 | 40
KJ150 | 12.5 | 3125 | 70 | 67 | 115 | 131.8 | 0.39 | 15.23 | 51.4 | 14.5 | 40
KJ150 | 12.5 | 3125 | 75 | 67 | 115 | 131.8 | 0.511 | 19.94 | 67.3 | 14.5 | 40
KJ150 | 12.5 | 3125 | 80 | 67 | 115 | 131.8 | 0.632 | 24.68 | 83.3 | 14.5 | 40
KJ150 | 12.5 | 3125 | 85 | 67 | 115 | 131.8 | 0.784 | 30.61 | 103.3 | 14.5 | 40
KJ150 | 12.5 | 3125 | 90 | 67 | 115 | 131.8 | 0.936 | 36.53 | 123.3 | 14.5 | 40
KJ150 | 12.5 | 3125 | 75 | 72 | 115 | 149.1 | 0.348 | 15.38 | 51.9 | 14.7 | 40
KJ150 | 12.5 | 3125 | 80 | 72 | 115 | 149.1 | 0.459 | 20.27 | 68.4 | 14.7 | 40
KJ150 | 12.5 | 3125 | 85 | 72 | 115 | 149.1 | 0.57 | 25.19 | 85 | 14.7 | 40
KJ150 | 12.5 | 3125 | 90 | 72 | 115 | 149.1 | 0.681 | 30.07 | 101.5 | 14.7 | 40
KJ150 | 12.5 | 3125 | 80 | 77 | 115 | 166.5 | 0.321 | 15.85 | 53.5 | 14.8 | 40
KJ150 | 12.5 | 3125 | 85 | 77 | 115 | 166.5 | 0.4 | 19.73 | 66.6 | 14.8 | 40
KJ150 | 12.5 | 3125 | 90 | 77 | 115 | 166.5 | 0.479 | 23.61 | 79.7 | 14.8 | 40
KJ150 | 12.5 | 3125 | 65 | 62 | 125 | 123.3 | 0.387 | 14.13 | 47.7 | 16.1 | 40
KJ150 | 12.5 | 3125 | 70 | 62 | 125 | 123.3 | 0.513 | 18.76 | 63.3 | 16.1 | 40
KJ150 | 12.5 | 3125 | 75 | 62 | 125 | 123.3 | 0.64 | 23.38 | 78.9 | 16.1 | 40
KJ150 | 12.5 | 3125 | 80 | 62 | 125 | 123.3 | 0.766 | 28 | 94.5 | 16.1 | 40
KJ150 | 12.5 | 3125 | 85 | 62 | 125 | 123.3 | 0.891 | 32.56 | 109.9 | 16.1 | 40
KJ150 | 12.5 | 3125 | 90 | 62 | 125 | 123.3 | 1 | 36.53 | 123.3 | 16.1 | 40
KJ150 | 12.5 | 3125 | 70 | 67 | 125 | 121.9 | 0.386 | 13.93 | 47 | 16.1 | 40
KJ150 | 12.5 | 3125 | 75 | 67 | 125 | 121.9 | 0.518 | 18.7 | 63.1 | 16.1 | 40
KJ150 | 12.5 | 3125 | 80 | 67 | 125 | 121.9 | 0.649 | 23.44 | 79.1 | 16.1 | 40
KJ150 | 12.5 | 3125 | 85 | 67 | 125 | 121.9 | 0.813 | 29.36 | 99.1 | 16.1 | 40
KJ150 | 12.5 | 3125 | 90 | 67 | 125 | 121.9 | 0.977 | 35.29 | 119.1 | 16.1 | 40
KJ150 | 12.5 | 3125 | 75 | 72 | 125 | 138 | 0.343 | 14.01 | 47.3 | 16.4 | 40
KJ150 | 12.5 | 3125 | 80 | 72 | 125 | 138 | 0.462 | 18.9 | 63.8 | 16.4 | 40
KJ150 | 12.5 | 3125 | 85 | 72 | 125 | 138 | 0.582 | 23.79 | 80.3 | 16.4 | 40
KJ150 | 12.5 | 3125 | 90 | 72 | 125 | 138 | 0.702 | 28.71 | 96.9 | 16.4 | 40
KJ150 | 12.5 | 3125 | 80 | 77 | 125 | 154.1 | 0.315 | 14.37 | 48.5 | 16.6 | 40
KJ150 | 12.5 | 3125 | 85 | 77 | 125 | 154.1 | 0.399 | 18.22 | 61.5 | 16.6 | 40
KJ150 | 12.5 | 3125 | 90 | 77 | 125 | 154.1 | 0.484 | 22.1 | 74.6 | 16.6 | 40
KJ150 | 12.5 | 3750 | 65 | 57 | 75 | 145.9 | 0.591 | 21.28 | 86.2 | 8.5 | 39
KJ150 | 12.5 | 3750 | 70 | 57 | 75 | 145.9 | 0.729 | 26.27 | 106.4 | 8.5 | 39
KJ150 | 12.5 | 3750 | 75 | 57 | 75 | 145.9 | 0.868 | 31.26 | 126.6 | 8.5 | 39
KJ150 | 12.5 | 3750 | 80 | 57 | 75 | 145.9 | 1 | 36.02 | 145.9 | 8.5 | 39
KJ150 | 12.5 | 3750 | 85 | 57 | 75 | 145.9 | 1 | 36.02 | 145.9 | 8.5 | 39
KJ150 | 12.5 | 3750 | 90 | 57 | 75 | 145.9 | 1 | 36.02 | 145.9 | 8.5 | 39
KJ150 | 12.5 | 3750 | 65 | 62 | 75 | 160 | 0.43 | 16.99 | 68.8 | 8.5 | 39
KJ150 | 12.5 | 3750 | 70 | 62 | 75 | 160 | 0.552 | 21.83 | 88.4 | 8.5 | 39
KJ150 | 12.5 | 3750 | 75 | 62 | 75 | 160 | 0.671 | 26.49 | 107.3 | 8.5 | 39
KJ150 | 12.5 | 3750 | 80 | 62 | 75 | 160 | 0.799 | 31.56 | 127.8 | 8.5 | 39
KJ150 | 12.5 | 3750 | 85 | 62 | 75 | 160 | 0.911 | 36 | 145.8 | 8.5 | 39
KJ150 | 12.5 | 3750 | 90 | 62 | 75 | 160 | 0.911 | 36 | 145.8 | 8.5 | 39
KJ150 | 12.5 | 3750 | 70 | 67 | 75 | 174 | 0.405 | 17.41 | 70.5 | 8.5 | 39
KJ150 | 12.5 | 3750 | 75 | 67 | 75 | 174 | 0.514 | 22.1 | 89.5 | 8.5 | 39
KJ150 | 12.5 | 3750 | 80 | 67 | 75 | 174 | 0.626 | 26.89 | 108.9 | 8.5 | 39
KJ150 | 12.5 | 3750 | 85 | 67 | 75 | 174 | 0.734 | 31.53 | 127.7 | 8.5 | 39
KJ150 | 12.5 | 3750 | 90 | 67 | 75 | 174 | 0.833 | 35.8 | 145 | 8.5 | 39
KJ150 | 12.5 | 3750 | 75 | 72 | 75 | 192.5 | 0.37 | 17.58 | 71.2 | 8.5 | 39
KJ150 | 12.5 | 3750 | 80 | 72 | 75 | 192.5 | 0.467 | 22.2 | 89.9 | 8.5 | 39
KJ150 | 12.5 | 3750 | 85 | 72 | 75 | 192.5 | 0.564 | 26.81 | 108.6 | 8.5 | 39
KJ150 | 12.5 | 3750 | 90 | 72 | 75 | 192.5 | 0.661 | 31.41 | 127.2 | 8.5 | 39
KJ150 | 12.5 | 3750 | 80 | 77 | 75 | 211 | 0.336 | 17.53 | 71 | 8.5 | 39
KJ150 | 12.5 | 3750 | 85 | 77 | 75 | 211 | 0.424 | 22.07 | 89.4 | 8.5 | 39
KJ150 | 12.5 | 3750 | 90 | 77 | 75 | 211 | 0.511 | 26.62 | 107.8 | 8.5 | 39
KJ150 | 12.5 | 3750 | 65 | 57 | 85 | 146.4 | 0.569 | 20.57 | 83.3 | 9.8 | 39
KJ150 | 12.5 | 3750 | 70 | 57 | 85 | 146.4 | 0.702 | 25.36 | 102.7 | 9.8 | 39
KJ150 | 12.5 | 3750 | 75 | 57 | 85 | 146.4 | 0.834 | 30.15 | 122.1 | 9.8 | 39
KJ150 | 12.5 | 3750 | 80 | 57 | 85 | 146.4 | 0.967 | 34.94 | 141.5 | 9.8 | 39
KJ150 | 12.5 | 3750 | 85 | 57 | 85 | 146.4 | 1 | 36.15 | 146.4 | 9.8 | 39
KJ150 | 12.5 | 3750 | 90 | 57 | 85 | 146.4 | 1 | 36.15 | 146.4 | 9.8 | 39
KJ150 | 12.5 | 3750 | 65 | 62 | 85 | 155.9 | 0.416 | 16 | 64.8 | 9.8 | 39
KJ150 | 12.5 | 3750 | 70 | 62 | 85 | 155.9 | 0.54 | 20.79 | 84.2 | 9.8 | 39
KJ150 | 12.5 | 3750 | 75 | 62 | 85 | 155.9 | 0.661 | 25.46 | 103.1 | 9.8 | 39
KJ150 | 12.5 | 3750 | 80 | 62 | 85 | 155.9 | 0.788 | 30.32 | 122.8 | 9.8 | 39
KJ150 | 12.5 | 3750 | 85 | 62 | 85 | 155.9 | 0.899 | 34.59 | 140.1 | 9.8 | 39
KJ150 | 12.5 | 3750 | 90 | 62 | 85 | 155.9 | 0.924 | 35.56 | 144 | 9.8 | 39
KJ150 | 12.5 | 3750 | 70 | 67 | 85 | 165.5 | 0.396 | 16.2 | 65.6 | 9.8 | 39
KJ150 | 12.5 | 3750 | 75 | 67 | 85 | 165.5 | 0.512 | 20.94 | 84.8 | 9.8 | 39
KJ150 | 12.5 | 3750 | 80 | 67 | 85 | 165.5 | 0.63 | 25.73 | 104.2 | 9.8 | 39
KJ150 | 12.5 | 3750 | 85 | 67 | 85 | 165.5 | 0.749 | 30.62 | 124 | 9.8 | 39
KJ150 | 12.5 | 3750 | 90 | 67 | 85 | 165.5 | 0.869 | 35.53 | 143.9 | 9.8 | 39
KJ150 | 12.5 | 3750 | 75 | 72 | 85 | 183.6 | 0.361 | 16.37 | 66.3 | 9.9 | 39
KJ150 | 12.5 | 3750 | 80 | 72 | 85 | 183.6 | 0.466 | 21.11 | 85.5 | 9.9 | 39
KJ150 | 12.5 | 3750 | 85 | 72 | 85 | 183.6 | 0.57 | 25.85 | 104.7 | 9.9 | 39
KJ150 | 12.5 | 3750 | 90 | 72 | 85 | 183.6 | 0.675 | 30.59 | 123.9 | 9.9 | 39
KJ150 | 12.5 | 3750 | 80 | 77 | 85 | 201.7 | 0.331 | 16.49 | 66.8 | 9.9 | 39
KJ150 | 12.5 | 3750 | 85 | 77 | 85 | 201.7 | 0.423 | 21.09 | 85.4 | 9.9 | 39
KJ150 | 12.5 | 3750 | 90 | 77 | 85 | 201.7 | 0.516 | 25.68 | 104 | 9.9 | 39
KJ150 | 12.5 | 3750 | 65 | 57 | 95 | 146.8 | 0.548 | 19.85 | 80.4 | 11.1 | 39
KJ150 | 12.5 | 3750 | 70 | 57 | 95 | 146.8 | 0.674 | 24.44 | 99 | 11.1 | 39
KJ150 | 12.5 | 3750 | 75 | 57 | 95 | 146.8 | 0.801 | 29.04 | 117.6 | 11.1 | 39
KJ150 | 12.5 | 3750 | 80 | 57 | 95 | 146.8 | 0.928 | 33.63 | 136.2 | 11.1 | 39
KJ150 | 12.5 | 3750 | 85 | 57 | 95 | 146.8 | 1 | 36.25 | 146.8 | 11.1 | 39
KJ150 | 12.5 | 3750 | 90 | 57 | 95 | 146.8 | 1 | 36.25 | 146.8 | 11.1 | 39
KJ150 | 12.5 | 3750 | 65 | 62 | 95 | 151.9 | 0.401 | 15.04 | 60.9 | 11.2 | 39
KJ150 | 12.5 | 3750 | 70 | 62 | 95 | 151.9 | 0.526 | 19.73 | 79.9 | 11.2 | 39
KJ150 | 12.5 | 3750 | 75 | 62 | 95 | 151.9 | 0.651 | 24.42 | 98.9 | 11.2 | 39
KJ150 | 12.5 | 3750 | 80 | 62 | 95 | 151.9 | 0.776 | 29.09 | 117.8 | 11.2 | 39
KJ150 | 12.5 | 3750 | 85 | 62 | 95 | 151.9 | 0.885 | 33.19 | 134.4 | 11.2 | 39
KJ150 | 12.5 | 3750 | 90 | 62 | 95 | 151.9 | 0.955 | 35.8 | 145 | 11.2 | 39
KJ150 | 12.5 | 3750 | 70 | 67 | 95 | 157.1 | 0.386 | 14.99 | 60.7 | 11.2 | 39
KJ150 | 12.5 | 3750 | 75 | 67 | 95 | 157.1 | 0.51 | 19.78 | 80.1 | 11.2 | 39
KJ150 | 12.5 | 3750 | 80 | 67 | 95 | 157.1 | 0.633 | 24.57 | 99.5 | 11.2 | 39
KJ150 | 12.5 | 3750 | 85 | 67 | 95 | 157.1 | 0.766 | 29.7 | 120.3 | 11.2 | 39
KJ150 | 12.5 | 3750 | 90 | 67 | 95 | 157.1 | 0.898 | 34.84 | 141.1 | 11.2 | 39
KJ150 | 12.5 | 3750 | 75 | 72 | 95 | 174.7 | 0.351 | 15.14 | 61.3 | 11.3 | 39
KJ150 | 12.5 | 3750 | 80 | 72 | 95 | 174.7 | 0.464 | 20.02 | 81.1 | 11.3 | 39
KJ150 | 12.5 | 3750 | 85 | 72 | 95 | 174.7 | 0.577 | 24.89 | 100.8 | 11.3 | 39
KJ150 | 12.5 | 3750 | 90 | 72 | 95 | 174.7 | 0.69 | 29.78 | 120.6 | 11.3 | 39
KJ150 | 12.5 | 3750 | 80 | 77 | 95 | 192.4 | 0.326 | 15.48 | 62.7 | 11.4 | 39
KJ150 | 12.5 | 3750 | 85 | 77 | 95 | 192.4 | 0.423 | 20.1 | 81.4 | 11.4 | 39
KJ150 | 12.5 | 3750 | 90 | 77 | 95 | 192.4 | 0.52 | 24.72 | 100.1 | 11.4 | 39
KJ150 | 12.5 | 3750 | 65 | 57 | 105 | 141.4 | 0.539 | 18.81 | 76.2 | 12.8 | 39
KJ150 | 12.5 | 3750 | 70 | 57 | 105 | 141.4 | 0.672 | 23.46 | 95 | 12.8 | 39
KJ150 | 12.5 | 3750 | 75 | 57 | 105 | 141.4 | 0.805 | 28.1 | 113.8 | 12.8 | 39
KJ150 | 12.5 | 3750 | 80 | 57 | 105 | 141.4 | 0.938 | 32.74 | 132.6 | 12.8 | 39
KJ150 | 12.5 | 3750 | 85 | 57 | 105 | 141.4 | 1 | 34.91 | 141.4 | 12.8 | 39
KJ150 | 12.5 | 3750 | 90 | 57 | 105 | 141.4 | 1 | 34.91 | 141.4 | 12.8 | 39
KJ150 | 12.5 | 3750 | 65 | 62 | 105 | 144.5 | 0.391 | 13.95 | 56.5 | 12.8 | 39
KJ150 | 12.5 | 3750 | 70 | 62 | 105 | 144.5 | 0.523 | 18.67 | 75.6 | 12.8 | 39
KJ150 | 12.5 | 3750 | 75 | 62 | 105 | 144.5 | 0.656 | 23.41 | 94.8 | 12.8 | 39
KJ150 | 12.5 | 3750 | 80 | 62 | 105 | 144.5 | 0.788 | 28.12 | 113.9 | 12.8 | 39
KJ150 | 12.5 | 3750 | 85 | 62 | 105 | 144.5 | 0.892 | 31.83 | 128.9 | 12.8 | 39
KJ150 | 12.5 | 3750 | 90 | 62 | 105 | 144.5 | 0.976 | 34.81 | 141 | 12.8 | 39
KJ150 | 12.5 | 3750 | 70 | 67 | 105 | 147.5 | 0.382 | 13.9 | 56.3 | 12.9 | 39
KJ150 | 12.5 | 3750 | 75 | 67 | 105 | 147.5 | 0.513 | 18.69 | 75.7 | 12.9 | 39
KJ150 | 12.5 | 3750 | 80 | 67 | 105 | 147.5 | 0.645 | 23.51 | 95.2 | 12.9 | 39
KJ150 | 12.5 | 3750 | 85 | 67 | 105 | 147.5 | 0.783 | 28.52 | 115.5 | 12.9 | 39
KJ150 | 12.5 | 3750 | 90 | 67 | 105 | 147.5 | 0.92 | 33.51 | 135.7 | 12.9 | 39
KJ150 | 12.5 | 3750 | 75 | 72 | 105 | 163.6 | 0.347 | 14 | 56.7 | 13 | 39
KJ150 | 12.5 | 3750 | 80 | 72 | 105 | 163.6 | 0.468 | 18.89 | 76.5 | 13 | 39
KJ150 | 12.5 | 3750 | 85 | 72 | 105 | 163.6 | 0.588 | 23.75 | 96.2 | 13 | 39
KJ150 | 12.5 | 3750 | 90 | 72 | 105 | 163.6 | 0.709 | 28.64 | 116 | 13 | 39
KJ150 | 12.5 | 3750 | 80 | 77 | 105 | 179.7 | 0.322 | 14.27 | 57.8 | 13.1 | 39
KJ150 | 12.5 | 3750 | 85 | 77 | 105 | 179.7 | 0.428 | 19.01 | 77 | 13.1 | 39
KJ150 | 12.5 | 3750 | 90 | 77 | 105 | 179.7 | 0.535 | 23.75 | 96.2 | 13.1 | 39
KJ150 | 12.5 | 3750 | 65 | 57 | 115 | 136 | 0.529 | 17.75 | 71.9 | 14.5 | 40
KJ150 | 12.5 | 3750 | 70 | 57 | 115 | 136 | 0.668 | 22.44 | 90.9 | 14.5 | 40
KJ150 | 12.5 | 3750 | 75 | 57 | 115 | 136 | 0.808 | 27.14 | 109.9 | 14.5 | 40
KJ150 | 12.5 | 3750 | 80 | 57 | 115 | 136 | 0.948 | 31.83 | 128.9 | 14.5 | 40
KJ150 | 12.5 | 3750 | 85 | 57 | 115 | 136 | 1 | 33.58 | 136 | 14.5 | 40
KJ150 | 12.5 | 3750 | 90 | 57 | 115 | 136 | 1 | 33.58 | 136 | 14.5 | 40
KJ150 | 12.5 | 3750 | 65 | 62 | 115 | 136 | 0.383 | 12.86 | 52.1 | 14.5 | 40
KJ150 | 12.5 | 3750 | 70 | 62 | 115 | 136 | 0.525 | 17.63 | 71.4 | 14.5 | 40
KJ150 | 12.5 | 3750 | 75 | 62 | 115 | 136 | 0.666 | 22.37 | 90.6 | 14.5 | 40
KJ150 | 12.5 | 3750 | 80 | 62 | 115 | 136 | 0.808 | 27.14 | 109.9 | 14.5 | 40
KJ150 | 12.5 | 3750 | 85 | 62 | 115 | 136 | 0.908 | 30.49 | 123.5 | 14.5 | 40
KJ150 | 12.5 | 3750 | 90 | 62 | 115 | 136 | 1 | 33.58 | 136 | 14.5 | 40
KJ150 | 12.5 | 3750 | 70 | 67 | 115 | 136 | 0.382 | 12.81 | 51.9 | 14.5 | 40
KJ150 | 12.5 | 3750 | 75 | 67 | 115 | 136 | 0.525 | 17.63 | 71.4 | 14.5 | 40
KJ150 | 12.5 | 3750 | 80 | 67 | 115 | 136 | 0.668 | 22.44 | 90.9 | 14.5 | 40
KJ150 | 12.5 | 3750 | 85 | 67 | 115 | 136 | 0.813 | 27.31 | 110.6 | 14.5 | 40
KJ150 | 12.5 | 3750 | 90 | 67 | 115 | 136 | 0.959 | 32.2 | 130.4 | 14.5 | 40
KJ150 | 12.5 | 3750 | 75 | 72 | 115 | 152.5 | 0.342 | 12.86 | 52.1 | 14.7 | 40
KJ150 | 12.5 | 3750 | 80 | 72 | 115 | 152.5 | 0.471 | 17.73 | 71.8 | 14.7 | 40
KJ150 | 12.5 | 3750 | 85 | 72 | 115 | 152.5 | 0.601 | 22.62 | 91.6 | 14.7 | 40
KJ150 | 12.5 | 3750 | 90 | 72 | 115 | 152.5 | 0.73 | 27.48 | 111.3 | 14.7 | 40
KJ150 | 12.5 | 3750 | 80 | 77 | 115 | 167.1 | 0.316 | 13.04 | 52.8 | 14.8 | 40
KJ150 | 12.5 | 3750 | 85 | 77 | 115 | 167.1 | 0.434 | 17.9 | 72.5 | 14.8 | 40
KJ150 | 12.5 | 3750 | 90 | 77 | 115 | 167.1 | 0.552 | 22.79 | 92.3 | 14.8 | 40
KJ150 | 12.5 | 3750 | 65 | 57 | 125 | 130.7 | 0.518 | 16.72 | 67.7 | 16.1 | 40
KJ150 | 12.5 | 3750 | 70 | 57 | 125 | 130.7 | 0.665 | 21.46 | 86.9 | 16.1 | 40
KJ150 | 12.5 | 3750 | 75 | 57 | 125 | 130.7 | 0.812 | 26.2 | 106.1 | 16.1 | 40
KJ150 | 12.5 | 3750 | 80 | 57 | 125 | 130.7 | 0.959 | 30.94 | 125.3 | 16.1 | 40
KJ150 | 12.5 | 3750 | 85 | 57 | 125 | 130.7 | 0.996 | 32.15 | 130.2 | 16.1 | 40
KJ150 | 12.5 | 3750 | 90 | 57 | 125 | 130.7 | 1 | 32.27 | 130.7 | 16.1 | 40
KJ150 | 12.5 | 3750 | 65 | 62 | 125 | 130.7 | 0.365 | 11.78 | 47.7 | 16.1 | 40
KJ150 | 12.5 | 3750 | 70 | 62 | 125 | 130.7 | 0.513 | 16.57 | 67.1 | 16.1 | 40
KJ150 | 12.5 | 3750 | 75 | 62 | 125 | 130.7 | 0.662 | 21.36 | 86.5 | 16.1 | 40
KJ150 | 12.5 | 3750 | 80 | 62 | 125 | 130.7 | 0.81 | 26.15 | 105.9 | 16.1 | 40
KJ150 | 12.5 | 3750 | 85 | 62 | 125 | 130.7 | 0.903 | 29.14 | 118 | 16.1 | 40
KJ150 | 12.5 | 3750 | 90 | 62 | 125 | 130.7 | 0.995 | 32.12 | 130.1 | 16.1 | 40
KJ150 | 12.5 | 3750 | 70 | 67 | 125 | 130.8 | 0.362 | 11.7 | 47.4 | 16.2 | 40
KJ150 | 12.5 | 3750 | 75 | 67 | 125 | 130.8 | 0.512 | 16.54 | 67 | 16.2 | 40
KJ150 | 12.5 | 3750 | 80 | 67 | 125 | 130.8 | 0.662 | 21.38 | 86.6 | 16.2 | 40
KJ150 | 12.5 | 3750 | 85 | 67 | 125 | 130.8 | 0.809 | 26.12 | 105.8 | 16.2 | 40
KJ150 | 12.5 | 3750 | 90 | 67 | 125 | 130.8 | 0.956 | 30.89 | 125.1 | 16.2 | 40
KJ150 | 12.5 | 3750 | 75 | 72 | 125 | 141.4 | 0.335 | 11.7 | 47.4 | 16.4 | 40
KJ150 | 12.5 | 3750 | 80 | 72 | 125 | 141.4 | 0.475 | 16.59 | 67.2 | 16.4 | 40
KJ150 | 12.5 | 3750 | 85 | 72 | 125 | 141.4 | 0.615 | 21.48 | 87 | 16.4 | 40
KJ150 | 12.5 | 3750 | 90 | 72 | 125 | 141.4 | 0.755 | 26.35 | 106.7 | 16.4 | 40
KJ150 | 12.5 | 3750 | 80 | 77 | 125 | 154.4 | 0.31 | 11.8 | 47.8 | 16.5 | 40
KJ150 | 12.5 | 3750 | 85 | 77 | 125 | 154.4 | 0.441 | 16.81 | 68.1 | 16.5 | 40
KJ150 | 12.5 | 3750 | 90 | 77 | 125 | 154.4 | 0.573 | 21.83 | 88.4 | 16.5 | 40
KJ150 | 12.5 | 4375 | 65 | 57 | 75 | 160 | 0.568 | 19.24 | 90.9 | 8.4 | 39
KJ150 | 12.5 | 4375 | 70 | 57 | 75 | 160 | 0.714 | 24.19 | 114.3 | 8.4 | 39
KJ150 | 12.5 | 4375 | 75 | 57 | 75 | 160 | 0.861 | 29.14 | 137.7 | 8.4 | 39
KJ150 | 12.5 | 4375 | 80 | 57 | 75 | 160 | 1 | 33.86 | 160 | 8.4 | 39
KJ150 | 12.5 | 4375 | 85 | 57 | 75 | 160 | 1 | 33.86 | 160 | 8.4 | 39
KJ150 | 12.5 | 4375 | 90 | 57 | 75 | 160 | 1 | 33.86 | 160 | 8.4 | 39
KJ150 | 12.5 | 4375 | 65 | 62 | 75 | 169.5 | 0.412 | 14.79 | 69.9 | 8.4 | 39
KJ150 | 12.5 | 4375 | 70 | 62 | 75 | 169.5 | 0.547 | 19.64 | 92.8 | 8.4 | 39
KJ150 | 12.5 | 4375 | 75 | 62 | 75 | 169.5 | 0.678 | 24.34 | 115 | 8.4 | 39
KJ150 | 12.5 | 4375 | 80 | 62 | 75 | 169.5 | 0.818 | 29.33 | 138.6 | 8.4 | 39
KJ150 | 12.5 | 4375 | 85 | 62 | 75 | 169.5 | 0.914 | 32.8 | 155 | 8.4 | 39
KJ150 | 12.5 | 4375 | 90 | 62 | 75 | 169.5 | 0.941 | 33.76 | 159.5 | 8.4 | 39
KJ150 | 12.5 | 4375 | 70 | 67 | 75 | 179 | 0.398 | 15.07 | 71.2 | 8.4 | 39
KJ150 | 12.5 | 4375 | 75 | 67 | 75 | 179 | 0.522 | 19.79 | 93.5 | 8.4 | 39
KJ150 | 12.5 | 4375 | 80 | 67 | 75 | 179 | 0.648 | 24.55 | 116 | 8.4 | 39
KJ150 | 12.5 | 4375 | 85 | 67 | 75 | 179 | 0.768 | 29.1 | 137.5 | 8.4 | 39
KJ150 | 12.5 | 4375 | 90 | 67 | 75 | 179 | 0.888 | 33.65 | 159 | 8.4 | 39
KJ150 | 12.5 | 4375 | 75 | 72 | 75 | 197.5 | 0.362 | 15.13 | 71.5 | 8.4 | 39
KJ150 | 12.5 | 4375 | 80 | 72 | 75 | 197.5 | 0.473 | 19.77 | 93.4 | 8.4 | 39
KJ150 | 12.5 | 4375 | 85 | 72 | 75 | 197.5 | 0.584 | 24.4 | 115.3 | 8.4 | 39
KJ150 | 12.5 | 4375 | 90 | 72 | 75 | 197.5 | 0.695 | 29.04 | 137.2 | 8.4 | 39
KJ150 | 12.5 | 4375 | 80 | 77 | 75 | 216 | 0.328 | 15.01 | 70.9 | 8.4 | 39
KJ150 | 12.5 | 4375 | 85 | 77 | 75 | 216 | 0.431 | 19.7 | 93.1 | 8.4 | 39
KJ150 | 12.5 | 4375 | 90 | 77 | 75 | 216 | 0.534 | 24.4 | 115.3 | 8.4 | 39
KJ150 | 12.5 | 4375 | 65 | 57 | 85 | 157.9 | 0.554 | 18.5 | 87.4 | 9.8 | 39
KJ150 | 12.5 | 4375 | 70 | 57 | 85 | 157.9 | 0.7 | 23.39 | 110.5 | 9.8 | 39
KJ150 | 12.5 | 4375 | 75 | 57 | 85 | 157.9 | 0.847 | 28.3 | 133.7 | 9.8 | 39
KJ150 | 12.5 | 4375 | 80 | 57 | 85 | 157.9 | 0.991 | 33.12 | 156.5 | 9.8 | 39
KJ150 | 12.5 | 4375 | 85 | 57 | 85 | 157.9 | 1 | 33.42 | 157.9 | 9.8 | 39
KJ150 | 12.5 | 4375 | 90 | 57 | 85 | 157.9 | 1 | 33.42 | 157.9 | 9.8 | 39
KJ150 | 12.5 | 4375 | 65 | 62 | 85 | 164.3 | 0.399 | 13.86 | 65.5 | 9.8 | 39
KJ150 | 12.5 | 4375 | 70 | 62 | 85 | 164.3 | 0.538 | 18.71 | 88.4 | 9.8 | 39
KJ150 | 12.5 | 4375 | 75 | 62 | 85 | 164.3 | 0.676 | 23.49 | 111 | 9.8 | 39
KJ150 | 12.5 | 4375 | 80 | 62 | 85 | 164.3 | 0.817 | 28.4 | 134.2 | 9.8 | 39
KJ150 | 12.5 | 4375 | 85 | 62 | 85 | 164.3 | 0.909 | 31.62 | 149.4 | 9.8 | 39
KJ150 | 12.5 | 4375 | 90 | 62 | 85 | 164.3 | 0.949 | 33.02 | 156 | 9.8 | 39
KJ150 | 12.5 | 4375 | 70 | 67 | 85 | 170.8 | 0.388 | 14.03 | 66.3 | 9.8 | 39
KJ150 | 12.5 | 4375 | 75 | 67 | 85 | 170.8 | 0.52 | 18.81 | 88.9 | 9.8 | 39
KJ150 | 12.5 | 4375 | 80 | 67 | 85 | 170.8 | 0.653 | 23.62 | 111.6 | 9.8 | 39
KJ150 | 12.5 | 4375 | 85 | 67 | 85 | 170.8 | 0.78 | 28.19 | 133.2 | 9.8 | 39
KJ150 | 12.5 | 4375 | 90 | 67 | 85 | 170.8 | 0.906 | 32.76 | 154.8 | 9.8 | 39
KJ150 | 12.5 | 4375 | 75 | 72 | 85 | 187.8 | 0.355 | 14.1 | 66.6 | 9.9 | 39
KJ150 | 12.5 | 4375 | 80 | 72 | 85 | 187.8 | 0.474 | 18.84 | 89 | 9.9 | 39
KJ150 | 12.5 | 4375 | 85 | 72 | 85 | 187.8 | 0.593 | 23.58 | 111.4 | 9.9 | 39
KJ150 | 12.5 | 4375 | 90 | 72 | 85 | 187.8 | 0.712 | 28.32 | 133.8 | 9.9 | 39
KJ150 | 12.5 | 4375 | 80 | 77 | 85 | 204.8 | 0.324 | 14.05 | 66.4 | 9.9 | 39
KJ150 | 12.5 | 4375 | 85 | 77 | 85 | 204.8 | 0.437 | 18.96 | 89.6 | 9.9 | 39
KJ150 | 12.5 | 4375 | 90 | 77 | 85 | 204.8 | 0.551 | 23.87 | 112.8 | 9.9 | 39
KJ150 | 12.5 | 4375 | 65 | 57 | 95 | 155.7 | 0.538 | 17.74 | 83.8 | 11.1 | 39
KJ150 | 12.5 | 4375 | 70 | 57 | 95 | 155.7 | 0.685 | 22.58 | 106.7 | 11.1 | 39
KJ150 | 12.5 | 4375 | 75 | 57 | 95 | 155.7 | 0.832 | 27.43 | 129.6 | 11.1 | 39
KJ150 | 12.5 | 4375 | 80 | 57 | 95 | 155.7 | 0.979 | 32.28 | 152.5 | 11.1 | 39
KJ150 | 12.5 | 4375 | 85 | 57 | 95 | 155.7 | 1 | 32.95 | 155.7 | 11.1 | 39
KJ150 | 12.5 | 4375 | 90 | 57 | 95 | 155.7 | 1 | 32.95 | 155.7 | 11.1 | 39
KJ150 | 12.5 | 4375 | 65 | 62 | 95 | 159.1 | 0.384 | 12.93 | 61.1 | 11.2 | 39
KJ150 | 12.5 | 4375 | 70 | 62 | 95 | 159.1 | 0.528 | 17.78 | 84 | 11.2 | 39
KJ150 | 12.5 | 4375 | 75 | 62 | 95 | 159.1 | 0.673 | 22.65 | 107 | 11.2 | 39
KJ150 | 12.5 | 4375 | 80 | 62 | 95 | 159.1 | 0.816 | 27.49 | 129.9 | 11.2 | 39
KJ150 | 12.5 | 4375 | 85 | 62 | 95 | 159.1 | 0.903 | 30.41 | 143.7 | 11.2 | 39
KJ150 | 12.5 | 4375 | 90 | 62 | 95 | 159.1 | 0.974 | 32.8 | 155 | 11.2 | 39
KJ150 | 12.5 | 4375 | 70 | 67 | 95 | 162.6 | 0.378 | 12.99 | 61.4 | 11.2 | 39
KJ150 | 12.5 | 4375 | 75 | 67 | 95 | 162.6 | 0.518 | 17.84 | 84.3 | 11.2 | 39
KJ150 | 12.5 | 4375 | 80 | 67 | 95 | 162.6 | 0.659 | 22.69 | 107.2 | 11.2 | 39
KJ150 | 12.5 | 4375 | 85 | 67 | 95 | 162.6 | 0.792 | 27.26 | 128.8 | 11.2 | 39
KJ150 | 12.5 | 4375 | 90 | 67 | 95 | 162.6 | 0.926 | 31.85 | 150.5 | 11.2 | 39
KJ150 | 12.5 | 4375 | 75 | 72 | 95 | 178.1 | 0.346 | 13.04 | 61.6 | 11.3 | 39
KJ150 | 12.5 | 4375 | 80 | 72 | 95 | 178.1 | 0.474 | 17.88 | 84.5 | 11.3 | 39
KJ150 | 12.5 | 4375 | 85 | 72 | 95 | 178.1 | 0.603 | 22.73 | 107.4 | 11.3 | 39
KJ150 | 12.5 | 4375 | 90 | 72 | 95 | 178.1 | 0.732 | 27.6 | 130.4 | 11.3 | 39
KJ150 | 12.5 | 4375 | 80 | 77 | 95 | 193.6 | 0.32 | 13.1 | 61.9 | 11.4 | 39
KJ150 | 12.5 | 4375 | 85 | 77 | 95 | 193.6 | 0.445 | 18.22 | 86.1 | 11.4 | 39
KJ150 | 12.5 | 4375 | 90 | 77 | 95 | 193.6 | 0.569 | 23.32 | 110.2 | 11.4 | 39
KJ150 | 12.5 | 4375 | 65 | 57 | 105 | 149.3 | 0.532 | 16.83 | 79.5 | 12.8 | 39
KJ150 | 12.5 | 4375 | 70 | 57 | 105 | 149.3 | 0.687 | 21.71 | 102.6 | 12.8 | 39
KJ150 | 12.5 | 4375 | 75 | 57 | 105 | 149.3 | 0.841 | 26.58 | 125.6 | 12.8 | 39
KJ150 | 12.5 | 4375 | 80 | 57 | 105 | 149.3 | 0.995 | 31.45 | 148.6 | 12.8 | 39
KJ150 | 12.5 | 4375 | 85 | 57 | 105 | 149.3 | 1 | 31.6 | 149.3 | 12.8 | 39
KJ150 | 12.5 | 4375 | 90 | 57 | 105 | 149.3 | 1 | 31.6 | 149.3 | 12.8 | 39
KJ150 | 12.5 | 4375 | 65 | 62 | 105 | 151.3 | 0.375 | 12 | 56.7 | 12.9 | 39
KJ150 | 12.5 | 4375 | 70 | 62 | 105 | 151.3 | 0.527 | 16.87 | 79.7 | 12.9 | 39
KJ150 | 12.5 | 4375 | 75 | 62 | 105 | 151.3 | 0.679 | 21.74 | 102.7 | 12.9 | 39
KJ150 | 12.5 | 4375 | 80 | 62 | 105 | 151.3 | 0.831 | 26.6 | 125.7 | 12.9 | 39
KJ150 | 12.5 | 4375 | 85 | 62 | 105 | 151.3 | 0.911 | 29.19 | 137.9 | 12.9 | 39
KJ150 | 12.5 | 4375 | 90 | 62 | 105 | 151.3 | 0.978 | 31.32 | 148 | 12.9 | 39
KJ150 | 12.5 | 4375 | 70 | 67 | 105 | 153.3 | 0.371 | 12.04 | 56.9 | 12.9 | 39
KJ150 | 12.5 | 4375 | 75 | 67 | 105 | 153.3 | 0.521 | 16.89 | 79.8 | 12.9 | 39
KJ150 | 12.5 | 4375 | 80 | 67 | 105 | 153.3 | 0.671 | 21.76 | 102.8 | 12.9 | 39
KJ150 | 12.5 | 4375 | 85 | 67 | 105 | 153.3 | 0.805 | 26.12 | 123.4 | 12.9 | 39
KJ150 | 12.5 | 4375 | 90 | 67 | 105 | 153.3 | 0.939 | 30.48 | 144 | 12.9 | 39
KJ150 | 12.5 | 4375 | 75 | 72 | 105 | 167 | 0.341 | 12.04 | 56.9 | 13 | 39
KJ150 | 12.5 | 4375 | 80 | 72 | 105 | 167 | 0.478 | 16.91 | 79.9 | 13 | 39
KJ150 | 12.5 | 4375 | 85 | 72 | 105 | 167 | 0.616 | 21.76 | 102.8 | 13 | 39
KJ150 | 12.5 | 4375 | 90 | 72 | 105 | 167 | 0.753 | 26.62 | 125.8 | 13 | 39
KJ150 | 12.5 | 4375 | 80 | 77 | 105 | 180.7 | 0.315 | 12.06 | 57 | 13.1 | 39
KJ150 | 12.5 | 4375 | 85 | 77 | 105 | 180.7 | 0.455 | 17.42 | 82.3 | 13.1 | 39
KJ150 | 12.5 | 4375 | 90 | 77 | 105 | 180.7 | 0.595 | 22.75 | 107.5 | 13.1 | 39
KJ150 | 12.5 | 4375 | 65 | 57 | 115 | 143 | 0.526 | 15.92 | 75.2 | 14.5 | 40
KJ150 | 12.5 | 4375 | 70 | 57 | 115 | 143 | 0.688 | 20.83 | 98.4 | 14.5 | 40
KJ150 | 12.5 | 4375 | 75 | 57 | 115 | 143 | 0.85 | 25.74 | 121.6 | 14.5 | 40
KJ150 | 12.5 | 4375 | 80 | 57 | 115 | 143 | 1 | 30.26 | 143 | 14.5 | 40
KJ150 | 12.5 | 4375 | 85 | 57 | 115 | 143 | 1 | 30.26 | 143 | 14.5 | 40
KJ150 | 12.5 | 4375 | 90 | 57 | 115 | 143 | 1 | 30.26 | 143 | 14.5 | 40
KJ150 | 12.5 | 4375 | 65 | 62 | 115 | 143.5 | 0.364 | 11.07 | 52.3 | 14.5 | 40
KJ150 | 12.5 | 4375 | 70 | 62 | 115 | 143.5 | 0.525 | 15.96 | 75.4 | 14.5 | 40
KJ150 | 12.5 | 4375 | 75 | 62 | 115 | 143.5 | 0.686 | 20.85 | 98.5 | 14.5 | 40
KJ150 | 12.5 | 4375 | 80 | 62 | 115 | 143.5 | 0.847 | 25.74 | 121.6 | 14.5 | 40
KJ150 | 12.5 | 4375 | 85 | 62 | 115 | 143.5 | 0.92 | 27.94 | 132 | 14.5 | 40
KJ150 | 12.5 | 4375 | 90 | 62 | 115 | 143.5 | 0.992 | 30.14 | 142.4 | 14.5 | 40
KJ150 | 12.5 | 4375 | 70 | 67 | 115 | 144 | 0.363 | 11.07 | 52.3 | 14.6 | 40
KJ150 | 12.5 | 4375 | 75 | 67 | 115 | 144 | 0.524 | 15.96 | 75.4 | 14.6 | 40
KJ150 | 12.5 | 4375 | 80 | 67 | 115 | 144 | 0.683 | 20.83 | 98.4 | 14.6 | 40
KJ150 | 12.5 | 4375 | 85 | 67 | 115 | 144 | 0.819 | 24.97 | 118 | 14.6 | 40
KJ150 | 12.5 | 4375 | 90 | 67 | 115 | 144 | 0.956 | 29.12 | 137.6 | 14.6 | 40
KJ150 | 12.5 | 4375 | 75 | 72 | 115 | 155.8 | 0.336 | 11.07 | 52.3 | 14.7 | 40
KJ150 | 12.5 | 4375 | 80 | 72 | 115 | 155.8 | 0.483 | 15.94 | 75.3 | 14.7 | 40
KJ150 | 12.5 | 4375 | 85 | 72 | 115 | 155.8 | 0.63 | 20.78 | 98.2 | 14.7 | 40
KJ150 | 12.5 | 4375 | 90 | 72 | 115 | 155.8 | 0.778 | 25.65 | 121.2 | 14.7 | 40
KJ150 | 12.5 | 4375 | 80 | 77 | 115 | 167.7 | 0.311 | 11.03 | 52.1 | 14.8 | 40
KJ150 | 12.5 | 4375 | 85 | 77 | 115 | 167.7 | 0.468 | 16.61 | 78.5 | 14.8 | 40
KJ150 | 12.5 | 4375 | 90 | 77 | 115 | 167.7 | 0.625 | 22.18 | 104.8 | 14.8 | 40
KJ150 | 12.5 | 4375 | 65 | 57 | 125 | 134.4 | 0.528 | 15.01 | 70.9 | 16.2 | 40
KJ150 | 12.5 | 4375 | 70 | 57 | 125 | 134.4 | 0.701 | 19.94 | 94.2 | 16.2 | 40
KJ150 | 12.5 | 4375 | 75 | 57 | 125 | 134.4 | 0.874 | 24.87 | 117.5 | 16.2 | 40
KJ150 | 12.5 | 4375 | 80 | 57 | 125 | 134.4 | 1 | 28.44 | 134.4 | 16.2 | 40
KJ150 | 12.5 | 4375 | 85 | 57 | 125 | 134.4 | 1 | 28.44 | 134.4 | 16.2 | 40
KJ150 | 12.5 | 4375 | 90 | 57 | 125 | 134.4 | 1 | 28.44 | 134.4 | 16.2 | 40
KJ150 | 12.5 | 4375 | 65 | 62 | 125 | 134.5 | 0.355 | 10.12 | 47.8 | 16.2 | 40
KJ150 | 12.5 | 4375 | 70 | 62 | 125 | 134.5 | 0.528 | 15.03 | 71 | 16.2 | 40
KJ150 | 12.5 | 4375 | 75 | 62 | 125 | 134.5 | 0.7 | 19.94 | 94.2 | 16.2 | 40
KJ150 | 12.5 | 4375 | 80 | 62 | 125 | 134.5 | 0.873 | 24.85 | 117.4 | 16.2 | 40
KJ150 | 12.5 | 4375 | 85 | 62 | 125 | 134.5 | 0.938 | 26.71 | 126.2 | 16.2 | 40
KJ150 | 12.5 | 4375 | 90 | 62 | 125 | 134.5 | 0.999 | 28.44 | 134.4 | 16.2 | 40
KJ150 | 12.5 | 4375 | 70 | 67 | 125 | 134.7 | 0.355 | 10.12 | 47.8 | 16.2 | 40
KJ150 | 12.5 | 4375 | 75 | 67 | 125 | 134.7 | 0.526 | 15.01 | 70.9 | 16.2 | 40
KJ150 | 12.5 | 4375 | 80 | 67 | 125 | 134.7 | 0.698 | 19.89 | 94 | 16.2 | 40
KJ150 | 12.5 | 4375 | 85 | 67 | 125 | 134.7 | 0.836 | 23.83 | 112.6 | 16.2 | 40
KJ150 | 12.5 | 4375 | 90 | 67 | 125 | 134.7 | 0.973 | 27.75 | 131.1 | 16.2 | 40
KJ150 | 12.5 | 4375 | 75 | 72 | 125 | 144.7 | 0.329 | 10.07 | 47.6 | 16.4 | 40
KJ150 | 12.5 | 4375 | 80 | 72 | 125 | 144.7 | 0.488 | 14.94 | 70.6 | 16.4 | 40
KJ150 | 12.5 | 4375 | 85 | 72 | 125 | 144.7 | 0.647 | 19.81 | 93.6 | 16.4 | 40
KJ150 | 12.5 | 4375 | 90 | 72 | 125 | 144.7 | 0.806 | 24.68 | 116.6 | 16.4 | 40
KJ150 | 12.5 | 4375 | 80 | 77 | 125 | 154.7 | 0.305 | 9.99 | 47.2 | 16.5 | 40
KJ150 | 12.5 | 4375 | 85 | 77 | 125 | 154.7 | 0.483 | 15.81 | 74.7 | 16.5 | 40
KJ150 | 12.5 | 4375 | 90 | 77 | 125 | 154.7 | 0.66 | 21.61 | 102.1 | 16.5 | 40
KJ150 | 12.5 | 5000 | 65 | 57 | 75 | 174.1 | 0.549 | 17.7 | 95.6 | 8.4 | 39
KJ150 | 12.5 | 5000 | 70 | 57 | 75 | 174.1 | 0.702 | 22.65 | 122.3 | 8.4 | 39
KJ150 | 12.5 | 5000 | 75 | 57 | 75 | 174.1 | 0.855 | 27.57 | 148.9 | 8.4 | 39
KJ150 | 12.5 | 5000 | 80 | 57 | 75 | 174.1 | 1 | 32.24 | 174.1 | 8.4 | 39
KJ150 | 12.5 | 5000 | 85 | 57 | 75 | 174.1 | 1 | 32.24 | 174.1 | 8.4 | 39
KJ150 | 12.5 | 5000 | 90 | 57 | 75 | 174.1 | 1 | 32.24 | 174.1 | 8.4 | 39
KJ150 | 12.5 | 5000 | 65 | 62 | 75 | 179.1 | 0.396 | 13.15 | 71 | 8.4 | 39
KJ150 | 12.5 | 5000 | 70 | 62 | 75 | 179.1 | 0.542 | 17.98 | 97.1 | 8.4 | 39
KJ150 | 12.5 | 5000 | 75 | 62 | 75 | 179.1 | 0.686 | 22.74 | 122.8 | 8.4 | 39
KJ150 | 12.5 | 5000 | 80 | 62 | 75 | 179.1 | 0.834 | 27.65 | 149.3 | 8.4 | 39
KJ150 | 12.5 | 5000 | 85 | 62 | 75 | 179.1 | 0.917 | 30.43 | 164.3 | 8.4 | 39
KJ150 | 12.5 | 5000 | 90 | 62 | 75 | 179.1 | 0.967 | 32.07 | 173.2 | 8.4 | 39
KJ150 | 12.5 | 5000 | 70 | 67 | 75 | 184 | 0.391 | 13.31 | 71.9 | 8.4 | 39
KJ150 | 12.5 | 5000 | 75 | 67 | 75 | 184 | 0.53 | 18.06 | 97.5 | 8.4 | 39
KJ150 | 12.5 | 5000 | 80 | 67 | 75 | 184 | 0.669 | 22.8 | 123.1 | 8.4 | 39
KJ150 | 12.5 | 5000 | 85 | 67 | 75 | 184 | 0.801 | 27.28 | 147.3 | 8.4 | 39
KJ150 | 12.5 | 5000 | 90 | 67 | 75 | 184 | 0.932 | 31.74 | 171.4 | 8.4 | 39
KJ150 | 12.5 | 5000 | 75 | 72 | 75 | 202.5 | 0.355 | 13.31 | 71.9 | 8.4 | 39
KJ150 | 12.5 | 5000 | 80 | 72 | 75 | 202.5 | 0.479 | 17.94 | 96.9 | 8.4 | 39
KJ150 | 12.5 | 5000 | 85 | 72 | 75 | 202.5 | 0.602 | 22.59 | 122 | 8.4 | 39
KJ150 | 12.5 | 5000 | 90 | 72 | 75 | 202.5 | 0.726 | 27.24 | 147.1 | 8.4 | 39
KJ150 | 12.5 | 5000 | 80 | 77 | 75 | 221 | 0.32 | 13.11 | 70.8 | 8.4 | 39
KJ150 | 12.5 | 5000 | 85 | 77 | 75 | 221 | 0.438 | 17.93 | 96.8 | 8.4 | 39
KJ150 | 12.5 | 5000 | 90 | 77 | 75 | 221 | 0.556 | 22.74 | 122.8 | 8.4 | 39
KJ150 | 12.5 | 5000 | 65 | 57 | 85 | 169.4 | 0.54 | 16.93 | 91.4 | 9.8 | 39
KJ150 | 12.5 | 5000 | 70 | 57 | 85 | 169.4 | 0.699 | 21.93 | 118.4 | 9.8 | 39
KJ150 | 12.5 | 5000 | 75 | 57 | 85 | 169.4 | 0.858 | 26.91 | 145.3 | 9.8 | 39
KJ150 | 12.5 | 5000 | 80 | 57 | 85 | 169.4 | 1 | 31.37 | 169.4 | 9.8 | 39
KJ150 | 12.5 | 5000 | 85 | 57 | 85 | 169.4 | 1 | 31.37 | 169.4 | 9.8 | 39
KJ150 | 12.5 | 5000 | 90 | 57 | 85 | 169.4 | 1 | 31.37 | 169.4 | 9.8 | 39
KJ150 | 12.5 | 5000 | 65 | 62 | 85 | 172.7 | 0.383 | 12.26 | 66.2 | 9.8 | 39
KJ150 | 12.5 | 5000 | 70 | 62 | 85 | 172.7 | 0.537 | 17.17 | 92.7 | 9.8 | 39
KJ150 | 12.5 | 5000 | 75 | 62 | 85 | 172.7 | 0.688 | 22.02 | 118.9 | 9.8 | 39
KJ150 | 12.5 | 5000 | 80 | 62 | 85 | 172.7 | 0.843 | 26.96 | 145.6 | 9.8 | 39
KJ150 | 12.5 | 5000 | 85 | 62 | 85 | 172.7 | 0.919 | 29.39 | 158.7 | 9.8 | 39
KJ150 | 12.5 | 5000 | 90 | 62 | 85 | 172.7 | 0.973 | 31.11 | 168 | 9.8 | 39
KJ150 | 12.5 | 5000 | 70 | 67 | 85 | 176 | 0.381 | 12.41 | 67 | 9.8 | 39
KJ150 | 12.5 | 5000 | 75 | 67 | 85 | 176 | 0.528 | 17.22 | 93 | 9.8 | 39
KJ150 | 12.5 | 5000 | 80 | 67 | 85 | 176 | 0.676 | 22.04 | 119 | 9.8 | 39
KJ150 | 12.5 | 5000 | 85 | 67 | 85 | 176 | 0.809 | 26.35 | 142.3 | 9.8 | 39
KJ150 | 12.5 | 5000 | 90 | 67 | 85 | 176 | 0.941 | 30.69 | 165.7 | 9.8 | 39
KJ150 | 12.5 | 5000 | 75 | 72 | 85 | 192 | 0.348 | 12.39 | 66.9 | 9.9 | 39
KJ150 | 12.5 | 5000 | 80 | 72 | 85 | 192 | 0.482 | 17.13 | 92.5 | 9.9 | 39
KJ150 | 12.5 | 5000 | 85 | 72 | 85 | 192 | 0.615 | 21.85 | 118 | 9.9 | 39
KJ150 | 12.5 | 5000 | 90 | 72 | 85 | 192 | 0.748 | 26.59 | 143.6 | 9.9 | 39
KJ150 | 12.5 | 5000 | 80 | 77 | 85 | 207.9 | 0.317 | 12.2 | 65.9 | 9.9 | 39
KJ150 | 12.5 | 5000 | 85 | 77 | 85 | 207.9 | 0.451 | 17.37 | 93.8 | 9.9 | 39
KJ150 | 12.5 | 5000 | 90 | 77 | 85 | 207.9 | 0.585 | 22.52 | 121.6 | 9.9 | 39
KJ150 | 12.5 | 5000 | 65 | 57 | 95 | 164.6 | 0.53 | 16.17 | 87.3 | 11.2 | 39
KJ150 | 12.5 | 5000 | 70 | 57 | 95 | 164.6 | 0.695 | 21.19 | 114.4 | 11.2 | 39
KJ150 | 12.5 | 5000 | 75 | 57 | 95 | 164.6 | 0.86 | 26.22 | 141.6 | 11.2 | 39
KJ150 | 12.5 | 5000 | 80 | 57 | 95 | 164.6 | 1 | 30.48 | 164.6 | 11.2 | 39
KJ150 | 12.5 | 5000 | 85 | 57 | 95 | 164.6 | 1 | 30.48 | 164.6 | 11.2 | 39
KJ150 | 12.5 | 5000 | 90 | 57 | 95 | 164.6 | 1 | 30.48 | 164.6 | 11.2 | 39
KJ150 | 12.5 | 5000 | 65 | 62 | 95 | 166.3 | 0.369 | 11.37 | 61.4 | 11.2 | 39
KJ150 | 12.5 | 5000 | 70 | 62 | 95 | 166.3 | 0.53 | 16.33 | 88.2 | 11.2 | 39
KJ150 | 12.5 | 5000 | 75 | 62 | 95 | 166.3 | 0.692 | 21.3 | 115 | 11.2 | 39
KJ150 | 12.5 | 5000 | 80 | 62 | 95 | 166.3 | 0.853 | 26.28 | 141.9 | 11.2 | 39
KJ150 | 12.5 | 5000 | 85 | 62 | 95 | 166.3 | 0.921 | 28.35 | 153.1 | 11.2 | 39
KJ150 | 12.5 | 5000 | 90 | 62 | 95 | 166.3 | 0.987 | 30.41 | 164.2 | 11.2 | 39
KJ150 | 12.5 | 5000 | 70 | 67 | 95 | 168 | 0.369 | 11.48 | 62 | 11.2 | 39
KJ150 | 12.5 | 5000 | 75 | 67 | 95 | 168 | 0.527 | 16.39 | 88.5 | 11.2 | 39
KJ150 | 12.5 | 5000 | 80 | 67 | 95 | 168 | 0.684 | 21.28 | 114.9 | 11.2 | 39
KJ150 | 12.5 | 5000 | 85 | 67 | 95 | 168 | 0.818 | 25.44 | 137.4 | 11.2 | 39
KJ150 | 12.5 | 5000 | 90 | 67 | 95 | 168 | 0.952 | 29.61 | 159.9 | 11.2 | 39
KJ150 | 12.5 | 5000 | 75 | 72 | 95 | 181.5 | 0.341 | 11.46 | 61.9 | 11.3 | 39
KJ150 | 12.5 | 5000 | 80 | 72 | 95 | 181.5 | 0.485 | 16.3 | 88 | 11.3 | 39
KJ150 | 12.5 | 5000 | 85 | 72 | 95 | 181.5 | 0.629 | 21.13 | 114.1 | 11.3 | 39
KJ150 | 12.5 | 5000 | 90 | 72 | 95 | 181.5 | 0.772 | 25.96 | 140.2 | 11.3 | 39
KJ150 | 12.5 | 5000 | 80 | 77 | 95 | 194.9 | 0.313 | 11.3 | 61 | 11.4 | 39
KJ150 | 12.5 | 5000 | 85 | 77 | 95 | 194.9 | 0.465 | 16.8 | 90.7 | 11.4 | 39
KJ150 | 12.5 | 5000 | 90 | 77 | 95 | 194.9 | 0.618 | 22.3 | 120.4 | 11.4 | 39
KJ150 | 12.5 | 5000 | 65 | 57 | 105 | 157.2 | 0.527 | 15.35 | 82.9 | 12.9 | 39
KJ150 | 12.5 | 5000 | 70 | 57 | 105 | 157.2 | 0.701 | 20.41 | 110.2 | 12.9 | 39
KJ150 | 12.5 | 5000 | 75 | 57 | 105 | 157.2 | 0.874 | 25.44 | 137.4 | 12.9 | 39
KJ150 | 12.5 | 5000 | 80 | 57 | 105 | 157.2 | 1 | 29.11 | 157.2 | 12.9 | 39
KJ150 | 12.5 | 5000 | 85 | 57 | 105 | 157.2 | 1 | 29.11 | 157.2 | 12.9 | 39
KJ150 | 12.5 | 5000 | 90 | 57 | 105 | 157.2 | 1 | 29.11 | 157.2 | 12.9 | 39
KJ150 | 12.5 | 5000 | 65 | 62 | 105 | 158.2 | 0.36 | 10.54 | 56.9 | 12.9 | 39
KJ150 | 12.5 | 5000 | 70 | 62 | 105 | 158.2 | 0.53 | 15.52 | 83.8 | 12.9 | 39
KJ150 | 12.5 | 5000 | 75 | 62 | 105 | 158.2 | 0.7 | 20.5 | 110.7 | 12.9 | 39
KJ150 | 12.5 | 5000 | 80 | 62 | 105 | 158.2 | 0.87 | 25.48 | 137.6 | 12.9 | 39
KJ150 | 12.5 | 5000 | 85 | 62 | 105 | 158.2 | 0.928 | 27.19 | 146.8 | 12.9 | 39
KJ150 | 12.5 | 5000 | 90 | 62 | 105 | 158.2 | 0.986 | 28.89 | 156 | 12.9 | 39
KJ150 | 12.5 | 5000 | 70 | 67 | 105 | 159.1 | 0.361 | 10.63 | 57.4 | 12.9 | 39
KJ150 | 12.5 | 5000 | 75 | 67 | 105 | 159.1 | 0.527 | 15.54 | 83.9 | 12.9 | 39
KJ150 | 12.5 | 5000 | 80 | 67 | 105 | 159.1 | 0.694 | 20.44 | 110.4 | 12.9 | 39
KJ150 | 12.5 | 5000 | 85 | 67 | 105 | 159.1 | 0.826 | 24.33 | 131.4 | 12.9 | 39
KJ150 | 12.5 | 5000 | 90 | 67 | 105 | 159.1 | 0.957 | 28.2 | 152.3 | 12.9 | 39
KJ150 | 12.5 | 5000 | 75 | 72 | 105 | 170.3 | 0.336 | 10.59 | 57.2 | 13 | 39
KJ150 | 12.5 | 5000 | 80 | 72 | 105 | 170.3 | 0.489 | 15.43 | 83.3 | 13 | 39
KJ150 | 12.5 | 5000 | 85 | 72 | 105 | 170.3 | 0.643 | 20.28 | 109.5 | 13 | 39
KJ150 | 12.5 | 5000 | 90 | 72 | 105 | 170.3 | 0.796 | 25.11 | 135.6 | 13 | 39
KJ150 | 12.5 | 5000 | 80 | 77 | 105 | 181.6 | 0.309 | 10.41 | 56.2 | 13.1 | 39
KJ150 | 12.5 | 5000 | 85 | 77 | 105 | 181.6 | 0.482 | 16.22 | 87.6 | 13.1 | 39
KJ150 | 12.5 | 5000 | 90 | 77 | 105 | 181.6 | 0.655 | 22.02 | 118.9 | 13.1 | 39
KJ150 | 12.5 | 5000 | 65 | 57 | 115 | 149.9 | 0.524 | 14.56 | 78.6 | 14.6 | 40
KJ150 | 12.5 | 5000 | 70 | 57 | 115 | 149.9 | 0.706 | 19.61 | 105.9 | 14.6 | 40
KJ150 | 12.5 | 5000 | 75 | 57 | 115 | 149.9 | 0.889 | 24.67 | 133.2 | 14.6 | 40
KJ150 | 12.5 | 5000 | 80 | 57 | 115 | 149.9 | 1 | 27.76 | 149.9 | 14.6 | 40
KJ150 | 12.5 | 5000 | 85 | 57 | 115 | 149.9 | 1 | 27.76 | 149.9 | 14.6 | 40
KJ150 | 12.5 | 5000 | 90 | 57 | 115 | 149.9 | 1 | 27.76 | 149.9 | 14.6 | 40
KJ150 | 12.5 | 5000 | 65 | 62 | 115 | 150 | 0.349 | 9.7 | 52.4 | 14.6 | 40
KJ150 | 12.5 | 5000 | 70 | 62 | 115 | 150 | 0.529 | 14.7 | 79.4 | 14.6 | 40
KJ150 | 12.5 | 5000 | 75 | 62 | 115 | 150 | 0.709 | 19.69 | 106.3 | 14.6 | 40
KJ150 | 12.5 | 5000 | 80 | 62 | 115 | 150 | 0.888 | 24.67 | 133.2 | 14.6 | 40
KJ150 | 12.5 | 5000 | 85 | 62 | 115 | 150 | 0.937 | 26.02 | 140.5 | 14.6 | 40
KJ150 | 12.5 | 5000 | 90 | 62 | 115 | 150 | 0.985 | 27.37 | 147.8 | 14.6 | 40
KJ150 | 12.5 | 5000 | 70 | 67 | 115 | 150.1 | 0.352 | 9.78 | 52.8 | 14.6 | 40
KJ150 | 12.5 | 5000 | 75 | 67 | 115 | 150.1 | 0.529 | 14.7 | 79.4 | 14.6 | 40
KJ150 | 12.5 | 5000 | 80 | 67 | 115 | 150.1 | 0.706 | 19.63 | 106 | 14.6 | 40
KJ150 | 12.5 | 5000 | 85 | 67 | 115 | 150.1 | 0.835 | 23.2 | 125.3 | 14.6 | 40
KJ150 | 12.5 | 5000 | 90 | 67 | 115 | 150.1 | 0.964 | 26.8 | 144.7 | 14.6 | 40
KJ150 | 12.5 | 5000 | 75 | 72 | 115 | 159.2 | 0.33 | 9.72 | 52.5 | 14.7 | 40
KJ150 | 12.5 | 5000 | 80 | 72 | 115 | 159.2 | 0.494 | 14.57 | 78.7 | 14.7 | 40
KJ150 | 12.5 | 5000 | 85 | 72 | 115 | 159.2 | 0.659 | 19.43 | 104.9 | 14.7 | 40
KJ150 | 12.5 | 5000 | 90 | 72 | 115 | 159.2 | 0.823 | 24.26 | 131 | 14.7 | 40
KJ150 | 12.5 | 5000 | 80 | 77 | 115 | 168.3 | 0.305 | 9.52 | 51.4 | 14.8 | 40
KJ150 | 12.5 | 5000 | 85 | 77 | 115 | 168.3 | 0.501 | 15.63 | 84.4 | 14.8 | 40
KJ150 | 12.5 | 5000 | 90 | 77 | 115 | 168.3 | 0.698 | 21.74 | 117.4 | 14.8 | 40
KJ150 | 12.5 | 5000 | 65 | 57 | 125 | 141 | 0.526 | 13.74 | 74.2 | 16.2 | 40
KJ150 | 12.5 | 5000 | 70 | 57 | 125 | 141 | 0.721 | 18.81 | 101.6 | 16.2 | 40
KJ150 | 12.5 | 5000 | 75 | 57 | 125 | 141 | 0.915 | 23.89 | 129 | 16.2 | 40
KJ150 | 12.5 | 5000 | 80 | 57 | 125 | 141 | 1 | 26.11 | 141 | 16.2 | 40
KJ150 | 12.5 | 5000 | 85 | 57 | 125 | 141 | 1 | 26.11 | 141 | 16.2 | 40
KJ150 | 12.5 | 5000 | 90 | 57 | 125 | 141 | 1 | 26.11 | 141 | 16.2 | 40
KJ150 | 12.5 | 5000 | 65 | 62 | 125 | 141.1 | 0.339 | 8.87 | 47.9 | 16.3 | 40
KJ150 | 12.5 | 5000 | 70 | 62 | 125 | 141.1 | 0.531 | 13.87 | 74.9 | 16.3 | 40
KJ150 | 12.5 | 5000 | 75 | 62 | 125 | 141.1 | 0.722 | 18.87 | 101.9 | 16.3 | 40
KJ150 | 12.5 | 5000 | 80 | 62 | 125 | 141.1 | 0.914 | 23.87 | 128.9 | 16.3 | 40
KJ150 | 12.5 | 5000 | 85 | 62 | 125 | 141.1 | 0.952 | 24.87 | 134.3 | 16.3 | 40
KJ150 | 12.5 | 5000 | 90 | 62 | 125 | 141.1 | 0.989 | 25.85 | 139.6 | 16.3 | 40
KJ150 | 12.5 | 5000 | 70 | 67 | 125 | 141.1 | 0.342 | 8.94 | 48.3 | 16.3 | 40
KJ150 | 12.5 | 5000 | 75 | 67 | 125 | 141.1 | 0.531 | 13.87 | 74.9 | 16.3 | 40
KJ150 | 12.5 | 5000 | 80 | 67 | 125 | 141.1 | 0.719 | 18.8 | 101.5 | 16.3 | 40
KJ150 | 12.5 | 5000 | 85 | 67 | 125 | 141.1 | 0.845 | 22.09 | 119.3 | 16.3 | 40
KJ150 | 12.5 | 5000 | 90 | 67 | 125 | 141.1 | 0.972 | 25.39 | 137.1 | 16.3 | 40
KJ150 | 12.5 | 5000 | 75 | 72 | 125 | 148 | 0.323 | 8.85 | 47.8 | 16.4 | 40
KJ150 | 12.5 | 5000 | 80 | 72 | 125 | 148 | 0.5 | 13.7 | 74 | 16.4 | 40
KJ150 | 12.5 | 5000 | 85 | 72 | 125 | 148 | 0.677 | 18.56 | 100.2 | 16.4 | 40
KJ150 | 12.5 | 5000 | 90 | 72 | 125 | 148 | 0.855 | 23.43 | 126.5 | 16.4 | 40
KJ150 | 12.5 | 5000 | 80 | 77 | 125 | 154.9 | 0.301 | 8.63 | 46.6 | 16.4 | 40
KJ150 | 12.5 | 5000 | 85 | 77 | 125 | 154.9 | 0.524 | 15.04 | 81.2 | 16.4 | 40
KJ150 | 12.5 | 5000 | 90 | 77 | 125 | 154.9 | 0.748 | 21.46 | 115.9 | 16.4 | 40
KJ150 | 12.5 | 5625 | 65 | 57 | 75 | 188.2 | 0.533 | 16.53 | 100.4 | 8.4 | 39
KJ150 | 12.5 | 5625 | 70 | 57 | 75 | 188.2 | 0.692 | 21.43 | 130.2 | 8.4 | 39
KJ150 | 12.5 | 5625 | 75 | 57 | 75 | 188.2 | 0.85 | 26.34 | 160 | 8.4 | 39
KJ150 | 12.5 | 5625 | 80 | 57 | 75 | 188.2 | 0.977 | 30.26 | 183.8 | 8.4 | 39
KJ150 | 12.5 | 5625 | 85 | 57 | 75 | 188.2 | 0.977 | 30.26 | 183.8 | 8.4 | 39
KJ150 | 12.5 | 5625 | 90 | 57 | 75 | 188.2 | 0.977 | 30.26 | 183.8 | 8.4 | 39
KJ150 | 12.5 | 5625 | 65 | 62 | 75 | 188.6 | 0.382 | 11.87 | 72.1 | 8.4 | 39
KJ150 | 12.5 | 5625 | 70 | 62 | 75 | 188.6 | 0.538 | 16.69 | 101.4 | 8.4 | 39
KJ150 | 12.5 | 5625 | 75 | 62 | 75 | 188.6 | 0.692 | 21.48 | 130.5 | 8.4 | 39
KJ150 | 12.5 | 5625 | 80 | 62 | 75 | 188.6 | 0.849 | 26.35 | 160.1 | 8.4 | 39
KJ150 | 12.5 | 5625 | 85 | 62 | 75 | 188.6 | 0.92 | 28.58 | 173.6 | 8.4 | 39
KJ150 | 12.5 | 5625 | 90 | 62 | 75 | 188.6 | 0.975 | 30.26 | 183.8 | 8.4 | 39
KJ150 | 12.5 | 5625 | 70 | 67 | 75 | 189 | 0.384 | 11.95 | 72.6 | 8.4 | 39
KJ150 | 12.5 | 5625 | 75 | 67 | 75 | 189 | 0.537 | 16.69 | 101.4 | 8.4 | 39
KJ150 | 12.5 | 5625 | 80 | 67 | 75 | 189 | 0.689 | 21.45 | 130.3 | 8.4 | 39
KJ150 | 12.5 | 5625 | 85 | 67 | 75 | 189 | 0.831 | 25.84 | 157 | 8.4 | 39
KJ150 | 12.5 | 5625 | 90 | 67 | 75 | 189 | 0.972 | 30.26 | 183.8 | 8.4 | 39
KJ150 | 12.5 | 5625 | 75 | 72 | 75 | 207.5 | 0.348 | 11.88 | 72.2 | 8.4 | 39
KJ150 | 12.5 | 5625 | 80 | 72 | 75 | 207.5 | 0.484 | 16.54 | 100.5 | 8.4 | 39
KJ150 | 12.5 | 5625 | 85 | 72 | 75 | 207.5 | 0.621 | 21.2 | 128.8 | 8.4 | 39
KJ150 | 12.5 | 5625 | 90 | 72 | 75 | 207.5 | 0.757 | 25.86 | 157.1 | 8.4 | 39
KJ150 | 12.5 | 5625 | 65 | 57 | 85 | 180.9 | 0.528 | 15.72 | 95.5 | 9.8 | 39
KJ150 | 12.5 | 5625 | 70 | 57 | 85 | 180.9 | 0.698 | 20.77 | 126.2 | 9.8 | 39
KJ150 | 12.5 | 5625 | 75 | 57 | 85 | 180.9 | 0.867 | 25.81 | 156.8 | 9.8 | 39
KJ150 | 12.5 | 5625 | 80 | 57 | 85 | 180.9 | 0.985 | 29.32 | 178.1 | 9.8 | 39
KJ150 | 12.5 | 5625 | 85 | 57 | 85 | 180.9 | 0.985 | 29.32 | 178.1 | 9.8 | 39
KJ150 | 12.5 | 5625 | 90 | 57 | 85 | 180.9 | 0.985 | 29.32 | 178.1 | 9.8 | 39
KJ150 | 12.5 | 5625 | 65 | 62 | 85 | 181.1 | 0.369 | 11.01 | 66.9 | 9.8 | 39
KJ150 | 12.5 | 5625 | 70 | 62 | 85 | 181.1 | 0.535 | 15.95 | 96.9 | 9.8 | 39
KJ150 | 12.5 | 5625 | 75 | 62 | 85 | 181.1 | 0.7 | 20.87 | 126.8 | 9.8 | 39
KJ150 | 12.5 | 5625 | 80 | 62 | 85 | 181.1 | 0.867 | 25.84 | 157 | 9.8 | 39
KJ150 | 12.5 | 5625 | 85 | 62 | 85 | 181.1 | 0.928 | 27.65 | 168 | 9.8 | 39
KJ150 | 12.5 | 5625 | 90 | 62 | 85 | 181.1 | 0.983 | 29.3 | 178 | 9.8 | 39
KJ150 | 12.5 | 5625 | 70 | 67 | 85 | 181.2 | 0.373 | 11.13 | 67.6 | 9.8 | 39
KJ150 | 12.5 | 5625 | 75 | 67 | 85 | 181.2 | 0.535 | 15.97 | 97 | 9.8 | 39
KJ150 | 12.5 | 5625 | 80 | 67 | 85 | 181.2 | 0.698 | 20.82 | 126.5 | 9.8 | 39
KJ150 | 12.5 | 5625 | 85 | 67 | 85 | 181.2 | 0.836 | 24.94 | 151.5 | 9.8 | 39
KJ150 | 12.5 | 5625 | 90 | 67 | 85 | 181.2 | 0.975 | 29.07 | 176.6 | 9.8 | 39
KJ150 | 12.5 | 5625 | 75 | 72 | 85 | 196.1 | 0.342 | 11.05 | 67.1 | 9.8 | 39
KJ150 | 12.5 | 5625 | 80 | 72 | 85 | 196.1 | 0.489 | 15.79 | 95.9 | 9.8 | 39
KJ150 | 12.5 | 5625 | 85 | 72 | 85 | 196.1 | 0.636 | 20.53 | 124.7 | 9.8 | 39
KJ150 | 12.5 | 5625 | 90 | 72 | 85 | 196.1 | 0.783 | 25.27 | 153.5 | 9.8 | 39
KJ150 | 12.5 | 5625 | 65 | 57 | 95 | 173.5 | 0.523 | 14.93 | 90.7 | 11.2 | 39
KJ150 | 12.5 | 5625 | 70 | 57 | 95 | 173.5 | 0.704 | 20.12 | 122.2 | 11.2 | 39
KJ150 | 12.5 | 5625 | 75 | 57 | 95 | 173.5 | 0.885 | 25.28 | 153.6 | 11.2 | 39
KJ150 | 12.5 | 5625 | 80 | 57 | 95 | 173.5 | 0.994 | 28.4 | 172.5 | 11.2 | 39
KJ150 | 12.5 | 5625 | 85 | 57 | 95 | 173.5 | 0.994 | 28.4 | 172.5 | 11.2 | 39
KJ150 | 12.5 | 5625 | 90 | 57 | 95 | 173.5 | 0.994 | 28.4 | 172.5 | 11.2 | 39
KJ150 | 12.5 | 5625 | 65 | 62 | 95 | 173.5 | 0.356 | 10.16 | 61.7 | 11.2 | 39
KJ150 | 12.5 | 5625 | 70 | 62 | 95 | 173.5 | 0.533 | 15.21 | 92.4 | 11.2 | 39
KJ150 | 12.5 | 5625 | 75 | 62 | 95 | 173.5 | 0.71 | 20.26 | 123.1 | 11.2 | 39
KJ150 | 12.5 | 5625 | 80 | 62 | 95 | 173.5 | 0.887 | 25.33 | 153.9 | 11.2 | 39
KJ150 | 12.5 | 5625 | 85 | 62 | 95 | 173.5 | 0.936 | 26.73 | 162.4 | 11.2 | 39
KJ150 | 12.5 | 5625 | 90 | 62 | 95 | 173.5 | 0.985 | 28.13 | 170.9 | 11.2 | 39
KJ150 | 12.5 | 5625 | 70 | 67 | 95 | 173.5 | 0.361 | 10.3 | 62.6 | 11.2 | 39
KJ150 | 12.5 | 5625 | 75 | 67 | 95 | 173.5 | 0.534 | 15.24 | 92.6 | 11.2 | 39
KJ150 | 12.5 | 5625 | 80 | 67 | 95 | 173.5 | 0.707 | 20.18 | 122.6 | 11.2 | 39
KJ150 | 12.5 | 5625 | 85 | 67 | 95 | 173.5 | 0.841 | 24.03 | 146 | 11.2 | 39
KJ150 | 12.5 | 5625 | 90 | 67 | 95 | 173.5 | 0.976 | 27.88 | 169.4 | 11.2 | 39
KJ150 | 12.5 | 5625 | 75 | 72 | 95 | 184.8 | 0.336 | 10.22 | 62.1 | 11.3 | 39
KJ150 | 12.5 | 5625 | 80 | 72 | 95 | 184.8 | 0.495 | 15.05 | 91.4 | 11.3 | 39
KJ150 | 12.5 | 5625 | 85 | 72 | 95 | 184.8 | 0.653 | 19.87 | 120.7 | 11.3 | 39
KJ150 | 12.5 | 5625 | 90 | 72 | 95 | 184.8 | 0.812 | 24.69 | 150 | 11.3 | 39
KJ150 | 12.5 | 5625 | 65 | 57 | 105 | 165 | 0.523 | 14.21 | 86.3 | 12.9 | 39
KJ150 | 12.5 | 5625 | 70 | 57 | 105 | 165 | 0.714 | 19.39 | 117.8 | 12.9 | 39
KJ150 | 12.5 | 5625 | 75 | 57 | 105 | 165 | 0.904 | 24.56 | 149.2 | 12.9 | 39
KJ150 | 12.5 | 5625 | 80 | 57 | 105 | 165 | 0.992 | 26.93 | 163.6 | 12.9 | 39
KJ150 | 12.5 | 5625 | 85 | 57 | 105 | 165 | 0.992 | 26.93 | 163.6 | 12.9 | 39
KJ150 | 12.5 | 5625 | 90 | 57 | 105 | 165 | 0.992 | 26.93 | 163.6 | 12.9 | 39
KJ150 | 12.5 | 5625 | 65 | 62 | 105 | 165 | 0.346 | 9.4 | 57.1 | 12.9 | 39
KJ150 | 12.5 | 5625 | 70 | 62 | 105 | 165 | 0.533 | 14.47 | 87.9 | 12.9 | 39
KJ150 | 12.5 | 5625 | 75 | 62 | 105 | 165 | 0.719 | 19.52 | 118.6 | 12.9 | 39
KJ150 | 12.5 | 5625 | 80 | 62 | 105 | 165 | 0.905 | 24.59 | 149.4 | 12.9 | 39
KJ150 | 12.5 | 5625 | 85 | 62 | 105 | 165 | 0.944 | 25.63 | 155.7 | 12.9 | 39
KJ150 | 12.5 | 5625 | 90 | 62 | 105 | 165 | 0.982 | 26.68 | 162.1 | 12.9 | 39
KJ150 | 12.5 | 5625 | 70 | 67 | 105 | 165 | 0.352 | 9.55 | 58 | 12.9 | 39
KJ150 | 12.5 | 5625 | 75 | 67 | 105 | 165 | 0.533 | 14.49 | 88 | 12.9 | 39
KJ150 | 12.5 | 5625 | 80 | 67 | 105 | 165 | 0.716 | 19.44 | 118.1 | 12.9 | 39
KJ150 | 12.5 | 5625 | 85 | 67 | 105 | 165 | 0.844 | 22.93 | 139.3 | 12.9 | 39
KJ150 | 12.5 | 5625 | 90 | 67 | 105 | 165 | 0.973 | 26.44 | 160.6 | 12.9 | 39
KJ150 | 12.5 | 5625 | 75 | 72 | 105 | 173.7 | 0.33 | 9.45 | 57.4 | 13 | 39
KJ150 | 12.5 | 5625 | 80 | 72 | 105 | 173.7 | 0.5 | 14.29 | 86.8 | 13 | 39
KJ150 | 12.5 | 5625 | 85 | 72 | 105 | 173.7 | 0.668 | 19.11 | 116.1 | 13 | 39
KJ150 | 12.5 | 5625 | 90 | 72 | 105 | 173.7 | 0.837 | 23.93 | 145.4 | 13 | 39
KJ150 | 12.5 | 5625 | 65 | 57 | 115 | 156 | 0.525 | 13.48 | 81.9 | 14.6 | 40
KJ150 | 12.5 | 5625 | 70 | 57 | 115 | 156 | 0.727 | 18.67 | 113.4 | 14.6 | 40
KJ150 | 12.5 | 5625 | 75 | 57 | 115 | 156 | 0.928 | 23.84 | 144.8 | 14.6 | 40
KJ150 | 12.5 | 5625 | 80 | 57 | 115 | 156 | 0.991 | 25.45 | 154.6 | 14.6 | 40
KJ150 | 12.5 | 5625 | 85 | 57 | 115 | 156 | 0.991 | 25.45 | 154.6 | 14.6 | 40
KJ150 | 12.5 | 5625 | 90 | 57 | 115 | 156 | 0.991 | 25.45 | 154.6 | 14.6 | 40
KJ150 | 12.5 | 5625 | 65 | 62 | 115 | 156.1 | 0.337 | 8.66 | 52.6 | 14.6 | 40
KJ150 | 12.5 | 5625 | 70 | 62 | 115 | 156.1 | 0.534 | 13.71 | 83.3 | 14.6 | 40
KJ150 | 12.5 | 5625 | 75 | 62 | 115 | 156.1 | 0.731 | 18.78 | 114.1 | 14.6 | 40
KJ150 | 12.5 | 5625 | 80 | 62 | 115 | 156.1 | 0.928 | 23.85 | 144.9 | 14.6 | 40
KJ150 | 12.5 | 5625 | 85 | 62 | 115 | 156.1 | 0.955 | 24.54 | 149.1 | 14.6 | 40
KJ150 | 12.5 | 5625 | 90 | 62 | 115 | 156.1 | 0.981 | 25.22 | 153.2 | 14.6 | 40
KJ150 | 12.5 | 5625 | 70 | 67 | 115 | 156.2 | 0.341 | 8.77 | 53.3 | 14.6 | 40
KJ150 | 12.5 | 5625 | 75 | 67 | 115 | 156.2 | 0.534 | 13.73 | 83.4 | 14.6 | 40
KJ150 | 12.5 | 5625 | 80 | 67 | 115 | 156.2 | 0.727 | 18.68 | 113.5 | 14.6 | 40
KJ150 | 12.5 | 5625 | 85 | 67 | 115 | 156.2 | 0.85 | 21.84 | 132.7 | 14.6 | 40
KJ150 | 12.5 | 5625 | 90 | 67 | 115 | 156.2 | 0.972 | 24.99 | 151.8 | 14.6 | 40
KJ150 | 12.5 | 5625 | 75 | 72 | 115 | 162.5 | 0.324 | 8.67 | 52.7 | 14.7 | 40
KJ150 | 12.5 | 5625 | 80 | 72 | 115 | 162.5 | 0.505 | 13.51 | 82.1 | 14.7 | 40
KJ150 | 12.5 | 5625 | 85 | 72 | 115 | 162.5 | 0.686 | 18.35 | 111.5 | 14.7 | 40
KJ150 | 12.5 | 5625 | 90 | 72 | 115 | 162.5 | 0.867 | 23.19 | 140.9 | 14.7 | 40
KJ150 | 12.5 | 5625 | 65 | 57 | 125 | 147.3 | 0.526 | 12.76 | 77.5 | 16.3 | 40
KJ150 | 12.5 | 5625 | 70 | 57 | 125 | 147.3 | 0.74 | 17.94 | 109 | 16.3 | 40
KJ150 | 12.5 | 5625 | 75 | 57 | 125 | 147.3 | 0.953 | 23.11 | 140.4 | 16.3 | 40
KJ150 | 12.5 | 5625 | 80 | 57 | 125 | 147.3 | 0.989 | 23.98 | 145.7 | 16.3 | 40
KJ150 | 12.5 | 5625 | 85 | 57 | 125 | 147.3 | 0.989 | 23.98 | 145.7 | 16.3 | 40
KJ150 | 12.5 | 5625 | 90 | 57 | 125 | 147.3 | 0.989 | 23.98 | 145.7 | 16.3 | 40
KJ150 | 12.5 | 5625 | 65 | 62 | 125 | 147.4 | 0.326 | 7.9 | 48 | 16.3 | 40
KJ150 | 12.5 | 5625 | 70 | 62 | 125 | 147.4 | 0.535 | 12.97 | 78.8 | 16.3 | 40
KJ150 | 12.5 | 5625 | 75 | 62 | 125 | 147.4 | 0.744 | 18.04 | 109.6 | 16.3 | 40
KJ150 | 12.5 | 5625 | 80 | 62 | 125 | 147.4 | 0.953 | 23.11 | 140.4 | 16.3 | 40
KJ150 | 12.5 | 5625 | 85 | 62 | 125 | 147.4 | 0.966 | 23.44 | 142.4 | 16.3 | 40
KJ150 | 12.5 | 5625 | 90 | 62 | 125 | 147.4 | 0.979 | 23.75 | 144.3 | 16.3 | 40
KJ150 | 12.5 | 5625 | 70 | 67 | 125 | 147.5 | 0.33 | 8.02 | 48.7 | 16.3 | 40
KJ150 | 12.5 | 5625 | 75 | 67 | 125 | 147.5 | 0.534 | 12.97 | 78.8 | 16.3 | 40
KJ150 | 12.5 | 5625 | 80 | 67 | 125 | 147.5 | 0.738 | 17.93 | 108.9 | 16.3 | 40
KJ150 | 12.5 | 5625 | 85 | 67 | 125 | 147.5 | 0.854 | 20.74 | 126 | 16.3 | 40
KJ150 | 12.5 | 5625 | 90 | 67 | 125 | 147.5 | 0.969 | 23.54 | 143 | 16.3 | 40
KJ150 | 12.5 | 5625 | 75 | 72 | 125 | 151.4 | 0.317 | 7.9 | 48 | 16.4 | 40
KJ150 | 12.5 | 5625 | 80 | 72 | 125 | 151.4 | 0.511 | 12.74 | 77.4 | 16.4 | 40
KJ150 | 12.5 | 5625 | 85 | 72 | 125 | 151.4 | 0.706 | 17.6 | 106.9 | 16.4 | 40
KJ150 | 12.5 | 5625 | 90 | 72 | 125 | 151.4 | 0.9 | 22.44 | 136.3 | 16.4 | 40
KJ150 | 12.5 | 6000 | 65 | 57 | 75 | 193.8 | 0.542 | 16.22 | 105.1 | 8.3 | 39
KJ150 | 12.5 | 6000 | 70 | 57 | 75 | 193.8 | 0.713 | 21.31 | 138.1 | 8.3 | 39
KJ150 | 12.5 | 6000 | 75 | 57 | 75 | 193.8 | 0.883 | 26.42 | 171.2 | 8.3 | 39
KJ150 | 12.5 | 6000 | 80 | 57 | 75 | 193.8 | 0.998 | 29.85 | 193.4 | 8.3 | 39
KJ150 | 12.5 | 6000 | 85 | 57 | 75 | 193.8 | 0.998 | 29.85 | 193.4 | 8.3 | 39
KJ150 | 12.5 | 6000 | 90 | 57 | 75 | 193.8 | 0.998 | 29.85 | 193.4 | 8.3 | 39
KJ150 | 12.5 | 6000 | 65 | 62 | 75 | 193.4 | 0.378 | 11.3 | 73.2 | 8.3 | 39
KJ150 | 12.5 | 6000 | 70 | 62 | 75 | 193.4 | 0.547 | 16.31 | 105.7 | 8.3 | 39
KJ150 | 12.5 | 6000 | 75 | 62 | 75 | 193.4 | 0.715 | 21.34 | 138.3 | 8.3 | 39
KJ150 | 12.5 | 6000 | 80 | 62 | 75 | 193.4 | 0.883 | 26.36 | 170.8 | 8.3 | 39
KJ150 | 12.5 | 6000 | 85 | 62 | 75 | 193.4 | 0.945 | 28.21 | 182.8 | 8.3 | 39
KJ150 | 12.5 | 6000 | 90 | 62 | 75 | 193.4 | 1 | 29.85 | 193.4 | 8.3 | 39
KJ150 | 12.5 | 6000 | 70 | 67 | 75 | 194 | 0.378 | 11.31 | 73.3 | 8.3 | 39
KJ150 | 12.5 | 6000 | 75 | 67 | 75 | 194 | 0.543 | 16.27 | 105.4 | 8.3 | 39
KJ150 | 12.5 | 6000 | 80 | 67 | 75 | 194 | 0.708 | 21.2 | 137.4 | 8.3 | 39
KJ150 | 12.5 | 6000 | 85 | 67 | 75 | 194 | 0.86 | 25.74 | 166.8 | 8.3 | 39
KJ150 | 12.5 | 6000 | 90 | 67 | 75 | 194 | 0.996 | 29.81 | 193.2 | 8.3 | 39
KJ150 | 12.5 | 6000 | 75 | 72 | 75 | 212.5 | 0.341 | 11.19 | 72.5 | 8.3 | 39
KJ150 | 12.5 | 6000 | 80 | 72 | 75 | 212.5 | 0.489 | 16.05 | 104 | 8.3 | 39
KJ150 | 12.5 | 6000 | 85 | 72 | 75 | 212.5 | 0.638 | 20.91 | 135.5 | 8.3 | 39
KJ150 | 12.5 | 6000 | 90 | 72 | 75 | 212.5 | 0.786 | 25.77 | 167 | 8.3 | 39
KJ150 | 12.5 | 6000 | 65 | 57 | 85 | 185 | 0.538 | 15.37 | 99.6 | 9.8 | 39
KJ150 | 12.5 | 6000 | 70 | 57 | 85 | 185 | 0.724 | 20.68 | 134 | 9.8 | 39
KJ150 | 12.5 | 6000 | 75 | 57 | 85 | 185 | 0.91 | 25.99 | 168.4 | 9.8 | 39
KJ150 | 12.5 | 6000 | 80 | 57 | 85 | 185 | 0.999 | 28.53 | 184.9 | 9.8 | 39
KJ150 | 12.5 | 6000 | 85 | 57 | 85 | 185 | 0.999 | 28.53 | 184.9 | 9.8 | 39
KJ150 | 12.5 | 6000 | 90 | 57 | 85 | 185 | 0.999 | 28.53 | 184.9 | 9.8 | 39
KJ150 | 12.5 | 6000 | 65 | 62 | 85 | 186 | 0.363 | 10.43 | 67.6 | 9.8 | 39
KJ150 | 12.5 | 6000 | 70 | 62 | 85 | 186 | 0.544 | 15.62 | 101.2 | 9.8 | 39
KJ150 | 12.5 | 6000 | 75 | 62 | 85 | 186 | 0.725 | 20.8 | 134.8 | 9.8 | 39
KJ150 | 12.5 | 6000 | 80 | 62 | 85 | 186 | 0.905 | 25.99 | 168.4 | 9.8 | 39
KJ150 | 12.5 | 6000 | 85 | 62 | 85 | 186 | 0.953 | 27.36 | 177.3 | 9.8 | 39
KJ150 | 12.5 | 6000 | 90 | 62 | 85 | 186 | 0.994 | 28.52 | 184.8 | 9.8 | 39
KJ150 | 12.5 | 6000 | 70 | 67 | 85 | 186.5 | 0.366 | 10.54 | 68.3 | 9.8 | 39
KJ150 | 12.5 | 6000 | 75 | 67 | 85 | 186.5 | 0.542 | 15.6 | 101.1 | 9.8 | 39
KJ150 | 12.5 | 6000 | 80 | 67 | 85 | 186.5 | 0.718 | 20.66 | 133.9 | 9.8 | 39
KJ150 | 12.5 | 6000 | 85 | 67 | 85 | 186.5 | 0.862 | 24.8 | 160.7 | 9.8 | 39
KJ150 | 12.5 | 6000 | 90 | 67 | 85 | 186.5 | 0.989 | 28.47 | 184.5 | 9.8 | 39
KJ150 | 12.5 | 6000 | 75 | 72 | 85 | 200.3 | 0.336 | 10.4 | 67.4 | 9.8 | 39
KJ150 | 12.5 | 6000 | 80 | 72 | 85 | 200.3 | 0.496 | 15.34 | 99.4 | 9.8 | 39
KJ150 | 12.5 | 6000 | 85 | 72 | 85 | 200.3 | 0.656 | 20.28 | 131.4 | 9.8 | 39
KJ150 | 12.5 | 6000 | 90 | 72 | 85 | 200.3 | 0.816 | 25.22 | 163.4 | 9.8 | 39
KJ150 | 12.5 | 6000 | 65 | 57 | 95 | 179 | 0.526 | 14.52 | 94.1 | 11.2 | 39
KJ150 | 12.5 | 6000 | 70 | 57 | 95 | 179 | 0.726 | 20.05 | 129.9 | 11.2 | 39
KJ150 | 12.5 | 6000 | 75 | 57 | 95 | 179 | 0.926 | 25.57 | 165.7 | 11.2 | 39
KJ150 | 12.5 | 6000 | 80 | 57 | 95 | 179 | 0.985 | 27.22 | 176.4 | 11.2 | 39
KJ150 | 12.5 | 6000 | 85 | 57 | 95 | 179 | 0.985 | 27.22 | 176.4 | 11.2 | 39
KJ150 | 12.5 | 6000 | 90 | 57 | 95 | 179 | 0.985 | 27.22 | 176.4 | 11.2 | 39
KJ150 | 12.5 | 6000 | 65 | 62 | 95 | 179 | 0.346 | 9.55 | 61.9 | 11.2 | 39
KJ150 | 12.5 | 6000 | 70 | 62 | 95 | 179 | 0.54 | 14.91 | 96.6 | 11.2 | 39
KJ150 | 12.5 | 6000 | 75 | 62 | 95 | 179 | 0.733 | 20.25 | 131.2 | 11.2 | 39
KJ150 | 12.5 | 6000 | 80 | 62 | 95 | 179 | 0.927 | 25.6 | 165.9 | 11.2 | 39
KJ150 | 12.5 | 6000 | 85 | 62 | 95 | 179 | 0.96 | 26.51 | 171.8 | 11.2 | 39
KJ150 | 12.5 | 6000 | 90 | 62 | 95 | 179 | 0.985 | 27.21 | 176.3 | 11.2 | 39
KJ150 | 12.5 | 6000 | 70 | 67 | 95 | 179 | 0.354 | 9.77 | 63.3 | 11.2 | 39
KJ150 | 12.5 | 6000 | 75 | 67 | 95 | 179 | 0.541 | 14.94 | 96.8 | 11.2 | 39
KJ150 | 12.5 | 6000 | 80 | 67 | 95 | 179 | 0.728 | 20.12 | 130.4 | 11.2 | 39
KJ150 | 12.5 | 6000 | 85 | 67 | 95 | 179 | 0.864 | 23.86 | 154.6 | 11.2 | 39
KJ150 | 12.5 | 6000 | 90 | 67 | 95 | 179 | 0.983 | 27.16 | 176 | 11.2 | 39
KJ150 | 12.5 | 6000 | 75 | 72 | 95 | 188.2 | 0.332 | 9.63 | 62.4 | 11.3 | 39
KJ150 | 12.5 | 6000 | 80 | 72 | 95 | 188.2 | 0.504 | 14.65 | 94.9 | 11.3 | 39
KJ150 | 12.5 | 6000 | 85 | 72 | 95 | 188.2 | 0.676 | 19.65 | 127.3 | 11.3 | 39
KJ150 | 12.5 | 6000 | 90 | 72 | 95 | 188.2 | 0.849 | 24.66 | 159.8 | 11.3 | 39
KJ150 | 12.5 | 6000 | 65 | 57 | 105 | 170.3 | 0.527 | 13.84 | 89.7 | 12.9 | 39
KJ150 | 12.5 | 6000 | 70 | 57 | 105 | 170.3 | 0.736 | 19.35 | 125.4 | 12.9 | 39
KJ150 | 12.5 | 6000 | 75 | 57 | 105 | 170.3 | 0.946 | 24.86 | 161.1 | 12.9 | 39
KJ150 | 12.5 | 6000 | 80 | 57 | 105 | 170.3 | 0.982 | 25.82 | 167.3 | 12.9 | 39
KJ150 | 12.5 | 6000 | 85 | 57 | 105 | 170.3 | 0.982 | 25.82 | 167.3 | 12.9 | 39
KJ150 | 12.5 | 6000 | 90 | 57 | 105 | 170.3 | 0.982 | 25.82 | 167.3 | 12.9 | 39
KJ150 | 12.5 | 6000 | 65 | 62 | 105 | 170.5 | 0.336 | 8.84 | 57.3 | 12.9 | 39
KJ150 | 12.5 | 6000 | 70 | 62 | 105 | 170.5 | 0.54 | 14.2 | 92 | 12.9 | 39
KJ150 | 12.5 | 6000 | 75 | 62 | 105 | 170.5 | 0.743 | 19.54 | 126.6 | 12.9 | 39
KJ150 | 12.5 | 6000 | 80 | 62 | 105 | 170.5 | 0.945 | 24.88 | 161.2 | 12.9 | 39
KJ150 | 12.5 | 6000 | 85 | 62 | 105 | 170.5 | 0.966 | 25.42 | 164.7 | 12.9 | 39
KJ150 | 12.5 | 6000 | 90 | 62 | 105 | 170.5 | 0.98 | 25.79 | 167.1 | 12.9 | 39
KJ150 | 12.5 | 6000 | 70 | 67 | 105 | 170.6 | 0.343 | 9.03 | 58.5 | 12.9 | 39
KJ150 | 12.5 | 6000 | 75 | 67 | 105 | 170.6 | 0.54 | 14.21 | 92.1 | 12.9 | 39
KJ150 | 12.5 | 6000 | 80 | 67 | 105 | 170.6 | 0.737 | 19.4 | 125.7 | 12.9 | 39
KJ150 | 12.5 | 6000 | 85 | 67 | 105 | 170.6 | 0.863 | 22.73 | 147.3 | 12.9 | 39
KJ150 | 12.5 | 6000 | 90 | 67 | 105 | 170.6 | 0.979 | 25.77 | 167 | 12.9 | 39
KJ150 | 12.5 | 6000 | 75 | 72 | 105 | 177 | 0.326 | 8.9 | 57.7 | 13 | 39
KJ150 | 12.5 | 6000 | 80 | 72 | 105 | 177 | 0.51 | 13.92 | 90.2 | 13 | 39
KJ150 | 12.5 | 6000 | 85 | 72 | 105 | 177 | 0.693 | 18.94 | 122.7 | 13 | 39
KJ150 | 12.5 | 6000 | 90 | 72 | 105 | 177 | 0.877 | 23.95 | 155.2 | 13 | 39
KJ150 | 12.5 | 6000 | 65 | 57 | 115 | 162 | 0.526 | 13.15 | 85.2 | 14.6 | 40
KJ150 | 12.5 | 6000 | 70 | 57 | 115 | 162 | 0.746 | 18.64 | 120.8 | 14.6 | 40
KJ150 | 12.5 | 6000 | 75 | 57 | 115 | 162 | 0.966 | 24.15 | 156.5 | 14.6 | 40
KJ150 | 12.5 | 6000 | 80 | 57 | 115 | 162 | 0.977 | 24.43 | 158.3 | 14.6 | 40
KJ150 | 12.5 | 6000 | 85 | 57 | 115 | 162 | 0.977 | 24.43 | 158.3 | 14.6 | 40
KJ150 | 12.5 | 6000 | 90 | 57 | 115 | 162 | 0.977 | 24.43 | 158.3 | 14.6 | 40
KJ150 | 12.5 | 6000 | 65 | 62 | 115 | 162.2 | 0.325 | 8.13 | 52.7 | 14.7 | 40
KJ150 | 12.5 | 6000 | 70 | 62 | 115 | 162.2 | 0.538 | 13.47 | 87.3 | 14.7 | 40
KJ150 | 12.5 | 6000 | 75 | 62 | 115 | 162.2 | 0.752 | 18.81 | 121.9 | 14.7 | 40
KJ150 | 12.5 | 6000 | 80 | 62 | 115 | 162.2 | 0.965 | 24.17 | 156.6 | 14.7 | 40
KJ150 | 12.5 | 6000 | 85 | 62 | 115 | 162.2 | 0.972 | 24.32 | 157.6 | 14.7 | 40
KJ150 | 12.5 | 6000 | 90 | 62 | 115 | 162.2 | 0.976 | 24.43 | 158.3 | 14.7 | 40
KJ150 | 12.5 | 6000 | 70 | 67 | 115 | 162.3 | 0.331 | 8.3 | 53.8 | 14.7 | 40
KJ150 | 12.5 | 6000 | 75 | 67 | 115 | 162.3 | 0.539 | 13.49 | 87.4 | 14.7 | 40
KJ150 | 12.5 | 6000 | 80 | 67 | 115 | 162.3 | 0.746 | 18.67 | 121 | 14.7 | 40
KJ150 | 12.5 | 6000 | 85 | 67 | 115 | 162.3 | 0.863 | 21.6 | 140 | 14.7 | 40
KJ150 | 12.5 | 6000 | 90 | 67 | 115 | 162.3 | 0.975 | 24.43 | 158.3 | 14.7 | 40
KJ150 | 12.5 | 6000 | 75 | 72 | 115 | 165.9 | 0.319 | 8.16 | 52.9 | 14.7 | 40
KJ150 | 12.5 | 6000 | 80 | 72 | 115 | 165.9 | 0.515 | 13.19 | 85.5 | 14.7 | 40
KJ150 | 12.5 | 6000 | 85 | 72 | 115 | 165.9 | 0.712 | 18.23 | 118.1 | 14.7 | 40
KJ150 | 12.5 | 6000 | 90 | 72 | 115 | 165.9 | 0.908 | 23.26 | 150.7 | 14.7 | 40
KJ150 | 12.5 | 6000 | 65 | 57 | 125 | 154.4 | 0.523 | 12.47 | 80.8 | 16.4 | 40
KJ150 | 12.5 | 6000 | 70 | 57 | 125 | 154.4 | 0.753 | 17.95 | 116.3 | 16.4 | 40
KJ150 | 12.5 | 6000 | 75 | 57 | 125 | 154.4 | 0.966 | 23.02 | 149.2 | 16.4 | 40
KJ150 | 12.5 | 6000 | 80 | 57 | 125 | 154.4 | 0.966 | 23.02 | 149.2 | 16.4 | 40
KJ150 | 12.5 | 6000 | 85 | 57 | 125 | 154.4 | 0.966 | 23.02 | 149.2 | 16.4 | 40
KJ150 | 12.5 | 6000 | 90 | 57 | 125 | 154.4 | 0.966 | 23.02 | 149.2 | 16.4 | 40
KJ150 | 12.5 | 6000 | 65 | 62 | 125 | 154.4 | 0.312 | 7.42 | 48.1 | 16.4 | 40
KJ150 | 12.5 | 6000 | 70 | 62 | 125 | 154.4 | 0.536 | 12.76 | 82.7 | 16.4 | 40
KJ150 | 12.5 | 6000 | 75 | 62 | 125 | 154.4 | 0.76 | 18.1 | 117.3 | 16.4 | 40
KJ150 | 12.5 | 6000 | 80 | 62 | 125 | 154.4 | 0.966 | 23.01 | 149.1 | 16.4 | 40
KJ150 | 12.5 | 6000 | 85 | 62 | 125 | 154.4 | 0.966 | 23.01 | 149.1 | 16.4 | 40
KJ150 | 12.5 | 6000 | 90 | 62 | 125 | 154.4 | 0.966 | 23.01 | 149.1 | 16.4 | 40
KJ150 | 12.5 | 6000 | 70 | 67 | 125 | 154.4 | 0.318 | 7.58 | 49.1 | 16.4 | 40
KJ150 | 12.5 | 6000 | 75 | 67 | 125 | 154.4 | 0.536 | 12.76 | 82.7 | 16.4 | 40
KJ150 | 12.5 | 6000 | 80 | 67 | 125 | 154.4 | 0.754 | 17.96 | 116.4 | 16.4 | 40
KJ150 | 12.5 | 6000 | 85 | 67 | 125 | 154.4 | 0.859 | 20.48 | 132.7 | 16.4 | 40
KJ150 | 12.5 | 6000 | 90 | 67 | 125 | 154.4 | 0.965 | 22.99 | 149 | 16.4 | 40
KJ150 | 12.5 | 6000 | 75 | 72 | 125 | 154.7 | 0.312 | 7.44 | 48.2 | 16.4 | 40
KJ150 | 12.5 | 6000 | 80 | 72 | 125 | 154.7 | 0.523 | 12.48 | 80.9 | 16.4 | 40
KJ150 | 12.5 | 6000 | 85 | 72 | 125 | 154.7 | 0.734 | 17.52 | 113.5 | 16.4 | 40
KJ150 | 12.5 | 6000 | 90 | 72 | 125 | 154.7 | 0.945 | 22.56 | 146.2 | 16.4 | 40
LV15 | 15 | 3750 | 65 | 57 | 75 | 153.5 | 0.643 | 24.37 | 98.7 |  | 30
LV15 | 15 | 3750 | 70 | 57 | 75 | 154.1 | 0.75 | 28.54 | 115.6 |  | 30
LV15 | 15 | 3750 | 75 | 57 | 75 | 154.5 | 0.867 | 33.09 | 134 |  | 30
LV15 | 15 | 3750 | 80 | 57 | 75 | 155.2 | 0.974 | 37.31 | 151.1 |  | 30
LV15 | 15 | 3750 | 85 | 57 | 75 | 163.1 | 0.974 | 39.23 | 158.9 |  | 30
LV15 | 15 | 3750 | 90 | 57 | 75 | 171.5 | 0.974 | 41.26 | 167.1 |  | 30
LV15 | 15 | 3750 | 65 | 62 | 75 | 167.7 | 0.478 | 19.78 | 80.1 |  | 30
LV15 | 15 | 3750 | 70 | 62 | 75 | 168.3 | 0.584 | 24.27 | 98.3 |  | 30
LV15 | 15 | 3750 | 75 | 62 | 75 | 168.8 | 0.691 | 28.81 | 116.7 |  | 30
LV15 | 15 | 3750 | 80 | 62 | 75 | 169.1 | 0.799 | 33.36 | 135.1 |  | 30
LV15 | 15 | 3750 | 85 | 62 | 75 | 169.2 | 0.906 | 37.85 | 153.3 |  | 30
LV15 | 15 | 3750 | 90 | 62 | 75 | 171.6 | 0.974 | 41.28 | 167.2 |  | 30
LV15 | 15 | 3750 | 70 | 67 | 75 | 183.2 | 0.438 | 19.83 | 80.3 |  | 30
LV15 | 15 | 3750 | 75 | 67 | 75 | 183.6 | 0.536 | 24.3 | 98.4 |  | 30
LV15 | 15 | 3750 | 80 | 67 | 75 | 183.9 | 0.633 | 28.77 | 116.5 |  | 30
LV15 | 15 | 3750 | 85 | 67 | 75 | 184.3 | 0.73 | 33.23 | 134.6 |  | 30
LV15 | 15 | 3750 | 90 | 67 | 75 | 184.5 | 0.828 | 37.7 | 152.7 |  | 30
LV15 | 15 | 3750 | 75 | 72 | 75 | 199 | 0.399 | 19.63 | 79.5 |  | 30
LV15 | 15 | 3750 | 80 | 72 | 75 | 199.3 | 0.487 | 23.98 | 97.1 |  | 30
LV15 | 15 | 3750 | 85 | 72 | 75 | 199.6 | 0.585 | 28.81 | 116.7 |  | 30
LV15 | 15 | 3750 | 90 | 72 | 75 | 199.8 | 0.672 | 33.16 | 134.3 |  | 30
LV15 | 15 | 3750 | 80 | 77 | 75 | 215.6 | 0.36 | 19.19 | 77.7 |  | 30
LV15 | 15 | 3750 | 85 | 77 | 75 | 215.7 | 0.448 | 23.85 | 96.6 |  | 30
LV15 | 15 | 3750 | 90 | 77 | 75 | 216 | 0.536 | 28.57 | 115.7 |  | 30
LV15 | 15 | 3750 | 65 | 57 | 85 | 146.1 | 0.643 | 23.19 | 93.9 |  | 30
LV15 | 15 | 3750 | 70 | 57 | 85 | 146.6 | 0.76 | 27.51 | 111.4 |  | 30
LV15 | 15 | 3750 | 75 | 57 | 85 | 147.1 | 0.886 | 32.2 | 130.4 |  | 30
LV15 | 15 | 3750 | 80 | 57 | 85 | 149 | 0.974 | 35.83 | 145.1 |  | 30
LV15 | 15 | 3750 | 85 | 57 | 85 | 157.2 | 0.974 | 37.8 | 153.1 |  | 30
LV15 | 15 | 3750 | 90 | 57 | 85 | 165.2 | 0.975 | 39.75 | 161 |  | 30
LV15 | 15 | 3750 | 65 | 62 | 85 | 160.3 | 0.477 | 18.89 | 76.5 |  | 30
LV15 | 15 | 3750 | 70 | 62 | 85 | 160.8 | 0.585 | 23.21 | 94 |  | 30
LV15 | 15 | 3750 | 75 | 62 | 85 | 161.4 | 0.701 | 27.95 | 113.2 |  | 30
LV15 | 15 | 3750 | 80 | 62 | 85 | 161.8 | 0.809 | 32.32 | 130.9 |  | 30
LV15 | 15 | 3750 | 85 | 62 | 85 | 161.9 | 0.915 | 36.59 | 148.2 |  | 30
LV15 | 15 | 3750 | 90 | 62 | 85 | 165.3 | 0.974 | 39.75 | 161 |  | 30
LV15 | 15 | 3750 | 70 | 67 | 85 | 175.2 | 0.438 | 18.96 | 76.8 |  | 30
LV15 | 15 | 3750 | 75 | 67 | 85 | 175.6 | 0.536 | 23.23 | 94.1 |  | 30
LV15 | 15 | 3750 | 80 | 67 | 85 | 176 | 0.643 | 27.95 | 113.2 |  | 30
LV15 | 15 | 3750 | 85 | 67 | 85 | 176.2 | 0.74 | 32.2 | 130.4 |  | 30
LV15 | 15 | 3750 | 90 | 67 | 85 | 176.4 | 0.848 | 36.91 | 149.5 |  | 30
LV15 | 15 | 3750 | 75 | 72 | 85 | 190.8 | 0.399 | 18.81 | 76.2 |  | 30
LV15 | 15 | 3750 | 80 | 72 | 85 | 191.2 | 0.497 | 23.46 | 95 |  | 30
LV15 | 15 | 3750 | 85 | 72 | 85 | 191.3 | 0.584 | 27.6 | 111.8 |  | 30
LV15 | 15 | 3750 | 90 | 72 | 85 | 191.4 | 0.682 | 32.22 | 130.5 |  | 30
LV15 | 15 | 3750 | 80 | 77 | 85 | 206.7 | 0.36 | 18.4 | 74.5 |  | 30
LV15 | 15 | 3750 | 85 | 77 | 85 | 207.1 | 0.448 | 22.91 | 92.8 |  | 30
LV15 | 15 | 3750 | 90 | 77 | 85 | 207.2 | 0.536 | 27.41 | 111 |  | 30
LV15 | 15 | 3750 | 65 | 57 | 95 | 138.4 | 0.652 | 22.3 | 90.3 |  | 31
LV15 | 15 | 3750 | 70 | 57 | 95 | 139 | 0.779 | 26.74 | 108.3 |  | 31
LV15 | 15 | 3750 | 75 | 57 | 95 | 139.6 | 0.896 | 30.89 | 125.1 |  | 31
LV15 | 15 | 3750 | 80 | 57 | 95 | 142.7 | 0.974 | 34.32 | 139 |  | 31
LV15 | 15 | 3750 | 85 | 57 | 95 | 150.6 | 0.974 | 36.22 | 146.7 |  | 31
LV15 | 15 | 3750 | 90 | 57 | 95 | 158.4 | 0.974 | 38.1 | 154.3 |  | 31
LV15 | 15 | 3750 | 65 | 62 | 95 | 152 | 0.477 | 17.9 | 72.5 |  | 31
LV15 | 15 | 3750 | 70 | 62 | 95 | 152.5 | 0.594 | 22.37 | 90.6 |  | 31
LV15 | 15 | 3750 | 75 | 62 | 95 | 153.1 | 0.711 | 26.86 | 108.8 |  | 31
LV15 | 15 | 3750 | 80 | 62 | 95 | 153.5 | 0.828 | 31.38 | 127.1 |  | 31
LV15 | 15 | 3750 | 85 | 62 | 95 | 153.5 | 0.935 | 35.43 | 143.5 |  | 31
LV15 | 15 | 3750 | 90 | 62 | 95 | 158.5 | 0.974 | 38.12 | 154.4 |  | 31
LV15 | 15 | 3750 | 70 | 67 | 95 | 166.5 | 0.438 | 18.02 | 73 |  | 31
LV15 | 15 | 3750 | 75 | 67 | 95 | 167 | 0.546 | 22.49 | 91.1 |  | 31
LV15 | 15 | 3750 | 80 | 67 | 95 | 167.4 | 0.652 | 26.96 | 109.2 |  | 31
LV15 | 15 | 3750 | 85 | 67 | 95 | 167.7 | 0.76 | 31.46 | 127.4 |  | 31
LV15 | 15 | 3750 | 90 | 67 | 95 | 168.1 | 0.857 | 35.58 | 144.1 |  | 31
LV15 | 15 | 3750 | 75 | 72 | 95 | 181.8 | 0.399 | 17.93 | 72.6 |  | 31
LV15 | 15 | 3750 | 80 | 72 | 95 | 181.9 | 0.497 | 22.32 | 90.4 |  | 31
LV15 | 15 | 3750 | 85 | 72 | 95 | 182.4 | 0.594 | 26.77 | 108.4 |  | 31
LV15 | 15 | 3750 | 90 | 72 | 95 | 182.3 | 0.692 | 31.14 | 126.1 |  | 31
LV15 | 15 | 3750 | 80 | 77 | 95 | 197.4 | 0.361 | 17.58 | 71.2 |  | 31
LV15 | 15 | 3750 | 85 | 77 | 95 | 197.8 | 0.458 | 22.37 | 90.6 |  | 31
LV15 | 15 | 3750 | 90 | 77 | 95 | 197.8 | 0.546 | 26.64 | 107.9 |  | 31
LV15 | 15 | 3750 | 65 | 57 | 105 | 130.3 | 0.652 | 20.99 | 85 |  | 31
LV15 | 15 | 3750 | 70 | 57 | 105 | 130.6 | 0.789 | 25.43 | 103 |  | 31
LV15 | 15 | 3750 | 75 | 57 | 105 | 130.9 | 0.926 | 29.93 | 121.2 |  | 31
LV15 | 15 | 3750 | 80 | 57 | 105 | 135.5 | 0.974 | 32.59 | 132 |  | 31
LV15 | 15 | 3750 | 85 | 57 | 105 | 143.4 | 0.974 | 34.47 | 139.6 |  | 31
LV15 | 15 | 3750 | 90 | 57 | 105 | 151.1 | 0.974 | 36.35 | 147.2 |  | 31
LV15 | 15 | 3750 | 65 | 62 | 105 | 143.2 | 0.477 | 16.86 | 68.3 |  | 31
LV15 | 15 | 3750 | 70 | 62 | 105 | 143.7 | 0.604 | 21.43 | 86.8 |  | 31
LV15 | 15 | 3750 | 75 | 62 | 105 | 144.2 | 0.721 | 25.65 | 103.9 |  | 31
LV15 | 15 | 3750 | 80 | 62 | 105 | 144.5 | 0.848 | 30.25 | 122.5 |  | 31
LV15 | 15 | 3750 | 85 | 62 | 105 | 143.5 | 0.974 | 34.49 | 139.7 |  | 31
LV15 | 15 | 3750 | 90 | 62 | 105 | 151.2 | 0.974 | 36.37 | 147.3 |  | 31
LV15 | 15 | 3750 | 70 | 67 | 105 | 157.2 | 0.438 | 17.01 | 68.9 |  | 31
LV15 | 15 | 3750 | 75 | 67 | 105 | 157.7 | 0.545 | 21.23 | 86 |  | 31
LV15 | 15 | 3750 | 80 | 67 | 105 | 158.1 | 0.662 | 25.85 | 104.7 |  | 31
LV15 | 15 | 3750 | 85 | 67 | 105 | 158.3 | 0.769 | 30.07 | 121.8 |  | 31
LV15 | 15 | 3750 | 90 | 67 | 105 | 158.6 | 0.887 | 34.72 | 140.6 |  | 31
LV15 | 15 | 3750 | 75 | 72 | 105 | 172.2 | 0.4 | 16.99 | 68.8 |  | 31
LV15 | 15 | 3750 | 80 | 72 | 105 | 172.3 | 0.497 | 21.14 | 85.6 |  | 31
LV15 | 15 | 3750 | 85 | 72 | 105 | 172.4 | 0.604 | 25.7 | 104.1 |  | 31
LV15 | 15 | 3750 | 90 | 72 | 105 | 172.4 | 0.711 | 30.27 | 122.6 |  | 31
LV15 | 15 | 3750 | 80 | 77 | 105 | 187.3 | 0.36 | 16.67 | 67.5 |  | 31
LV15 | 15 | 3750 | 85 | 77 | 105 | 187.5 | 0.458 | 21.21 | 85.9 |  | 31
LV15 | 15 | 3750 | 90 | 77 | 105 | 187.5 | 0.555 | 25.7 | 104.1 |  | 31
LV15 | 15 | 3750 | 65 | 57 | 115 | 121.3 | 0.662 | 19.83 | 80.3 |  | 32
LV15 | 15 | 3750 | 70 | 57 | 115 | 121.8 | 0.809 | 24.32 | 98.5 |  | 32
LV15 | 15 | 3750 | 75 | 57 | 115 | 121.6 | 0.945 | 28.37 | 114.9 |  | 32
LV15 | 15 | 3750 | 80 | 57 | 115 | 127.9 | 0.974 | 30.77 | 124.6 |  | 32
LV15 | 15 | 3750 | 85 | 57 | 115 | 135.8 | 0.974 | 32.67 | 132.3 |  | 32
LV15 | 15 | 3750 | 90 | 57 | 115 | 143.4 | 0.974 | 34.49 | 139.7 |  | 32
LV15 | 15 | 3750 | 65 | 62 | 115 | 133.7 | 0.477 | 15.75 | 63.8 |  | 32
LV15 | 15 | 3750 | 70 | 62 | 115 | 134.4 | 0.603 | 20.02 | 81.1 |  | 32
LV15 | 15 | 3750 | 75 | 62 | 115 | 134.7 | 0.741 | 24.64 | 99.8 |  | 32
LV15 | 15 | 3750 | 80 | 62 | 115 | 135 | 0.867 | 28.91 | 117.1 |  | 32
LV15 | 15 | 3750 | 85 | 62 | 115 | 135.7 | 0.974 | 32.64 | 132.2 |  | 32
LV15 | 15 | 3750 | 90 | 62 | 115 | 143.5 | 0.974 | 34.49 | 139.7 |  | 32
LV15 | 15 | 3750 | 70 | 67 | 115 | 147.3 | 0.439 | 15.95 | 64.6 |  | 32
LV15 | 15 | 3750 | 75 | 67 | 115 | 147.8 | 0.555 | 20.27 | 82.1 |  | 32
LV15 | 15 | 3750 | 80 | 67 | 115 | 148.1 | 0.673 | 24.59 | 99.6 |  | 32
LV15 | 15 | 3750 | 85 | 67 | 115 | 148.3 | 0.789 | 28.89 | 117 |  | 32
LV15 | 15 | 3750 | 90 | 67 | 115 | 148 | 0.916 | 33.46 | 135.5 |  | 32
LV15 | 15 | 3750 | 75 | 72 | 115 | 161.6 | 0.399 | 15.93 | 64.5 |  | 32
LV15 | 15 | 3750 | 80 | 72 | 115 | 161.8 | 0.507 | 20.25 | 82 |  | 32
LV15 | 15 | 3750 | 85 | 72 | 115 | 161.7 | 0.614 | 24.52 | 99.3 |  | 32
LV15 | 15 | 3750 | 90 | 72 | 115 | 162 | 0.721 | 28.84 | 116.8 |  | 32
LV15 | 15 | 3750 | 80 | 77 | 115 | 176.5 | 0.36 | 15.7 | 63.6 |  | 32
LV15 | 15 | 3750 | 85 | 77 | 115 | 176.9 | 0.467 | 20.42 | 82.7 |  | 32
LV15 | 15 | 3750 | 90 | 77 | 115 | 176.4 | 0.565 | 24.62 | 99.7 |  | 32
LV15 | 15 | 3750 | 65 | 57 | 125 | 111.7 | 0.672 | 18.54 | 75.1 |  | 32
LV15 | 15 | 3750 | 70 | 57 | 125 | 112.2 | 0.828 | 22.94 | 92.9 |  | 32
LV15 | 15 | 3750 | 75 | 57 | 125 | 112.2 | 0.974 | 26.99 | 109.3 |  | 32
LV15 | 15 | 3750 | 80 | 57 | 125 | 119.8 | 0.974 | 28.81 | 116.7 |  | 32
LV15 | 15 | 3750 | 85 | 57 | 125 | 127.4 | 0.974 | 30.64 | 124.1 |  | 32
LV15 | 15 | 3750 | 90 | 57 | 125 | 134.9 | 0.974 | 32.44 | 131.4 |  | 32
LV15 | 15 | 3750 | 65 | 62 | 125 | 123.6 | 0.477 | 14.57 | 59 |  | 32
LV15 | 15 | 3750 | 70 | 62 | 125 | 124.3 | 0.614 | 18.84 | 76.3 |  | 32
LV15 | 15 | 3750 | 75 | 62 | 125 | 124.7 | 0.759 | 23.38 | 94.7 |  | 32
LV15 | 15 | 3750 | 80 | 62 | 125 | 124.7 | 0.897 | 27.6 | 111.8 |  | 32
LV15 | 15 | 3750 | 85 | 62 | 125 | 127.5 | 0.974 | 30.67 | 124.2 |  | 32
LV15 | 15 | 3750 | 90 | 62 | 125 | 134.9 | 0.974 | 32.44 | 131.4 |  | 32
LV15 | 15 | 3750 | 70 | 67 | 125 | 137.1 | 0.438 | 14.84 | 60.1 |  | 32
LV15 | 15 | 3750 | 75 | 67 | 125 | 137.3 | 0.565 | 19.16 | 77.6 |  | 32
LV15 | 15 | 3750 | 80 | 67 | 125 | 137.4 | 0.691 | 23.46 | 95 |  | 32
LV15 | 15 | 3750 | 85 | 67 | 125 | 137.4 | 0.818 | 27.75 | 112.4 |  | 32
LV15 | 15 | 3750 | 90 | 67 | 125 | 136.9 | 0.944 | 31.93 | 129.3 |  | 32
LV15 | 15 | 3750 | 75 | 72 | 125 | 150.4 | 0.4 | 14.84 | 60.1 |  | 32
LV15 | 15 | 3750 | 80 | 72 | 125 | 150.3 | 0.516 | 19.16 | 77.6 |  | 32
LV15 | 15 | 3750 | 85 | 72 | 125 | 150.6 | 0.633 | 23.53 | 95.3 |  | 32
LV15 | 15 | 3750 | 90 | 72 | 125 | 150.5 | 0.75 | 27.88 | 112.9 |  | 32
LV15 | 15 | 3750 | 80 | 77 | 125 | 164.5 | 0.37 | 15.04 | 60.9 |  | 32
LV15 | 15 | 3750 | 85 | 77 | 125 | 164.6 | 0.467 | 18.99 | 76.9 |  | 32
LV15 | 15 | 3750 | 90 | 77 | 125 | 164.3 | 0.575 | 23.31 | 94.4 |  | 32
LV15 | 15 | 4500 | 65 | 57 | 75 | 160.4 | 0.653 | 21.54 | 104.7 |  | 30
LV15 | 15 | 4500 | 70 | 57 | 75 | 161.1 | 0.789 | 26.15 | 127.1 |  | 30
LV15 | 15 | 4500 | 75 | 57 | 75 | 161.7 | 0.915 | 30.45 | 148 |  | 30
LV15 | 15 | 4500 | 80 | 57 | 75 | 166.3 | 0.974 | 33.33 | 162 |  | 30
LV15 | 15 | 4500 | 85 | 57 | 75 | 175.4 | 0.974 | 35.16 | 170.9 |  | 30
LV15 | 15 | 4500 | 90 | 57 | 75 | 184 | 0.974 | 36.89 | 179.3 |  | 30
LV15 | 15 | 4500 | 65 | 62 | 75 | 174.8 | 0.477 | 17.16 | 83.4 |  | 30
LV15 | 15 | 4500 | 70 | 62 | 75 | 175.6 | 0.604 | 21.83 | 106.1 |  | 30
LV15 | 15 | 4500 | 75 | 62 | 75 | 176.3 | 0.721 | 26.15 | 127.1 |  | 30
LV15 | 15 | 4500 | 80 | 62 | 75 | 176.7 | 0.838 | 30.47 | 148.1 |  | 30
LV15 | 15 | 4500 | 85 | 62 | 75 | 177 | 0.964 | 35.12 | 170.7 |  | 30
LV15 | 15 | 4500 | 90 | 62 | 75 | 184.2 | 0.974 | 36.91 | 179.4 |  | 30
LV15 | 15 | 4500 | 70 | 67 | 75 | 190.8 | 0.439 | 17.22 | 83.7 |  | 30
LV15 | 15 | 4500 | 75 | 67 | 75 | 191.4 | 0.545 | 21.48 | 104.4 |  | 30
LV15 | 15 | 4500 | 80 | 67 | 75 | 191.7 | 0.662 | 26.13 | 127 |  | 30
LV15 | 15 | 4500 | 85 | 67 | 75 | 191.9 | 0.77 | 30.39 | 147.7 |  | 30
LV15 | 15 | 4500 | 90 | 67 | 75 | 192 | 0.886 | 35.02 | 170.2 |  | 30
LV15 | 15 | 4500 | 75 | 72 | 75 | 207.1 | 0.399 | 17.02 | 82.7 |  | 30
LV15 | 15 | 4500 | 80 | 72 | 75 | 207.5 | 0.507 | 21.63 | 105.1 |  | 30
LV15 | 15 | 4500 | 85 | 72 | 75 | 207.9 | 0.604 | 25.82 | 125.5 |  | 30
LV15 | 15 | 4500 | 90 | 72 | 75 | 208.1 | 0.711 | 30.43 | 147.9 |  | 30
LV15 | 15 | 4500 | 80 | 77 | 75 | 224 | 0.36 | 16.6 | 80.7 |  | 30
LV15 | 15 | 4500 | 85 | 77 | 75 | 224 | 0.458 | 21.09 | 102.5 |  | 30
LV15 | 15 | 4500 | 90 | 77 | 75 | 224.1 | 0.555 | 25.6 | 124.4 |  | 30
LV15 | 15 | 4500 | 65 | 57 | 85 | 152.6 | 0.663 | 20.8 | 101.1 |  | 30
LV15 | 15 | 4500 | 70 | 57 | 85 | 153.3 | 0.799 | 25.21 | 122.5 |  | 30
LV15 | 15 | 4500 | 75 | 57 | 85 | 153.5 | 0.936 | 29.55 | 143.6 |  | 30
LV15 | 15 | 4500 | 80 | 57 | 85 | 159.8 | 0.974 | 32.02 | 155.6 |  | 30
LV15 | 15 | 4500 | 85 | 57 | 85 | 168.4 | 0.974 | 33.74 | 164 |  | 30
LV15 | 15 | 4500 | 90 | 57 | 85 | 177.1 | 0.974 | 35.49 | 172.5 |  | 30
LV15 | 15 | 4500 | 65 | 62 | 85 | 166.7 | 0.478 | 16.38 | 79.6 |  | 30
LV15 | 15 | 4500 | 70 | 62 | 85 | 167.4 | 0.604 | 20.8 | 101.1 |  | 30
LV15 | 15 | 4500 | 75 | 62 | 85 | 168 | 0.73 | 25.25 | 122.7 |  | 30
LV15 | 15 | 4500 | 80 | 62 | 85 | 168.4 | 0.857 | 29.71 | 144.4 |  | 30
LV15 | 15 | 4500 | 85 | 62 | 85 | 168.5 | 0.974 | 33.77 | 164.1 |  | 30
LV15 | 15 | 4500 | 90 | 62 | 85 | 177.2 | 0.974 | 35.51 | 172.6 |  | 30
LV15 | 15 | 4500 | 70 | 67 | 85 | 182.1 | 0.438 | 16.42 | 79.8 |  | 30
LV15 | 15 | 4500 | 75 | 67 | 85 | 182.7 | 0.555 | 20.86 | 101.4 |  | 30
LV15 | 15 | 4500 | 80 | 67 | 85 | 183 | 0.672 | 25.31 | 123 |  | 30
LV15 | 15 | 4500 | 85 | 67 | 85 | 183.2 | 0.789 | 29.73 | 144.5 |  | 30
LV15 | 15 | 4500 | 90 | 67 | 85 | 183.3 | 0.906 | 34.18 | 166.1 |  | 30
LV15 | 15 | 4500 | 75 | 72 | 85 | 198.3 | 0.399 | 16.3 | 79.2 |  | 30
LV15 | 15 | 4500 | 80 | 72 | 85 | 198.5 | 0.507 | 20.7 | 100.6 |  | 30
LV15 | 15 | 4500 | 85 | 72 | 85 | 198.9 | 0.613 | 25.1 | 122 |  | 30
LV15 | 15 | 4500 | 90 | 72 | 85 | 199.1 | 0.721 | 29.53 | 143.5 |  | 30
LV15 | 15 | 4500 | 80 | 77 | 85 | 214.5 | 0.37 | 16.34 | 79.4 |  | 30
LV15 | 15 | 4500 | 85 | 77 | 85 | 214.6 | 0.467 | 20.64 | 100.3 |  | 30
LV15 | 15 | 4500 | 90 | 77 | 85 | 214.7 | 0.565 | 24.96 | 121.3 |  | 30
LV15 | 15 | 4500 | 65 | 57 | 95 | 144.3 | 0.672 | 19.96 | 97 |  | 31
LV15 | 15 | 4500 | 70 | 57 | 95 | 145 | 0.808 | 24.12 | 117.2 |  | 31
LV15 | 15 | 4500 | 75 | 57 | 95 | 144.9 | 0.954 | 28.46 | 138.3 |  | 31
LV15 | 15 | 4500 | 80 | 57 | 95 | 152.5 | 0.974 | 30.56 | 148.5 |  | 31
LV15 | 15 | 4500 | 85 | 57 | 95 | 161 | 0.974 | 32.26 | 156.8 |  | 31
LV15 | 15 | 4500 | 90 | 57 | 95 | 169.6 | 0.974 | 33.99 | 165.2 |  | 31
LV15 | 15 | 4500 | 65 | 62 | 95 | 157.7 | 0.477 | 15.49 | 75.3 |  | 31
LV15 | 15 | 4500 | 70 | 62 | 95 | 158.4 | 0.614 | 20 | 97.2 |  | 31
LV15 | 15 | 4500 | 75 | 62 | 95 | 159 | 0.74 | 24.22 | 117.7 |  | 31
LV15 | 15 | 4500 | 80 | 62 | 95 | 159.4 | 0.877 | 28.77 | 139.8 |  | 31
LV15 | 15 | 4500 | 85 | 62 | 95 | 161.1 | 0.974 | 32.28 | 156.9 |  | 31
LV15 | 15 | 4500 | 90 | 62 | 95 | 169.7 | 0.974 | 34.01 | 165.3 |  | 31
LV15 | 15 | 4500 | 70 | 67 | 95 | 172.8 | 0.438 | 15.58 | 75.7 |  | 31
LV15 | 15 | 4500 | 75 | 67 | 95 | 173.3 | 0.565 | 20.14 | 97.9 |  | 31
LV15 | 15 | 4500 | 80 | 67 | 95 | 173.6 | 0.682 | 24.36 | 118.4 |  | 31
LV15 | 15 | 4500 | 85 | 67 | 95 | 173.8 | 0.808 | 28.91 | 140.5 |  | 31
LV15 | 15 | 4500 | 90 | 67 | 95 | 174 | 0.925 | 33.13 | 161 |  | 31
LV15 | 15 | 4500 | 75 | 72 | 95 | 188.5 | 0.399 | 15.49 | 75.3 |  | 31
LV15 | 15 | 4500 | 80 | 72 | 95 | 188.9 | 0.516 | 20.06 | 97.5 |  | 31
LV15 | 15 | 4500 | 85 | 72 | 95 | 189.1 | 0.623 | 24.26 | 117.9 |  | 31
LV15 | 15 | 4500 | 90 | 72 | 95 | 189.3 | 0.74 | 28.83 | 140.1 |  | 31
LV15 | 15 | 4500 | 80 | 77 | 95 | 204.3 | 0.37 | 15.56 | 75.6 |  | 31
LV15 | 15 | 4500 | 85 | 77 | 95 | 204.5 | 0.467 | 19.67 | 95.6 |  | 31
LV15 | 15 | 4500 | 90 | 77 | 95 | 204.5 | 0.575 | 24.18 | 117.5 |  | 31
LV15 | 15 | 4500 | 65 | 57 | 105 | 135.1 | 0.682 | 18.95 | 92.1 |  | 31
LV15 | 15 | 4500 | 70 | 57 | 105 | 135.7 | 0.828 | 23.13 | 112.4 |  | 31
LV15 | 15 | 4500 | 75 | 57 | 105 | 136 | 0.974 | 27.26 | 132.5 |  | 31
LV15 | 15 | 4500 | 80 | 57 | 105 | 144.5 | 0.974 | 28.97 | 140.8 |  | 31
LV15 | 15 | 4500 | 85 | 57 | 105 | 153.1 | 0.974 | 30.68 | 149.1 |  | 31
LV15 | 15 | 4500 | 90 | 57 | 105 | 161.6 | 0.974 | 32.39 | 157.4 |  | 31
LV15 | 15 | 4500 | 65 | 62 | 105 | 148.1 | 0.477 | 14.55 | 70.7 |  | 31
LV15 | 15 | 4500 | 70 | 62 | 105 | 148.7 | 0.623 | 19.07 | 92.7 |  | 31
LV15 | 15 | 4500 | 75 | 62 | 105 | 149.3 | 0.76 | 23.35 | 113.5 |  | 31
LV15 | 15 | 4500 | 80 | 62 | 105 | 149.4 | 0.896 | 27.55 | 133.9 |  | 31
LV15 | 15 | 4500 | 85 | 62 | 105 | 153.1 | 0.975 | 30.7 | 149.2 |  | 31
LV15 | 15 | 4500 | 90 | 62 | 105 | 161.7 | 0.974 | 32.41 | 157.5 |  | 31
LV15 | 15 | 4500 | 70 | 67 | 105 | 162.8 | 0.439 | 14.69 | 71.4 |  | 31
LV15 | 15 | 4500 | 75 | 67 | 105 | 163.2 | 0.565 | 18.97 | 92.2 |  | 31
LV15 | 15 | 4500 | 80 | 67 | 105 | 163.5 | 0.692 | 23.27 | 113.1 |  | 31
LV15 | 15 | 4500 | 85 | 67 | 105 | 163.8 | 0.828 | 27.9 | 135.6 |  | 31
LV15 | 15 | 4500 | 90 | 67 | 105 | 163.6 | 0.955 | 32.14 | 156.2 |  | 31
LV15 | 15 | 4500 | 75 | 72 | 105 | 178 | 0.399 | 14.63 | 71.1 |  | 31
LV15 | 15 | 4500 | 80 | 72 | 105 | 178.3 | 0.517 | 18.95 | 92.1 |  | 31
LV15 | 15 | 4500 | 85 | 72 | 105 | 178.6 | 0.633 | 23.27 | 113.1 |  | 31
LV15 | 15 | 4500 | 90 | 72 | 105 | 178.8 | 0.76 | 27.94 | 135.8 |  | 31
LV15 | 15 | 4500 | 80 | 77 | 105 | 193.4 | 0.37 | 14.73 | 71.6 |  | 31
LV15 | 15 | 4500 | 85 | 77 | 105 | 193.4 | 0.477 | 18.99 | 92.3 |  | 31
LV15 | 15 | 4500 | 90 | 77 | 105 | 193.4 | 0.584 | 23.25 | 113 |  | 31
LV15 | 15 | 4500 | 65 | 57 | 115 | 125.4 | 0.691 | 17.84 | 86.7 |  | 32
LV15 | 15 | 4500 | 70 | 57 | 115 | 125.9 | 0.847 | 21.95 | 106.7 |  | 32
LV15 | 15 | 4500 | 75 | 57 | 115 | 127.7 | 0.974 | 25.6 | 124.4 |  | 32
LV15 | 15 | 4500 | 80 | 57 | 115 | 136.2 | 0.974 | 27.28 | 132.6 |  | 32
LV15 | 15 | 4500 | 85 | 57 | 115 | 144.6 | 0.974 | 28.97 | 140.8 |  | 32
LV15 | 15 | 4500 | 90 | 57 | 115 | 152.9 | 0.974 | 30.64 | 148.9 |  | 32
LV15 | 15 | 4500 | 65 | 62 | 115 | 137.9 | 0.487 | 13.83 | 67.2 |  | 32
LV15 | 15 | 4500 | 70 | 62 | 115 | 138.7 | 0.633 | 18.07 | 87.8 |  | 32
LV15 | 15 | 4500 | 75 | 62 | 115 | 139.1 | 0.779 | 22.3 | 108.4 |  | 32
LV15 | 15 | 4500 | 80 | 62 | 115 | 139.1 | 0.925 | 26.48 | 128.7 |  | 32
LV15 | 15 | 4500 | 85 | 62 | 115 | 144.6 | 0.974 | 28.97 | 140.8 |  | 32
LV15 | 15 | 4500 | 90 | 62 | 115 | 152.9 | 0.974 | 30.66 | 149 |  | 32
LV15 | 15 | 4500 | 70 | 67 | 115 | 152 | 0.438 | 13.7 | 66.6 |  | 32
LV15 | 15 | 4500 | 75 | 67 | 115 | 152.3 | 0.575 | 18 | 87.5 |  | 32
LV15 | 15 | 4500 | 80 | 67 | 115 | 152.7 | 0.711 | 22.35 | 108.6 |  | 32
LV15 | 15 | 4500 | 85 | 67 | 115 | 153.2 | 0.847 | 26.71 | 129.8 |  | 32
LV15 | 15 | 4500 | 90 | 67 | 115 | 153 | 0.974 | 30.66 | 149 |  | 32
LV15 | 15 | 4500 | 75 | 72 | 115 | 166.9 | 0.399 | 13.7 | 66.6 |  | 32
LV15 | 15 | 4500 | 80 | 72 | 115 | 167.3 | 0.526 | 18.11 | 88 |  | 32
LV15 | 15 | 4500 | 85 | 72 | 115 | 167.3 | 0.653 | 22.47 | 109.2 |  | 32
LV15 | 15 | 4500 | 90 | 72 | 115 | 167.5 | 0.779 | 26.85 | 130.5 |  | 32
LV15 | 15 | 4500 | 80 | 77 | 115 | 181.6 | 0.37 | 13.83 | 67.2 |  | 32
LV15 | 15 | 4500 | 85 | 77 | 115 | 181.5 | 0.487 | 18.19 | 88.4 |  | 32
LV15 | 15 | 4500 | 90 | 77 | 115 | 181.3 | 0.604 | 22.53 | 109.5 |  | 32
LV15 | 15 | 4500 | 65 | 57 | 125 | 115.1 | 0.701 | 16.6 | 80.7 |  | 32
LV15 | 15 | 4500 | 70 | 57 | 125 | 115.5 | 0.877 | 20.84 | 101.3 |  | 32
LV15 | 15 | 4500 | 75 | 57 | 125 | 118.9 | 0.974 | 23.83 | 115.8 |  | 32
LV15 | 15 | 4500 | 80 | 57 | 125 | 127.1 | 0.974 | 25.47 | 123.8 |  | 32
LV15 | 15 | 4500 | 85 | 57 | 125 | 135.2 | 0.974 | 27.1 | 131.7 |  | 32
LV15 | 15 | 4500 | 90 | 57 | 125 | 143.5 | 0.974 | 28.77 | 139.8 |  | 32
LV15 | 15 | 4500 | 65 | 62 | 125 | 127.1 | 0.487 | 12.74 | 61.9 |  | 32
LV15 | 15 | 4500 | 70 | 62 | 125 | 127.8 | 0.643 | 16.91 | 82.2 |  | 32
LV15 | 15 | 4500 | 75 | 62 | 125 | 128.3 | 0.799 | 21.09 | 102.5 |  | 32
LV15 | 15 | 4500 | 80 | 62 | 125 | 127.2 | 0.974 | 25.49 | 123.9 |  | 32
LV15 | 15 | 4500 | 85 | 62 | 125 | 135.4 | 0.974 | 27.14 | 131.9 |  | 32
LV15 | 15 | 4500 | 90 | 62 | 125 | 143.5 | 0.974 | 28.77 | 139.8 |  | 32
LV15 | 15 | 4500 | 70 | 67 | 125 | 140.6 | 0.448 | 12.96 | 63 |  | 32
LV15 | 15 | 4500 | 75 | 67 | 125 | 141 | 0.584 | 16.95 | 82.4 |  | 32
LV15 | 15 | 4500 | 80 | 67 | 125 | 141.3 | 0.73 | 21.23 | 103.2 |  | 32
LV15 | 15 | 4500 | 85 | 67 | 125 | 141.3 | 0.877 | 25.49 | 123.9 |  | 32
LV15 | 15 | 4500 | 90 | 67 | 125 | 143.5 | 0.974 | 28.77 | 139.8 |  | 32
LV15 | 15 | 4500 | 75 | 72 | 125 | 154.9 | 0.409 | 13.05 | 63.4 |  | 32
LV15 | 15 | 4500 | 80 | 72 | 125 | 155 | 0.536 | 17.1 | 83.1 |  | 32
LV15 | 15 | 4500 | 85 | 72 | 125 | 155.2 | 0.672 | 21.46 | 104.3 |  | 32
LV15 | 15 | 4500 | 90 | 72 | 125 | 155.1 | 0.809 | 25.8 | 125.4 |  | 32
LV15 | 15 | 4500 | 80 | 77 | 125 | 168.7 | 0.37 | 12.84 | 62.4 |  | 32
LV15 | 15 | 4500 | 85 | 77 | 125 | 169.1 | 0.497 | 17.28 | 84 |  | 32
LV15 | 15 | 4500 | 90 | 77 | 125 | 168.6 | 0.614 | 21.3 | 103.5 |  | 32
LV15 | 15 | 5250 | 65 | 57 | 75 | 165.5 | 0.672 | 19.61 | 111.2 |  | 30
LV15 | 15 | 5250 | 70 | 57 | 75 | 166.3 | 0.818 | 24 | 136.1 |  | 30
LV15 | 15 | 5250 | 75 | 57 | 75 | 166 | 0.974 | 28.52 | 161.7 |  | 30
LV15 | 15 | 5250 | 80 | 57 | 75 | 175.9 | 0.974 | 30.21 | 171.3 |  | 30
LV15 | 15 | 5250 | 85 | 57 | 75 | 185.1 | 0.974 | 31.8 | 180.3 |  | 30
LV15 | 15 | 5250 | 90 | 57 | 75 | 194.7 | 0.974 | 33.44 | 189.6 |  | 30
LV15 | 15 | 5250 | 65 | 62 | 75 | 180.5 | 0.477 | 15.19 | 86.1 |  | 30
LV15 | 15 | 5250 | 70 | 62 | 75 | 181.5 | 0.614 | 19.65 | 111.4 |  | 30
LV15 | 15 | 5250 | 75 | 62 | 75 | 181.9 | 0.75 | 24.06 | 136.4 |  | 30
LV15 | 15 | 5250 | 80 | 62 | 75 | 182.3 | 0.886 | 28.5 | 161.6 |  | 30
LV15 | 15 | 5250 | 85 | 62 | 75 | 185.1 | 0.974 | 31.8 | 180.3 |  | 30
LV15 | 15 | 5250 | 90 | 62 | 75 | 194.8 | 0.974 | 33.46 | 189.7 |  | 30
LV15 | 15 | 5250 | 70 | 67 | 75 | 196.5 | 0.438 | 15.19 | 86.1 |  | 30
LV15 | 15 | 5250 | 75 | 67 | 75 | 197.3 | 0.565 | 19.66 | 111.5 |  | 30
LV15 | 15 | 5250 | 80 | 67 | 75 | 197.7 | 0.691 | 24.11 | 136.7 |  | 30
LV15 | 15 | 5250 | 85 | 67 | 75 | 198 | 0.818 | 28.57 | 162 |  | 30
LV15 | 15 | 5250 | 90 | 67 | 75 | 198 | 0.935 | 32.65 | 185.1 |  | 30
LV15 | 15 | 5250 | 75 | 72 | 75 | 213.1 | 0.399 | 15.01 | 85.1 |  | 30
LV15 | 15 | 5250 | 80 | 72 | 75 | 213.5 | 0.516 | 19.44 | 110.2 |  | 30
LV15 | 15 | 5250 | 85 | 72 | 75 | 213.7 | 0.633 | 23.86 | 135.3 |  | 30
LV15 | 15 | 5250 | 90 | 72 | 75 | 213.9 | 0.75 | 28.29 | 160.4 |  | 30
LV15 | 15 | 5250 | 80 | 77 | 75 | 230.4 | 0.37 | 15.04 | 85.3 |  | 30
LV15 | 15 | 5250 | 85 | 77 | 75 | 230.3 | 0.477 | 19.38 | 109.9 |  | 30
LV15 | 15 | 5250 | 90 | 77 | 75 | 230.8 | 0.584 | 23.79 | 134.9 |  | 30
LV15 | 15 | 5250 | 65 | 57 | 85 | 157.1 | 0.682 | 18.89 | 107.1 |  | 30
LV15 | 15 | 5250 | 70 | 57 | 85 | 157.8 | 0.838 | 23.32 | 132.2 |  | 30
LV15 | 15 | 5250 | 75 | 57 | 85 | 158.9 | 0.974 | 27.3 | 154.8 |  | 30
LV15 | 15 | 5250 | 80 | 57 | 85 | 168.3 | 0.974 | 28.92 | 164 |  | 30
LV15 | 15 | 5250 | 85 | 57 | 85 | 177.6 | 0.974 | 30.51 | 173 |  | 30
LV15 | 15 | 5250 | 90 | 57 | 85 | 187 | 0.974 | 32.13 | 182.2 |  | 30
LV15 | 15 | 5250 | 65 | 62 | 85 | 172.5 | 0.487 | 14.81 | 84 |  | 30
LV15 | 15 | 5250 | 70 | 62 | 85 | 172.4 | 0.623 | 18.94 | 107.4 |  | 30
LV15 | 15 | 5250 | 75 | 62 | 85 | 172.8 | 0.77 | 23.46 | 133 |  | 30
LV15 | 15 | 5250 | 80 | 62 | 85 | 173.2 | 0.906 | 27.67 | 156.9 |  | 30
LV15 | 15 | 5250 | 85 | 62 | 85 | 177.6 | 0.974 | 30.51 | 173 |  | 30
LV15 | 15 | 5250 | 90 | 62 | 85 | 187 | 0.974 | 32.13 | 182.2 |  | 30
LV15 | 15 | 5250 | 70 | 67 | 85 | 187.1 | 0.438 | 14.46 | 82 |  | 30
LV15 | 15 | 5250 | 75 | 67 | 85 | 187.9 | 0.575 | 19.05 | 108 |  | 30
LV15 | 15 | 5250 | 80 | 67 | 85 | 188.6 | 0.701 | 23.33 | 132.3 |  | 30
LV15 | 15 | 5250 | 85 | 67 | 85 | 188.9 | 0.828 | 27.58 | 156.4 |  | 30
LV15 | 15 | 5250 | 90 | 67 | 85 | 187.4 | 0.964 | 31.87 | 180.7 |  | 30
LV15 | 15 | 5250 | 75 | 72 | 85 | 203.5 | 0.4 | 14.34 | 81.3 |  | 30
LV15 | 15 | 5250 | 80 | 72 | 85 | 204 | 0.526 | 18.92 | 107.3 |  | 30
LV15 | 15 | 5250 | 85 | 72 | 85 | 204.2 | 0.643 | 23.16 | 131.3 |  | 30
LV15 | 15 | 5250 | 90 | 72 | 85 | 204.2 | 0.77 | 27.72 | 157.2 |  | 30
LV15 | 15 | 5250 | 80 | 77 | 85 | 220.5 | 0.37 | 14.39 | 81.6 |  | 30
LV15 | 15 | 5250 | 85 | 77 | 85 | 220.6 | 0.477 | 18.57 | 105.3 |  | 30
LV15 | 15 | 5250 | 90 | 77 | 85 | 220.7 | 0.594 | 23.12 | 131.1 |  | 30
LV15 | 15 | 5250 | 65 | 57 | 95 | 148.2 | 0.692 | 18.08 | 102.5 |  | 31
LV15 | 15 | 5250 | 70 | 57 | 95 | 148.9 | 0.848 | 22.26 | 126.2 |  | 31
LV15 | 15 | 5250 | 75 | 57 | 95 | 151 | 0.974 | 25.94 | 147.1 |  | 31
LV15 | 15 | 5250 | 80 | 57 | 95 | 160.3 | 0.974 | 27.55 | 156.2 |  | 31
LV15 | 15 | 5250 | 85 | 57 | 95 | 169.6 | 0.974 | 29.14 | 165.2 |  | 31
LV15 | 15 | 5250 | 90 | 57 | 95 | 178.7 | 0.974 | 30.71 | 174.1 |  | 31
LV15 | 15 | 5250 | 65 | 62 | 95 | 161.9 | 0.487 | 13.9 | 78.8 |  | 31
LV15 | 15 | 5250 | 70 | 62 | 95 | 162.8 | 0.633 | 18.18 | 103.1 |  | 31
LV15 | 15 | 5250 | 75 | 62 | 95 | 163.1 | 0.779 | 22.42 | 127.1 |  | 31
LV15 | 15 | 5250 | 80 | 62 | 95 | 163.6 | 0.925 | 26.7 | 151.4 |  | 31
LV15 | 15 | 5250 | 85 | 62 | 95 | 169.6 | 0.974 | 29.14 | 165.2 |  | 31
LV15 | 15 | 5250 | 90 | 62 | 95 | 178.9 | 0.974 | 30.72 | 174.2 |  | 31
LV15 | 15 | 5250 | 70 | 67 | 95 | 177.3 | 0.438 | 13.7 | 77.7 |  | 31
LV15 | 15 | 5250 | 75 | 67 | 95 | 178 | 0.575 | 18.04 | 102.3 |  | 31
LV15 | 15 | 5250 | 80 | 67 | 95 | 178.6 | 0.711 | 22.4 | 127 |  | 31
LV15 | 15 | 5250 | 85 | 67 | 95 | 179.2 | 0.848 | 26.79 | 151.9 |  | 31
LV15 | 15 | 5250 | 90 | 67 | 95 | 178.8 | 0.974 | 30.72 | 174.2 |  | 31
LV15 | 15 | 5250 | 75 | 72 | 95 | 193.2 | 0.409 | 13.93 | 79 |  | 31
LV15 | 15 | 5250 | 80 | 72 | 95 | 193.5 | 0.526 | 17.95 | 101.8 |  | 31
LV15 | 15 | 5250 | 85 | 72 | 95 | 193.8 | 0.653 | 22.31 | 126.5 |  | 31
LV15 | 15 | 5250 | 90 | 72 | 95 | 193.9 | 0.779 | 26.65 | 151.1 |  | 31
LV15 | 15 | 5250 | 80 | 77 | 95 | 209.7 | 0.37 | 13.69 | 77.6 |  | 31
LV15 | 15 | 5250 | 85 | 77 | 95 | 209.8 | 0.487 | 18.02 | 102.2 |  | 31
LV15 | 15 | 5250 | 90 | 77 | 95 | 209.8 | 0.604 | 22.35 | 126.7 |  | 31
LV15 | 15 | 5250 | 65 | 57 | 105 | 138.3 | 0.701 | 17.11 | 97 |  | 31
LV15 | 15 | 5250 | 70 | 57 | 105 | 139 | 0.867 | 21.25 | 120.5 |  | 31
LV15 | 15 | 5250 | 75 | 57 | 105 | 142.6 | 0.974 | 24.5 | 138.9 |  | 31
LV15 | 15 | 5250 | 80 | 57 | 105 | 151.7 | 0.974 | 26.07 | 147.8 |  | 31
LV15 | 15 | 5250 | 85 | 57 | 105 | 160.9 | 0.974 | 27.64 | 156.7 |  | 31
LV15 | 15 | 5250 | 90 | 57 | 105 | 170 | 0.974 | 29.21 | 165.6 |  | 31
LV15 | 15 | 5250 | 65 | 62 | 105 | 151.7 | 0.487 | 13.03 | 73.9 |  | 31
LV15 | 15 | 5250 | 70 | 62 | 105 | 152.5 | 0.643 | 17.3 | 98.1 |  | 31
LV15 | 15 | 5250 | 75 | 62 | 105 | 152.9 | 0.799 | 21.53 | 122.1 |  | 31
LV15 | 15 | 5250 | 80 | 62 | 105 | 153.4 | 0.955 | 25.84 | 146.5 |  | 31
LV15 | 15 | 5250 | 85 | 62 | 105 | 161 | 0.974 | 27.65 | 156.8 |  | 31
LV15 | 15 | 5250 | 90 | 62 | 105 | 170 | 0.974 | 29.21 | 165.6 |  | 31
LV15 | 15 | 5250 | 70 | 67 | 105 | 166.7 | 0.448 | 13.17 | 74.7 |  | 31
LV15 | 15 | 5250 | 75 | 67 | 105 | 167.4 | 0.584 | 17.25 | 97.8 |  | 31
LV15 | 15 | 5250 | 80 | 67 | 105 | 167.9 | 0.73 | 21.62 | 122.6 |  | 31
LV15 | 15 | 5250 | 85 | 67 | 105 | 168 | 0.877 | 25.98 | 147.3 |  | 31
LV15 | 15 | 5250 | 90 | 67 | 105 | 170.1 | 0.974 | 29.22 | 165.7 |  | 31
LV15 | 15 | 5250 | 75 | 72 | 105 | 181.9 | 0.409 | 13.12 | 74.4 |  | 31
LV15 | 15 | 5250 | 80 | 72 | 105 | 182.3 | 0.536 | 17.23 | 97.7 |  | 31
LV15 | 15 | 5250 | 85 | 72 | 105 | 182.6 | 0.673 | 21.66 | 122.8 |  | 31
LV15 | 15 | 5250 | 90 | 72 | 105 | 182.6 | 0.798 | 25.71 | 145.8 |  | 31
LV15 | 15 | 5250 | 80 | 77 | 105 | 197.9 | 0.37 | 12.93 | 73.3 |  | 31
LV15 | 15 | 5250 | 85 | 77 | 105 | 198.1 | 0.497 | 17.35 | 98.4 |  | 31
LV15 | 15 | 5250 | 90 | 77 | 105 | 198.2 | 0.614 | 21.46 | 121.7 |  | 31
LV15 | 15 | 5250 | 65 | 57 | 115 | 128 | 0.711 | 16.05 | 91 |  | 32
LV15 | 15 | 5250 | 70 | 57 | 115 | 128.4 | 0.896 | 20.3 | 115.1 |  | 32
LV15 | 15 | 5250 | 75 | 57 | 115 | 133.6 | 0.974 | 22.95 | 130.1 |  | 32
LV15 | 15 | 5250 | 80 | 57 | 115 | 142.6 | 0.974 | 24.5 | 138.9 |  | 32
LV15 | 15 | 5250 | 85 | 57 | 115 | 151.6 | 0.974 | 26.05 | 147.7 |  | 32
LV15 | 15 | 5250 | 90 | 57 | 115 | 160.4 | 0.974 | 27.57 | 156.3 |  | 32
LV15 | 15 | 5250 | 65 | 62 | 115 | 140.7 | 0.487 | 12.08 | 68.5 |  | 32
LV15 | 15 | 5250 | 70 | 62 | 115 | 141.5 | 0.652 | 16.28 | 92.3 |  | 32
LV15 | 15 | 5250 | 75 | 62 | 115 | 142 | 0.818 | 20.49 | 116.2 |  | 32
LV15 | 15 | 5250 | 80 | 62 | 115 | 142.4 | 0.974 | 24.46 | 138.7 |  | 32
LV15 | 15 | 5250 | 85 | 62 | 115 | 151.6 | 0.974 | 26.05 | 147.7 |  | 32
LV15 | 15 | 5250 | 90 | 62 | 115 | 160.5 | 0.974 | 27.57 | 156.3 |  | 32
LV15 | 15 | 5250 | 70 | 67 | 115 | 155.3 | 0.448 | 12.28 | 69.6 |  | 32
LV15 | 15 | 5250 | 75 | 67 | 115 | 156.1 | 0.594 | 16.35 | 92.7 |  | 32
LV15 | 15 | 5250 | 80 | 67 | 115 | 156.4 | 0.75 | 20.69 | 117.3 |  | 32
LV15 | 15 | 5250 | 85 | 67 | 115 | 156.3 | 0.906 | 24.97 | 141.6 |  | 32
LV15 | 15 | 5250 | 90 | 67 | 115 | 160.6 | 0.974 | 27.58 | 156.4 |  | 32
LV15 | 15 | 5250 | 75 | 72 | 115 | 170.1 | 0.409 | 12.28 | 69.6 |  | 32
LV15 | 15 | 5250 | 80 | 72 | 115 | 170.4 | 0.545 | 16.38 | 92.9 |  | 32
LV15 | 15 | 5250 | 85 | 72 | 115 | 170.6 | 0.692 | 20.81 | 118 |  | 32
LV15 | 15 | 5250 | 90 | 72 | 115 | 170.8 | 0.828 | 24.94 | 141.4 |  | 32
LV15 | 15 | 5250 | 80 | 77 | 115 | 185.5 | 0.37 | 12.12 | 68.7 |  | 32
LV15 | 15 | 5250 | 85 | 77 | 115 | 185.6 | 0.506 | 16.58 | 94 |  | 32
LV15 | 15 | 5250 | 90 | 77 | 115 | 184.9 | 0.633 | 20.65 | 117.1 |  | 32
LV15 | 15 | 5250 | 65 | 57 | 125 | 117 | 0.73 | 15.06 | 85.4 |  | 32
LV15 | 15 | 5250 | 70 | 57 | 125 | 117.3 | 0.925 | 19.14 | 108.5 |  | 32
LV15 | 15 | 5250 | 75 | 57 | 125 | 124.1 | 0.974 | 21.32 | 120.9 |  | 32
LV15 | 15 | 5250 | 80 | 57 | 125 | 132.9 | 0.974 | 22.82 | 129.4 |  | 32
LV15 | 15 | 5250 | 85 | 57 | 125 | 141.6 | 0.974 | 24.32 | 137.9 |  | 32
LV15 | 15 | 5250 | 90 | 57 | 125 | 150.4 | 0.974 | 25.84 | 146.5 |  | 32
LV15 | 15 | 5250 | 65 | 62 | 125 | 129.2 | 0.497 | 11.32 | 64.2 |  | 32
LV15 | 15 | 5250 | 70 | 62 | 125 | 130 | 0.672 | 15.41 | 87.4 |  | 32
LV15 | 15 | 5250 | 75 | 62 | 125 | 130.7 | 0.847 | 19.52 | 110.7 |  | 32
LV15 | 15 | 5250 | 80 | 62 | 125 | 133 | 0.974 | 22.84 | 129.5 |  | 32
LV15 | 15 | 5250 | 85 | 62 | 125 | 141.5 | 0.975 | 24.32 | 137.9 |  | 32
LV15 | 15 | 5250 | 90 | 62 | 125 | 150.2 | 0.974 | 25.8 | 146.3 |  | 32
LV15 | 15 | 5250 | 70 | 67 | 125 | 143.3 | 0.448 | 11.32 | 64.2 |  | 32
LV15 | 15 | 5250 | 75 | 67 | 125 | 144 | 0.613 | 15.57 | 88.3 |  | 32
LV15 | 15 | 5250 | 80 | 67 | 125 | 144.3 | 0.78 | 19.84 | 112.5 |  | 32
LV15 | 15 | 5250 | 85 | 67 | 125 | 143.7 | 0.945 | 23.95 | 135.8 |  | 32
LV15 | 15 | 5250 | 90 | 67 | 125 | 150.3 | 0.974 | 25.82 | 146.4 |  | 32
LV15 | 15 | 5250 | 75 | 72 | 125 | 157.5 | 0.409 | 11.36 | 64.4 |  | 32
LV15 | 15 | 5250 | 80 | 72 | 125 | 157.6 | 0.565 | 15.71 | 89.1 |  | 32
LV15 | 15 | 5250 | 85 | 72 | 125 | 157.7 | 0.711 | 19.77 | 112.1 |  | 32
LV15 | 15 | 5250 | 90 | 72 | 125 | 157.6 | 0.867 | 24.09 | 136.6 |  | 32
LV15 | 15 | 5250 | 80 | 77 | 125 | 172.4 | 0.38 | 11.55 | 65.5 |  | 32
LV15 | 15 | 5250 | 85 | 77 | 125 | 172.1 | 0.517 | 15.68 | 88.9 |  | 32
LV15 | 15 | 5250 | 90 | 77 | 125 | 171.9 | 0.653 | 19.79 | 112.2 |  | 32
LV15 | 15 | 6000 | 65 | 57 | 75 | 169.7 | 0.691 | 18.1 | 117.3 |  | 30
LV15 | 15 | 6000 | 70 | 57 | 75 | 170.3 | 0.857 | 22.53 | 146 |  | 30
LV15 | 15 | 6000 | 75 | 57 | 75 | 173.1 | 0.974 | 26.02 | 168.6 |  | 30
LV15 | 15 | 6000 | 80 | 57 | 75 | 183.3 | 0.974 | 27.56 | 178.6 |  | 30
LV15 | 15 | 6000 | 85 | 57 | 75 | 193.2 | 0.974 | 29.04 | 188.2 |  | 30
LV15 | 15 | 6000 | 90 | 57 | 75 | 203.4 | 0.974 | 30.57 | 198.1 |  | 30
LV15 | 15 | 6000 | 65 | 62 | 75 | 184.5 | 0.487 | 13.86 | 89.8 |  | 30
LV15 | 15 | 6000 | 70 | 62 | 75 | 185.5 | 0.633 | 18.12 | 117.4 |  | 30
LV15 | 15 | 6000 | 75 | 62 | 75 | 186.2 | 0.789 | 22.67 | 146.9 |  | 30
LV15 | 15 | 6000 | 80 | 62 | 75 | 186.9 | 0.925 | 26.68 | 172.9 |  | 30
LV15 | 15 | 6000 | 85 | 62 | 75 | 193.4 | 0.974 | 29.07 | 188.4 |  | 30
LV15 | 15 | 6000 | 90 | 62 | 75 | 203.2 | 0.974 | 30.54 | 197.9 |  | 30
LV15 | 15 | 6000 | 70 | 67 | 75 | 200.8 | 0.448 | 13.89 | 90 |  | 30
LV15 | 15 | 6000 | 75 | 67 | 75 | 201.4 | 0.584 | 18.16 | 117.7 |  | 30
LV15 | 15 | 6000 | 80 | 67 | 75 | 202.3 | 0.721 | 22.5 | 145.8 |  | 30
LV15 | 15 | 6000 | 85 | 67 | 75 | 202.7 | 0.857 | 26.82 | 173.8 |  | 30
LV15 | 15 | 6000 | 90 | 67 | 75 | 203.5 | 0.974 | 30.59 | 198.2 |  | 30
LV15 | 15 | 6000 | 75 | 72 | 75 | 218 | 0.409 | 13.77 | 89.2 |  | 30
LV15 | 15 | 6000 | 80 | 72 | 75 | 218.3 | 0.536 | 18.04 | 116.9 |  | 30
LV15 | 15 | 6000 | 85 | 72 | 75 | 218.6 | 0.662 | 22.35 | 144.8 |  | 30
LV15 | 15 | 6000 | 90 | 72 | 75 | 218.8 | 0.789 | 26.65 | 172.7 |  | 30
LV15 | 15 | 6000 | 80 | 77 | 75 | 235.2 | 0.37 | 13.44 | 87.1 |  | 30
LV15 | 15 | 6000 | 85 | 77 | 75 | 235.3 | 0.487 | 17.69 | 114.6 |  | 30
LV15 | 15 | 6000 | 90 | 77 | 75 | 235.6 | 0.614 | 22.31 | 144.6 |  | 30
LV15 | 15 | 6000 | 65 | 57 | 85 | 160.8 | 0.701 | 17.41 | 112.8 |  | 30
LV15 | 15 | 6000 | 70 | 57 | 85 | 161.5 | 0.867 | 21.6 | 140 |  | 30
LV15 | 15 | 6000 | 75 | 57 | 85 | 165.4 | 0.975 | 24.88 | 161.2 |  | 30
LV15 | 15 | 6000 | 80 | 57 | 85 | 175.4 | 0.974 | 26.36 | 170.8 |  | 30
LV15 | 15 | 6000 | 85 | 57 | 85 | 185.3 | 0.974 | 27.85 | 180.5 |  | 30
LV15 | 15 | 6000 | 90 | 57 | 85 | 195.2 | 0.974 | 29.35 | 190.2 |  | 30
LV15 | 15 | 6000 | 65 | 62 | 85 | 174.9 | 0.487 | 13.15 | 85.2 |  | 30
LV15 | 15 | 6000 | 70 | 62 | 85 | 175.9 | 0.643 | 17.45 | 113.1 |  | 30
LV15 | 15 | 6000 | 75 | 62 | 85 | 176.7 | 0.799 | 21.79 | 141.2 |  | 30
LV15 | 15 | 6000 | 80 | 62 | 85 | 176.9 | 0.955 | 26.06 | 168.9 |  | 30
LV15 | 15 | 6000 | 85 | 62 | 85 | 185.2 | 0.974 | 27.84 | 180.4 |  | 30
LV15 | 15 | 6000 | 90 | 62 | 85 | 195.3 | 0.974 | 29.35 | 190.2 |  | 30
LV15 | 15 | 6000 | 70 | 67 | 85 | 191.1 | 0.448 | 13.21 | 85.6 |  | 30
LV15 | 15 | 6000 | 75 | 67 | 85 | 192 | 0.584 | 17.31 | 112.2 |  | 30
LV15 | 15 | 6000 | 80 | 67 | 85 | 192.5 | 0.731 | 21.71 | 140.7 |  | 30
LV15 | 15 | 6000 | 85 | 67 | 85 | 193 | 0.877 | 26.11 | 169.2 |  | 30
LV15 | 15 | 6000 | 90 | 67 | 85 | 195.3 | 0.974 | 29.35 | 190.2 |  | 30
LV15 | 15 | 6000 | 75 | 72 | 85 | 207.6 | 0.409 | 13.12 | 85 |  | 30
LV15 | 15 | 6000 | 80 | 72 | 85 | 208.4 | 0.536 | 17.22 | 111.6 |  | 30
LV15 | 15 | 6000 | 85 | 72 | 85 | 208.6 | 0.672 | 21.64 | 140.2 |  | 30
LV15 | 15 | 6000 | 90 | 72 | 85 | 208.8 | 0.808 | 26.05 | 168.8 |  | 30
LV15 | 15 | 6000 | 80 | 77 | 85 | 225.1 | 0.37 | 12.85 | 83.3 |  | 30
LV15 | 15 | 6000 | 85 | 77 | 85 | 224.7 | 0.497 | 17.22 | 111.6 |  | 30
LV15 | 15 | 6000 | 90 | 77 | 85 | 225.2 | 0.623 | 21.67 | 140.4 |  | 30
LV15 | 15 | 6000 | 65 | 57 | 95 | 151 | 0.711 | 16.57 | 107.4 |  | 31
LV15 | 15 | 6000 | 70 | 57 | 95 | 151.5 | 0.886 | 20.73 | 134.3 |  | 31
LV15 | 15 | 6000 | 75 | 57 | 95 | 157 | 0.974 | 23.6 | 152.9 |  | 31
LV15 | 15 | 6000 | 80 | 57 | 95 | 166.8 | 0.974 | 25.08 | 162.5 |  | 31
LV15 | 15 | 6000 | 85 | 57 | 95 | 176.6 | 0.974 | 26.54 | 172 |  | 31
LV15 | 15 | 6000 | 90 | 57 | 95 | 186.3 | 0.974 | 28.01 | 181.5 |  | 31
LV15 | 15 | 6000 | 65 | 62 | 95 | 164.8 | 0.487 | 12.39 | 80.3 |  | 31
LV15 | 15 | 6000 | 70 | 62 | 95 | 165.9 | 0.653 | 16.71 | 108.3 |  | 31
LV15 | 15 | 6000 | 75 | 62 | 95 | 166.6 | 0.818 | 21.03 | 136.3 |  | 31
LV15 | 15 | 6000 | 80 | 62 | 95 | 166.8 | 0.974 | 25.08 | 162.5 |  | 31
LV15 | 15 | 6000 | 85 | 62 | 95 | 176.6 | 0.974 | 26.54 | 172 |  | 31
LV15 | 15 | 6000 | 90 | 62 | 95 | 186.4 | 0.974 | 28.02 | 181.6 |  | 31
LV15 | 15 | 6000 | 70 | 67 | 95 | 180.5 | 0.448 | 12.48 | 80.9 |  | 31
LV15 | 15 | 6000 | 75 | 67 | 95 | 181.5 | 0.594 | 16.65 | 107.9 |  | 31
LV15 | 15 | 6000 | 80 | 67 | 95 | 182 | 0.75 | 21.06 | 136.5 |  | 31
LV15 | 15 | 6000 | 85 | 67 | 95 | 182.2 | 0.896 | 25.2 | 163.3 |  | 31
LV15 | 15 | 6000 | 90 | 67 | 95 | 186.4 | 0.974 | 28.02 | 181.6 |  | 31
LV15 | 15 | 6000 | 75 | 72 | 95 | 196.8 | 0.409 | 12.42 | 80.5 |  | 31
LV15 | 15 | 6000 | 80 | 72 | 95 | 197.5 | 0.545 | 16.62 | 107.7 |  | 31
LV15 | 15 | 6000 | 85 | 72 | 95 | 198 | 0.692 | 21.14 | 137 |  | 31
LV15 | 15 | 6000 | 90 | 72 | 95 | 197.9 | 0.828 | 25.29 | 163.9 |  | 31
LV15 | 15 | 6000 | 80 | 77 | 95 | 213.5 | 0.37 | 12.19 | 79 |  | 31
LV15 | 15 | 6000 | 85 | 77 | 95 | 214.2 | 0.507 | 16.74 | 108.5 |  | 31
LV15 | 15 | 6000 | 90 | 77 | 95 | 213.6 | 0.633 | 20.88 | 135.3 |  | 31
LV15 | 15 | 6000 | 65 | 57 | 105 | 140.9 | 0.72 | 15.66 | 101.5 |  | 31
LV15 | 15 | 6000 | 70 | 57 | 105 | 141.2 | 0.916 | 19.95 | 129.3 |  | 31
LV15 | 15 | 6000 | 75 | 57 | 105 | 147.9 | 0.974 | 22.24 | 144.1 |  | 31
LV15 | 15 | 6000 | 80 | 57 | 105 | 157.6 | 0.975 | 23.7 | 153.6 |  | 31
LV15 | 15 | 6000 | 85 | 57 | 105 | 167.2 | 0.974 | 25.14 | 162.9 |  | 31
LV15 | 15 | 6000 | 90 | 57 | 105 | 176.9 | 0.974 | 26.59 | 172.3 |  | 31
LV15 | 15 | 6000 | 65 | 62 | 105 | 154.1 | 0.496 | 11.81 | 76.5 |  | 31
LV15 | 15 | 6000 | 70 | 62 | 105 | 155.2 | 0.662 | 15.86 | 102.8 |  | 31
LV15 | 15 | 6000 | 75 | 62 | 105 | 156 | 0.838 | 20.17 | 130.7 |  | 31
LV15 | 15 | 6000 | 80 | 62 | 105 | 157.7 | 0.974 | 23.7 | 153.6 |  | 31
LV15 | 15 | 6000 | 85 | 62 | 105 | 167.2 | 0.974 | 25.14 | 162.9 |  | 31
LV15 | 15 | 6000 | 90 | 62 | 105 | 176.9 | 0.974 | 26.59 | 172.3 |  | 31
LV15 | 15 | 6000 | 70 | 67 | 105 | 169.4 | 0.448 | 11.71 | 75.9 |  | 31
LV15 | 15 | 6000 | 75 | 67 | 105 | 170.3 | 0.604 | 15.86 | 102.8 |  | 31
LV15 | 15 | 6000 | 80 | 67 | 105 | 170.6 | 0.77 | 20.26 | 131.3 |  | 31
LV15 | 15 | 6000 | 85 | 67 | 105 | 171.3 | 0.915 | 24.2 | 156.8 |  | 31
LV15 | 15 | 6000 | 90 | 67 | 105 | 177 | 0.974 | 26.6 | 172.4 |  | 31
LV15 | 15 | 6000 | 75 | 72 | 105 | 185.3 | 0.409 | 11.7 | 75.8 |  | 31
LV15 | 15 | 6000 | 80 | 72 | 105 | 185.9 | 0.555 | 15.93 | 103.2 |  | 31
LV15 | 15 | 6000 | 85 | 72 | 105 | 185.9 | 0.701 | 20.12 | 130.4 |  | 31
LV15 | 15 | 6000 | 90 | 72 | 105 | 185.7 | 0.857 | 24.57 | 159.2 |  | 31
LV15 | 15 | 6000 | 80 | 77 | 105 | 201.2 | 0.38 | 11.79 | 76.4 |  | 31
LV15 | 15 | 6000 | 85 | 77 | 105 | 201.3 | 0.516 | 16.03 | 103.9 |  | 31
LV15 | 15 | 6000 | 90 | 77 | 105 | 201.5 | 0.653 | 20.29 | 131.5 |  | 31
LV15 | 15 | 6000 | 65 | 57 | 115 | 129.7 | 0.74 | 14.81 | 96 |  | 32
LV15 | 15 | 6000 | 70 | 57 | 115 | 130.7 | 0.945 | 19.06 | 123.5 |  | 32
LV15 | 15 | 6000 | 75 | 57 | 115 | 138.3 | 0.974 | 20.79 | 134.7 |  | 32
LV15 | 15 | 6000 | 80 | 57 | 115 | 148 | 0.974 | 22.24 | 144.1 |  | 32
LV15 | 15 | 6000 | 85 | 57 | 115 | 157.2 | 0.975 | 23.64 | 153.2 |  | 32
LV15 | 15 | 6000 | 90 | 57 | 115 | 166.7 | 0.974 | 25.05 | 162.3 |  | 32
LV15 | 15 | 6000 | 65 | 62 | 115 | 142.7 | 0.497 | 10.94 | 70.9 |  | 32
LV15 | 15 | 6000 | 70 | 62 | 115 | 143.7 | 0.682 | 15.12 | 98 |  | 32
LV15 | 15 | 6000 | 75 | 62 | 115 | 144.3 | 0.857 | 19.09 | 123.7 |  | 32
LV15 | 15 | 6000 | 80 | 62 | 115 | 147.8 | 0.974 | 22.22 | 144 |  | 32
LV15 | 15 | 6000 | 85 | 62 | 115 | 157.2 | 0.975 | 23.64 | 153.2 |  | 32
LV15 | 15 | 6000 | 90 | 62 | 115 | 166.6 | 0.974 | 25.05 | 162.3 |  | 32
LV15 | 15 | 6000 | 70 | 67 | 115 | 157.6 | 0.457 | 11.13 | 72.1 |  | 32
LV15 | 15 | 6000 | 75 | 67 | 115 | 158.3 | 0.623 | 15.23 | 98.7 |  | 32
LV15 | 15 | 6000 | 80 | 67 | 115 | 158.8 | 0.789 | 19.34 | 125.3 |  | 32
LV15 | 15 | 6000 | 85 | 67 | 115 | 157.1 | 0.975 | 23.63 | 153.1 |  | 32
LV15 | 15 | 6000 | 90 | 67 | 115 | 166.7 | 0.974 | 25.05 | 162.3 |  | 32
LV15 | 15 | 6000 | 75 | 72 | 115 | 172.7 | 0.419 | 11.16 | 72.3 |  | 32
LV15 | 15 | 6000 | 80 | 72 | 115 | 173.2 | 0.565 | 15.09 | 97.8 |  | 32
LV15 | 15 | 6000 | 85 | 72 | 115 | 173.3 | 0.731 | 19.54 | 126.6 |  | 32
LV15 | 15 | 6000 | 90 | 72 | 115 | 172.8 | 0.886 | 23.63 | 153.1 |  | 32
LV15 | 15 | 6000 | 80 | 77 | 115 | 188.1 | 0.38 | 11.03 | 71.5 |  | 32
LV15 | 15 | 6000 | 85 | 77 | 115 | 188.3 | 0.526 | 15.29 | 99.1 |  | 32
LV15 | 15 | 6000 | 90 | 77 | 115 | 188.2 | 0.672 | 19.52 | 126.5 |  | 32
LV15 | 15 | 6000 | 65 | 57 | 125 | 117.8 | 0.76 | 13.81 | 89.5 |  | 32
LV15 | 15 | 6000 | 70 | 57 | 125 | 118.8 | 0.974 | 17.85 | 115.7 |  | 32
LV15 | 15 | 6000 | 75 | 57 | 125 | 128.1 | 0.974 | 19.26 | 124.8 |  | 32
LV15 | 15 | 6000 | 80 | 57 | 125 | 137.4 | 0.974 | 20.65 | 133.8 |  | 32
LV15 | 15 | 6000 | 85 | 57 | 125 | 146.5 | 0.974 | 22.02 | 142.7 |  | 32
LV15 | 15 | 6000 | 90 | 57 | 125 | 155.7 | 0.974 | 23.4 | 151.6 |  | 32
LV15 | 15 | 6000 | 65 | 62 | 125 | 130.7 | 0.507 | 10.22 | 66.2 |  | 32
LV15 | 15 | 6000 | 70 | 62 | 125 | 131.8 | 0.691 | 14.06 | 91.1 |  | 32
LV15 | 15 | 6000 | 75 | 62 | 125 | 132 | 0.896 | 18.26 | 118.3 |  | 32
LV15 | 15 | 6000 | 80 | 62 | 125 | 137.6 | 0.974 | 20.68 | 134 |  | 32
LV15 | 15 | 6000 | 85 | 62 | 125 | 146.6 | 0.974 | 22.04 | 142.8 |  | 32
LV15 | 15 | 6000 | 90 | 62 | 125 | 155.7 | 0.974 | 23.41 | 151.7 |  | 32
LV15 | 15 | 6000 | 70 | 67 | 125 | 144.9 | 0.458 | 10.23 | 66.3 |  | 32
LV15 | 15 | 6000 | 75 | 67 | 125 | 145.6 | 0.633 | 14.23 | 92.2 |  | 32
LV15 | 15 | 6000 | 80 | 67 | 125 | 146.3 | 0.818 | 18.47 | 119.7 |  | 32
LV15 | 15 | 6000 | 85 | 67 | 125 | 146.6 | 0.974 | 22.04 | 142.8 |  | 32
LV15 | 15 | 6000 | 90 | 67 | 125 | 155.7 | 0.974 | 23.41 | 151.7 |  | 32
LV15 | 15 | 6000 | 75 | 72 | 125 | 159.5 | 0.419 | 10.31 | 66.8 |  | 32
LV15 | 15 | 6000 | 80 | 72 | 125 | 159.8 | 0.584 | 14.41 | 93.4 |  | 32
LV15 | 15 | 6000 | 85 | 72 | 125 | 159.7 | 0.75 | 18.49 | 119.8 |  | 32
LV15 | 15 | 6000 | 90 | 72 | 125 | 159.7 | 0.915 | 22.56 | 146.2 |  | 32
LV15 | 15 | 6000 | 80 | 77 | 125 | 174.4 | 0.389 | 10.48 | 67.9 |  | 32
LV15 | 15 | 6000 | 85 | 77 | 125 | 174.4 | 0.536 | 14.41 | 93.4 |  | 32
LV15 | 15 | 6000 | 90 | 77 | 125 | 174 | 0.691 | 18.56 | 120.3 |  | 32
LV15 | 15 | 6750 | 65 | 57 | 75 | 172.7 | 0.711 | 16.84 | 122.8 |  | 30
LV15 | 15 | 6750 | 70 | 57 | 75 | 173.5 | 0.886 | 21.1 | 153.8 |  | 30
LV15 | 15 | 6750 | 75 | 57 | 75 | 179.4 | 0.974 | 23.96 | 174.7 |  | 30
LV15 | 15 | 6750 | 80 | 57 | 75 | 189.8 | 0.974 | 25.36 | 184.9 |  | 30
LV15 | 15 | 6750 | 85 | 57 | 75 | 200.4 | 0.974 | 26.78 | 195.2 |  | 30
LV15 | 15 | 6750 | 90 | 57 | 75 | 210.9 | 0.974 | 28.18 | 205.4 |  | 30
LV15 | 15 | 6750 | 65 | 62 | 75 | 187.8 | 0.487 | 12.55 | 91.5 |  | 30
LV15 | 15 | 6750 | 70 | 62 | 75 | 189.1 | 0.653 | 16.93 | 123.4 |  | 30
LV15 | 15 | 6750 | 75 | 62 | 75 | 189.7 | 0.818 | 21.29 | 155.2 |  | 30
LV15 | 15 | 6750 | 80 | 62 | 75 | 189.9 | 0.974 | 25.36 | 184.9 |  | 30
LV15 | 15 | 6750 | 85 | 62 | 75 | 200.4 | 0.974 | 26.78 | 195.2 |  | 30
LV15 | 15 | 6750 | 90 | 62 | 75 | 210.9 | 0.974 | 28.19 | 205.5 |  | 30
LV15 | 15 | 6750 | 70 | 67 | 75 | 204.4 | 0.448 | 12.57 | 91.6 |  | 30
LV15 | 15 | 6750 | 75 | 67 | 75 | 205.3 | 0.594 | 16.74 | 122 |  | 30
LV15 | 15 | 6750 | 80 | 67 | 75 | 205.8 | 0.75 | 21.18 | 154.4 |  | 30
LV15 | 15 | 6750 | 85 | 67 | 75 | 205.7 | 0.906 | 25.57 | 186.4 |  | 30
LV15 | 15 | 6750 | 90 | 67 | 75 | 210.9 | 0.974 | 28.19 | 205.5 |  | 30
LV15 | 15 | 6750 | 75 | 72 | 75 | 221.5 | 0.409 | 12.43 | 90.6 |  | 30
LV15 | 15 | 6750 | 80 | 72 | 75 | 222.3 | 0.546 | 16.64 | 121.3 |  | 30
LV15 | 15 | 6750 | 85 | 72 | 75 | 222.5 | 0.692 | 21.11 | 153.9 |  | 30
LV15 | 15 | 6750 | 90 | 72 | 75 | 222.8 | 0.828 | 25.31 | 184.5 |  | 30
LV15 | 15 | 6750 | 80 | 77 | 75 | 239.1 | 0.38 | 12.46 | 90.8 |  | 30
LV15 | 15 | 6750 | 85 | 77 | 75 | 239.4 | 0.507 | 16.64 | 121.3 |  | 30
LV15 | 15 | 6750 | 90 | 77 | 75 | 239.6 | 0.633 | 20.81 | 151.7 |  | 30
LV15 | 15 | 6750 | 65 | 57 | 85 | 163.2 | 0.721 | 16.13 | 117.6 |  | 30
LV15 | 15 | 6750 | 70 | 57 | 85 | 163.9 | 0.906 | 20.37 | 148.5 |  | 30
LV15 | 15 | 6750 | 75 | 57 | 85 | 170.9 | 0.974 | 22.84 | 166.5 |  | 30
LV15 | 15 | 6750 | 80 | 57 | 85 | 181.4 | 0.974 | 24.24 | 176.7 |  | 30
LV15 | 15 | 6750 | 85 | 57 | 85 | 191.7 | 0.974 | 25.62 | 186.8 |  | 30
LV15 | 15 | 6750 | 90 | 57 | 85 | 202.2 | 0.974 | 27.01 | 196.9 |  | 30
LV15 | 15 | 6750 | 65 | 62 | 85 | 177.8 | 0.487 | 11.88 | 86.6 |  | 30
LV15 | 15 | 6750 | 70 | 62 | 85 | 179.1 | 0.662 | 16.27 | 118.6 |  | 30
LV15 | 15 | 6750 | 75 | 62 | 85 | 180 | 0.828 | 20.45 | 149.1 |  | 30
LV15 | 15 | 6750 | 80 | 62 | 85 | 181.4 | 0.974 | 24.24 | 176.7 |  | 30
LV15 | 15 | 6750 | 85 | 62 | 85 | 192.1 | 0.974 | 25.67 | 187.1 |  | 30
LV15 | 15 | 6750 | 90 | 62 | 85 | 202.2 | 0.974 | 27.02 | 197 |  | 30
LV15 | 15 | 6750 | 70 | 67 | 85 | 194 | 0.448 | 11.92 | 86.9 |  | 30
LV15 | 15 | 6750 | 75 | 67 | 85 | 194.9 | 0.604 | 16.15 | 117.7 |  | 30
LV15 | 15 | 6750 | 80 | 67 | 85 | 195.5 | 0.77 | 20.64 | 150.5 |  | 30
LV15 | 15 | 6750 | 85 | 67 | 85 | 195.9 | 0.916 | 24.61 | 179.4 |  | 30
LV15 | 15 | 6750 | 90 | 67 | 85 | 202.2 | 0.974 | 27.02 | 197 |  | 30
LV15 | 15 | 6750 | 75 | 72 | 85 | 210.9 | 0.409 | 11.84 | 86.3 |  | 30
LV15 | 15 | 6750 | 80 | 72 | 85 | 211.7 | 0.555 | 16.12 | 117.5 |  | 30
LV15 | 15 | 6750 | 85 | 72 | 85 | 212 | 0.701 | 20.4 | 148.7 |  | 30
LV15 | 15 | 6750 | 90 | 72 | 85 | 212.1 | 0.847 | 24.65 | 179.7 |  | 30
LV15 | 15 | 6750 | 80 | 77 | 85 | 228.2 | 0.38 | 11.89 | 86.7 |  | 30
LV15 | 15 | 6750 | 85 | 77 | 85 | 228.6 | 0.516 | 16.19 | 118 |  | 30
LV15 | 15 | 6750 | 90 | 77 | 85 | 228.7 | 0.652 | 20.47 | 149.2 |  | 30
LV15 | 15 | 6750 | 65 | 57 | 95 | 153 | 0.731 | 15.34 | 111.8 |  | 31
LV15 | 15 | 6750 | 70 | 57 | 95 | 154.2 | 0.925 | 19.57 | 142.7 |  | 31
LV15 | 15 | 6750 | 75 | 57 | 95 | 161.9 | 0.974 | 21.63 | 157.7 |  | 31
LV15 | 15 | 6750 | 80 | 57 | 95 | 172.2 | 0.974 | 23 | 167.7 |  | 31
LV15 | 15 | 6750 | 85 | 57 | 95 | 182.4 | 0.974 | 24.38 | 177.7 |  | 31
LV15 | 15 | 6750 | 90 | 57 | 95 | 192.8 | 0.974 | 25.76 | 187.8 |  | 31
LV15 | 15 | 6750 | 65 | 62 | 95 | 167.2 | 0.497 | 11.4 | 83.1 |  | 31
LV15 | 15 | 6750 | 70 | 62 | 95 | 168.6 | 0.672 | 15.54 | 113.3 |  | 31
LV15 | 15 | 6750 | 75 | 62 | 95 | 169.5 | 0.848 | 19.71 | 143.7 |  | 31
LV15 | 15 | 6750 | 80 | 62 | 95 | 172.2 | 0.974 | 23.02 | 167.8 |  | 31
LV15 | 15 | 6750 | 85 | 62 | 95 | 182.5 | 0.974 | 24.39 | 177.8 |  | 31
LV15 | 15 | 6750 | 90 | 62 | 95 | 192.8 | 0.974 | 25.76 | 187.8 |  | 31
LV15 | 15 | 6750 | 70 | 67 | 95 | 183 | 0.458 | 11.5 | 83.8 |  | 31
LV15 | 15 | 6750 | 75 | 67 | 95 | 183.8 | 0.614 | 15.47 | 112.8 |  | 31
LV15 | 15 | 6750 | 80 | 67 | 95 | 184.5 | 0.779 | 19.73 | 143.8 |  | 31
LV15 | 15 | 6750 | 85 | 67 | 95 | 184.5 | 0.945 | 23.92 | 174.4 |  | 31
LV15 | 15 | 6750 | 90 | 67 | 95 | 192.8 | 0.974 | 25.76 | 187.8 |  | 31
LV15 | 15 | 6750 | 75 | 72 | 95 | 199.5 | 0.419 | 11.45 | 83.5 |  | 31
LV15 | 15 | 6750 | 80 | 72 | 95 | 200.3 | 0.565 | 15.53 | 113.2 |  | 31
LV15 | 15 | 6750 | 85 | 72 | 95 | 200.6 | 0.721 | 19.84 | 144.6 |  | 31
LV15 | 15 | 6750 | 90 | 72 | 95 | 200.4 | 0.877 | 24.1 | 175.7 |  | 31
LV15 | 15 | 6750 | 80 | 77 | 95 | 216.5 | 0.38 | 11.29 | 82.3 |  | 31
LV15 | 15 | 6750 | 85 | 77 | 95 | 216.9 | 0.516 | 15.36 | 112 |  | 31
LV15 | 15 | 6750 | 90 | 77 | 95 | 216.9 | 0.662 | 19.7 | 143.6 |  | 31
LV15 | 15 | 6750 | 65 | 57 | 105 | 142.2 | 0.75 | 14.64 | 106.7 |  | 31
LV15 | 15 | 6750 | 70 | 57 | 105 | 142.8 | 0.955 | 18.71 | 136.4 |  | 31
LV15 | 15 | 6750 | 75 | 57 | 105 | 152.3 | 0.974 | 20.36 | 148.4 |  | 31
LV15 | 15 | 6750 | 80 | 57 | 105 | 162.6 | 0.974 | 21.71 | 158.3 |  | 31
LV15 | 15 | 6750 | 85 | 57 | 105 | 172.6 | 0.975 | 23.07 | 168.2 |  | 31
LV15 | 15 | 6750 | 90 | 57 | 105 | 182.6 | 0.974 | 24.4 | 177.9 |  | 31
LV15 | 15 | 6750 | 65 | 62 | 105 | 155.9 | 0.497 | 10.63 | 77.5 |  | 31
LV15 | 15 | 6750 | 70 | 62 | 105 | 157.3 | 0.682 | 14.71 | 107.2 |  | 31
LV15 | 15 | 6750 | 75 | 62 | 105 | 157.9 | 0.877 | 18.98 | 138.4 |  | 31
LV15 | 15 | 6750 | 80 | 62 | 105 | 162.5 | 0.974 | 21.7 | 158.2 |  | 31
LV15 | 15 | 6750 | 85 | 62 | 105 | 172.4 | 0.974 | 23.03 | 167.9 |  | 31
LV15 | 15 | 6750 | 90 | 62 | 105 | 182.6 | 0.974 | 24.4 | 177.9 |  | 31
LV15 | 15 | 6750 | 70 | 67 | 105 | 171.3 | 0.458 | 10.75 | 78.4 |  | 31
LV15 | 15 | 6750 | 75 | 67 | 105 | 172.2 | 0.633 | 14.95 | 109 |  | 31
LV15 | 15 | 6750 | 80 | 67 | 105 | 172.9 | 0.799 | 18.94 | 138.1 |  | 31
LV15 | 15 | 6750 | 85 | 67 | 105 | 172.7 | 0.974 | 23.07 | 168.2 |  | 31
LV15 | 15 | 6750 | 90 | 67 | 105 | 182.7 | 0.974 | 24.42 | 178 |  | 31
LV15 | 15 | 6750 | 75 | 72 | 105 | 187.5 | 0.419 | 10.77 | 78.5 |  | 31
LV15 | 15 | 6750 | 80 | 72 | 105 | 188 | 0.575 | 14.83 | 108.1 |  | 31
LV15 | 15 | 6750 | 85 | 72 | 105 | 188.2 | 0.74 | 19.11 | 139.3 |  | 31
LV15 | 15 | 6750 | 90 | 72 | 105 | 188.4 | 0.896 | 23.16 | 168.8 |  | 31
LV15 | 15 | 6750 | 80 | 77 | 105 | 203.7 | 0.38 | 10.62 | 77.4 |  | 31
LV15 | 15 | 6750 | 85 | 77 | 105 | 204 | 0.536 | 14.99 | 109.3 |  | 31
LV15 | 15 | 6750 | 90 | 77 | 105 | 204 | 0.682 | 19.08 | 139.1 |  | 31
LV15 | 15 | 6750 | 65 | 57 | 115 | 130.8 | 0.77 | 13.81 | 100.7 |  | 32
LV15 | 15 | 6750 | 70 | 57 | 115 | 132.1 | 0.974 | 17.64 | 128.6 |  | 32
LV15 | 15 | 6750 | 75 | 57 | 115 | 142.1 | 0.975 | 19 | 138.5 |  | 32
LV15 | 15 | 6750 | 80 | 57 | 115 | 152.2 | 0.974 | 20.33 | 148.2 |  | 32
LV15 | 15 | 6750 | 85 | 57 | 115 | 161.6 | 0.974 | 21.59 | 157.4 |  | 32
LV15 | 15 | 6750 | 90 | 57 | 115 | 171.9 | 0.974 | 22.96 | 167.4 |  | 32
LV15 | 15 | 6750 | 65 | 62 | 115 | 144.1 | 0.507 | 10.01 | 73 |  | 32
LV15 | 15 | 6750 | 70 | 62 | 115 | 145.2 | 0.701 | 13.96 | 101.8 |  | 32
LV15 | 15 | 6750 | 75 | 62 | 115 | 145.9 | 0.906 | 18.13 | 132.2 |  | 32
LV15 | 15 | 6750 | 80 | 62 | 115 | 152.1 | 0.974 | 20.33 | 148.2 |  | 32
LV15 | 15 | 6750 | 85 | 62 | 115 | 162 | 0.974 | 21.65 | 157.8 |  | 32
LV15 | 15 | 6750 | 90 | 62 | 115 | 171.9 | 0.974 | 22.96 | 167.4 |  | 32
LV15 | 15 | 6750 | 70 | 67 | 115 | 158.8 | 0.458 | 9.97 | 72.7 |  | 32
LV15 | 15 | 6750 | 75 | 67 | 115 | 159.9 | 0.643 | 14.1 | 102.8 |  | 32
LV15 | 15 | 6750 | 80 | 67 | 115 | 160.3 | 0.828 | 18.2 | 132.7 |  | 32
LV15 | 15 | 6750 | 85 | 67 | 115 | 162.1 | 0.974 | 21.66 | 157.9 |  | 32
LV15 | 15 | 6750 | 90 | 67 | 115 | 171.8 | 0.974 | 22.96 | 167.4 |  | 32
LV15 | 15 | 6750 | 75 | 72 | 115 | 174.7 | 0.419 | 10.04 | 73.2 |  | 32
LV15 | 15 | 6750 | 80 | 72 | 115 | 174.9 | 0.594 | 14.25 | 103.9 |  | 32
LV15 | 15 | 6750 | 85 | 72 | 115 | 175.1 | 0.76 | 18.24 | 133 |  | 32
LV15 | 15 | 6750 | 90 | 72 | 115 | 174.3 | 0.935 | 22.36 | 163 |  | 32
LV15 | 15 | 6750 | 80 | 77 | 115 | 190.5 | 0.39 | 10.18 | 74.2 |  | 32
LV15 | 15 | 6750 | 85 | 77 | 115 | 190.4 | 0.546 | 14.25 | 103.9 |  | 32
LV15 | 15 | 6750 | 90 | 77 | 115 | 190.5 | 0.701 | 18.33 | 133.6 |  | 32
LV15 | 15 | 6750 | 65 | 57 | 125 | 118.8 | 0.789 | 12.85 | 93.7 |  | 32
LV15 | 15 | 6750 | 70 | 57 | 125 | 121.5 | 0.974 | 16.23 | 118.3 |  | 32
LV15 | 15 | 6750 | 75 | 57 | 125 | 131.3 | 0.974 | 17.54 | 127.9 |  | 32
LV15 | 15 | 6750 | 80 | 57 | 125 | 141.1 | 0.974 | 18.85 | 137.4 |  | 32
LV15 | 15 | 6750 | 85 | 57 | 125 | 150.7 | 0.974 | 20.14 | 146.8 |  | 32
LV15 | 15 | 6750 | 90 | 57 | 125 | 160.2 | 0.974 | 21.4 | 156 |  | 32
LV15 | 15 | 6750 | 65 | 62 | 125 | 131.8 | 0.507 | 9.16 | 66.8 |  | 32
LV15 | 15 | 6750 | 70 | 62 | 125 | 132.8 | 0.721 | 13.13 | 95.7 |  | 32
LV15 | 15 | 6750 | 75 | 62 | 125 | 132.8 | 0.945 | 17.22 | 125.5 |  | 32
LV15 | 15 | 6750 | 80 | 62 | 125 | 141 | 0.974 | 18.85 | 137.4 |  | 32
LV15 | 15 | 6750 | 85 | 62 | 125 | 150.5 | 0.974 | 20.11 | 146.6 |  | 32
LV15 | 15 | 6750 | 90 | 62 | 125 | 160.2 | 0.974 | 21.4 | 156 |  | 32
LV15 | 15 | 6750 | 70 | 67 | 125 | 145.8 | 0.468 | 9.36 | 68.2 |  | 32
LV15 | 15 | 6750 | 75 | 67 | 125 | 146.7 | 0.662 | 13.32 | 97.1 |  | 32
LV15 | 15 | 6750 | 80 | 67 | 125 | 146.9 | 0.857 | 17.27 | 125.9 |  | 32
LV15 | 15 | 6750 | 85 | 67 | 125 | 150.7 | 0.974 | 20.14 | 146.8 |  | 32
LV15 | 15 | 6750 | 90 | 67 | 125 | 160.2 | 0.974 | 21.4 | 156 |  | 32
LV15 | 15 | 6750 | 75 | 72 | 125 | 160.6 | 0.428 | 9.44 | 68.8 |  | 32
LV15 | 15 | 6750 | 80 | 72 | 125 | 161.6 | 0.604 | 13.39 | 97.6 |  | 32
LV15 | 15 | 6750 | 85 | 72 | 125 | 161.1 | 0.789 | 17.43 | 127.1 |  | 32
LV15 | 15 | 6750 | 90 | 72 | 125 | 160.1 | 0.974 | 21.4 | 156 |  | 32
LV15 | 15 | 6750 | 80 | 77 | 125 | 175.8 | 0.39 | 9.4 | 68.5 |  | 32
LV15 | 15 | 6750 | 85 | 77 | 125 | 175.9 | 0.555 | 13.4 | 97.7 |  | 32
LV15 | 15 | 6750 | 90 | 77 | 125 | 175.7 | 0.731 | 17.61 | 128.4 |  | 32
LV15 | 15 | 7500 | 65 | 57 | 75 | 175.3 | 0.73 | 15.8 | 128 |  | 30
LV15 | 15 | 7500 | 70 | 57 | 75 | 176.3 | 0.916 | 19.94 | 161.5 |  | 30
LV15 | 15 | 7500 | 75 | 57 | 75 | 184.5 | 0.974 | 22.19 | 179.7 |  | 30
LV15 | 15 | 7500 | 80 | 57 | 75 | 195.5 | 0.974 | 23.51 | 190.4 |  | 30
LV15 | 15 | 7500 | 85 | 57 | 75 | 206.4 | 0.974 | 24.81 | 201 |  | 30
LV15 | 15 | 7500 | 90 | 57 | 75 | 217.4 | 0.974 | 26.14 | 211.7 |  | 30
LV15 | 15 | 7500 | 65 | 62 | 75 | 190.4 | 0.497 | 11.68 | 94.6 |  | 30
LV15 | 15 | 7500 | 70 | 62 | 75 | 191.7 | 0.672 | 15.91 | 128.9 |  | 30
LV15 | 15 | 7500 | 75 | 62 | 75 | 192.9 | 0.848 | 20.19 | 163.5 |  | 30
LV15 | 15 | 7500 | 80 | 62 | 75 | 195.5 | 0.974 | 23.52 | 190.5 |  | 30
LV15 | 15 | 7500 | 85 | 62 | 75 | 206.4 | 0.974 | 24.83 | 201.1 |  | 30
LV15 | 15 | 7500 | 90 | 62 | 75 | 217.4 | 0.974 | 26.15 | 211.8 |  | 30
LV15 | 15 | 7500 | 70 | 67 | 75 | 207.4 | 0.448 | 11.47 | 92.9 |  | 30
LV15 | 15 | 7500 | 75 | 67 | 75 | 208.3 | 0.614 | 15.78 | 127.8 |  | 30
LV15 | 15 | 7500 | 80 | 67 | 75 | 209 | 0.779 | 20.1 | 162.8 |  | 30
LV15 | 15 | 7500 | 85 | 67 | 75 | 210.4 | 0.935 | 24.28 | 196.7 |  | 30
LV15 | 15 | 7500 | 90 | 67 | 75 | 217.5 | 0.974 | 26.15 | 211.8 |  | 30
LV15 | 15 | 7500 | 75 | 72 | 75 | 224.5 | 0.419 | 11.6 | 94 |  | 30
LV15 | 15 | 7500 | 80 | 72 | 75 | 225.5 | 0.565 | 15.73 | 127.4 |  | 30
LV15 | 15 | 7500 | 85 | 72 | 75 | 225.7 | 0.721 | 20.09 | 162.7 |  | 30
LV15 | 15 | 7500 | 90 | 72 | 75 | 225.8 | 0.867 | 24.16 | 195.7 |  | 30
LV15 | 15 | 7500 | 80 | 77 | 75 | 242.9 | 0.38 | 11.4 | 92.3 |  | 30
LV15 | 15 | 7500 | 85 | 77 | 75 | 242.6 | 0.526 | 15.75 | 127.6 |  | 30
LV15 | 15 | 7500 | 90 | 77 | 75 | 242.8 | 0.662 | 19.85 | 160.8 |  | 30
LV15 | 15 | 7500 | 65 | 57 | 85 | 165.5 | 0.74 | 15.12 | 122.5 |  | 30
LV15 | 15 | 7500 | 70 | 57 | 85 | 166.1 | 0.945 | 19.37 | 156.9 |  | 30
LV15 | 15 | 7500 | 75 | 57 | 85 | 175.6 | 0.974 | 21.12 | 171.1 |  | 30
LV15 | 15 | 7500 | 80 | 57 | 85 | 186.5 | 0.974 | 22.42 | 181.6 |  | 30
LV15 | 15 | 7500 | 85 | 57 | 85 | 197.3 | 0.974 | 23.73 | 192.2 |  | 30
LV15 | 15 | 7500 | 90 | 57 | 85 | 208.1 | 0.975 | 25.04 | 202.8 |  | 30
LV15 | 15 | 7500 | 65 | 62 | 85 | 179.9 | 0.497 | 11.04 | 89.4 |  | 30
LV15 | 15 | 7500 | 70 | 62 | 85 | 181.3 | 0.682 | 15.26 | 123.6 |  | 30
LV15 | 15 | 7500 | 75 | 62 | 85 | 182.3 | 0.867 | 19.51 | 158 |  | 30
LV15 | 15 | 7500 | 80 | 62 | 85 | 186.5 | 0.974 | 22.43 | 181.7 |  | 30
LV15 | 15 | 7500 | 85 | 62 | 85 | 197.3 | 0.974 | 23.73 | 192.2 |  | 30
LV15 | 15 | 7500 | 90 | 62 | 85 | 208.2 | 0.974 | 25.04 | 202.8 |  | 30
LV15 | 15 | 7500 | 70 | 67 | 85 | 196.4 | 0.458 | 11.1 | 89.9 |  | 30
LV15 | 15 | 7500 | 75 | 67 | 85 | 197.7 | 0.623 | 15.21 | 123.2 |  | 30
LV15 | 15 | 7500 | 80 | 67 | 85 | 198.3 | 0.799 | 19.56 | 158.4 |  | 30
LV15 | 15 | 7500 | 85 | 67 | 85 | 197.4 | 0.974 | 23.74 | 192.3 |  | 30
LV15 | 15 | 7500 | 90 | 67 | 85 | 208.2 | 0.974 | 25.04 | 202.8 |  | 30
LV15 | 15 | 7500 | 75 | 72 | 85 | 213.6 | 0.419 | 11.05 | 89.5 |  | 30
LV15 | 15 | 7500 | 80 | 72 | 85 | 214.5 | 0.575 | 15.22 | 123.3 |  | 30
LV15 | 15 | 7500 | 85 | 72 | 85 | 214.9 | 0.731 | 19.38 | 157 |  | 30
LV15 | 15 | 7500 | 90 | 72 | 85 | 214.6 | 0.896 | 23.74 | 192.3 |  | 30
LV15 | 15 | 7500 | 80 | 77 | 85 | 231.1 | 0.38 | 10.84 | 87.8 |  | 30
LV15 | 15 | 7500 | 85 | 77 | 85 | 231.4 | 0.526 | 15.02 | 121.7 |  | 30
LV15 | 15 | 7500 | 90 | 77 | 85 | 231.3 | 0.682 | 19.47 | 157.7 |  | 30
LV15 | 15 | 7500 | 65 | 57 | 95 | 154.8 | 0.76 | 14.52 | 117.6 |  | 31
LV15 | 15 | 7500 | 70 | 57 | 95 | 155.2 | 0.974 | 18.65 | 151.1 |  | 31
LV15 | 15 | 7500 | 75 | 57 | 95 | 166.1 | 0.974 | 19.98 | 161.8 |  | 31
LV15 | 15 | 7500 | 80 | 57 | 95 | 176.9 | 0.974 | 21.27 | 172.3 |  | 31
LV15 | 15 | 7500 | 85 | 57 | 95 | 187.5 | 0.974 | 22.56 | 182.7 |  | 31
LV15 | 15 | 7500 | 90 | 57 | 95 | 198.2 | 0.974 | 23.84 | 193.1 |  | 31
LV15 | 15 | 7500 | 65 | 62 | 95 | 168.8 | 0.497 | 10.36 | 83.9 |  | 31
LV15 | 15 | 7500 | 70 | 62 | 95 | 170.2 | 0.692 | 14.53 | 117.7 |  | 31
LV15 | 15 | 7500 | 75 | 62 | 95 | 171.1 | 0.887 | 18.73 | 151.7 |  | 31
LV15 | 15 | 7500 | 80 | 62 | 95 | 176.8 | 0.974 | 21.26 | 172.2 |  | 31
LV15 | 15 | 7500 | 85 | 62 | 95 | 187.6 | 0.974 | 22.56 | 182.7 |  | 31
LV15 | 15 | 7500 | 90 | 62 | 95 | 198.3 | 0.974 | 23.85 | 193.2 |  | 31
LV15 | 15 | 7500 | 70 | 67 | 95 | 185.2 | 0.458 | 10.47 | 84.8 |  | 31
LV15 | 15 | 7500 | 75 | 67 | 95 | 186.3 | 0.633 | 14.56 | 117.9 |  | 31
LV15 | 15 | 7500 | 80 | 67 | 95 | 187.1 | 0.818 | 18.9 | 153.1 |  | 31
LV15 | 15 | 7500 | 85 | 67 | 95 | 187.6 | 0.974 | 22.57 | 182.8 |  | 31
LV15 | 15 | 7500 | 90 | 67 | 95 | 198.3 | 0.974 | 23.84 | 193.1 |  | 31
LV15 | 15 | 7500 | 75 | 72 | 95 | 201.8 | 0.419 | 10.43 | 84.5 |  | 31
LV15 | 15 | 7500 | 80 | 72 | 95 | 202.6 | 0.584 | 14.62 | 118.4 |  | 31
LV15 | 15 | 7500 | 85 | 72 | 95 | 202.5 | 0.75 | 18.75 | 151.9 |  | 31
LV15 | 15 | 7500 | 90 | 72 | 95 | 202.8 | 0.916 | 22.93 | 185.7 |  | 31
LV15 | 15 | 7500 | 80 | 77 | 95 | 218.7 | 0.39 | 10.52 | 85.2 |  | 31
LV15 | 15 | 7500 | 85 | 77 | 95 | 219.1 | 0.536 | 14.49 | 117.4 |  | 31
LV15 | 15 | 7500 | 90 | 77 | 95 | 219.1 | 0.692 | 18.72 | 151.6 |  | 31
LV15 | 15 | 7500 | 65 | 57 | 105 | 143.5 | 0.769 | 13.63 | 110.4 |  | 31
LV15 | 15 | 7500 | 70 | 57 | 105 | 145.2 | 0.975 | 17.47 | 141.5 |  | 31
LV15 | 15 | 7500 | 75 | 57 | 105 | 155.9 | 0.974 | 18.75 | 151.9 |  | 31
LV15 | 15 | 7500 | 80 | 57 | 105 | 166.7 | 0.974 | 20.04 | 162.3 |  | 31
LV15 | 15 | 7500 | 85 | 57 | 105 | 177.3 | 0.974 | 21.32 | 172.7 |  | 31
LV15 | 15 | 7500 | 90 | 57 | 105 | 187.7 | 0.974 | 22.57 | 182.8 |  | 31
LV15 | 15 | 7500 | 65 | 62 | 105 | 157.1 | 0.507 | 9.83 | 79.6 |  | 31
LV15 | 15 | 7500 | 70 | 62 | 105 | 158.5 | 0.711 | 13.91 | 112.7 |  | 31
LV15 | 15 | 7500 | 75 | 62 | 105 | 159.8 | 0.906 | 17.86 | 144.7 |  | 31
LV15 | 15 | 7500 | 80 | 62 | 105 | 166.6 | 0.974 | 20.04 | 162.3 |  | 31
LV15 | 15 | 7500 | 85 | 62 | 105 | 177.2 | 0.974 | 21.31 | 172.6 |  | 31
LV15 | 15 | 7500 | 90 | 62 | 105 | 187.6 | 0.974 | 22.57 | 182.8 |  | 31
LV15 | 15 | 7500 | 70 | 67 | 105 | 172.9 | 0.468 | 9.99 | 80.9 |  | 31
LV15 | 15 | 7500 | 75 | 67 | 105 | 173.8 | 0.653 | 14.01 | 113.5 |  | 31
LV15 | 15 | 7500 | 80 | 67 | 105 | 174.5 | 0.838 | 18.05 | 146.2 |  | 31
LV15 | 15 | 7500 | 85 | 67 | 105 | 177.3 | 0.974 | 21.32 | 172.7 |  | 31
LV15 | 15 | 7500 | 90 | 67 | 105 | 187.6 | 0.974 | 22.57 | 182.8 |  | 31
LV15 | 15 | 7500 | 75 | 72 | 105 | 189.1 | 0.429 | 10.01 | 81.1 |  | 31
LV15 | 15 | 7500 | 80 | 72 | 105 | 189.9 | 0.595 | 13.94 | 112.9 |  | 31
LV15 | 15 | 7500 | 85 | 72 | 105 | 190.3 | 0.769 | 18.07 | 146.4 |  | 31
LV15 | 15 | 7500 | 90 | 72 | 105 | 189.3 | 0.945 | 22.09 | 178.9 |  | 31
LV15 | 15 | 7500 | 80 | 77 | 105 | 206 | 0.389 | 9.9 | 80.2 |  | 31
LV15 | 15 | 7500 | 85 | 77 | 105 | 205.7 | 0.545 | 13.85 | 112.2 |  | 31
LV15 | 15 | 7500 | 90 | 77 | 105 | 205.7 | 0.711 | 18.05 | 146.2 |  | 31
LV15 | 15 | 7500 | 65 | 57 | 115 | 131.7 | 0.789 | 12.83 | 103.9 |  | 32
LV15 | 15 | 7500 | 70 | 57 | 115 | 134.7 | 0.974 | 16.2 | 131.2 |  | 32
LV15 | 15 | 7500 | 75 | 57 | 115 | 145.2 | 0.974 | 17.46 | 141.4 |  | 32
LV15 | 15 | 7500 | 80 | 57 | 115 | 155.6 | 0.974 | 18.72 | 151.6 |  | 32
LV15 | 15 | 7500 | 85 | 57 | 115 | 166 | 0.973 | 19.95 | 161.6 |  | 32
LV15 | 15 | 7500 | 90 | 57 | 115 | 176.1 | 0.974 | 21.17 | 171.5 |  | 32
LV15 | 15 | 7500 | 65 | 62 | 115 | 144.6 | 0.507 | 9.05 | 73.3 |  | 32
LV15 | 15 | 7500 | 70 | 62 | 115 | 146.2 | 0.731 | 13.19 | 106.8 |  | 32
LV15 | 15 | 7500 | 75 | 62 | 115 | 146.6 | 0.945 | 17.1 | 138.5 |  | 32
LV15 | 15 | 7500 | 80 | 62 | 115 | 155.6 | 0.974 | 18.72 | 151.6 |  | 32
LV15 | 15 | 7500 | 85 | 62 | 115 | 166 | 0.974 | 19.96 | 161.7 |  | 32
LV15 | 15 | 7500 | 90 | 62 | 115 | 176.1 | 0.974 | 21.17 | 171.5 |  | 32
LV15 | 15 | 7500 | 70 | 67 | 115 | 160.3 | 0.468 | 9.26 | 75 |  | 32
LV15 | 15 | 7500 | 75 | 67 | 115 | 161.2 | 0.663 | 13.19 | 106.8 |  | 32
LV15 | 15 | 7500 | 80 | 67 | 115 | 161.4 | 0.867 | 17.27 | 139.9 |  | 32
LV15 | 15 | 7500 | 85 | 67 | 115 | 165.9 | 0.974 | 19.95 | 161.6 |  | 32
LV15 | 15 | 7500 | 90 | 67 | 115 | 176.1 | 0.974 | 21.17 | 171.5 |  | 32
LV15 | 15 | 7500 | 75 | 72 | 115 | 175.8 | 0.428 | 9.3 | 75.3 |  | 32
LV15 | 15 | 7500 | 80 | 72 | 115 | 176.4 | 0.613 | 13.36 | 108.2 |  | 32
LV15 | 15 | 7500 | 85 | 72 | 115 | 176.7 | 0.799 | 17.43 | 141.2 |  | 32
LV15 | 15 | 7500 | 90 | 72 | 115 | 176.2 | 0.974 | 21.19 | 171.6 |  | 32
LV15 | 15 | 7500 | 80 | 77 | 115 | 191.5 | 0.39 | 9.21 | 74.6 |  | 32
LV15 | 15 | 7500 | 85 | 77 | 115 | 191.9 | 0.565 | 13.38 | 108.4 |  | 32
LV15 | 15 | 7500 | 90 | 77 | 115 | 191.3 | 0.74 | 17.48 | 141.6 |  | 32
LV15 | 15 | 7500 | 65 | 57 | 125 | 119.3 | 0.818 | 12.05 | 97.6 |  | 32
LV15 | 15 | 7500 | 70 | 57 | 125 | 123.6 | 0.974 | 14.86 | 120.4 |  | 32
LV15 | 15 | 7500 | 75 | 57 | 125 | 133.9 | 0.974 | 16.1 | 130.4 |  | 32
LV15 | 15 | 7500 | 80 | 57 | 125 | 143.9 | 0.974 | 17.31 | 140.2 |  | 32
LV15 | 15 | 7500 | 85 | 57 | 125 | 154 | 0.974 | 18.52 | 150 |  | 32
LV15 | 15 | 7500 | 90 | 57 | 125 | 163.8 | 0.974 | 19.69 | 159.5 |  | 32
LV15 | 15 | 7500 | 65 | 62 | 125 | 131.7 | 0.516 | 8.4 | 68 |  | 32
LV15 | 15 | 7500 | 70 | 62 | 125 | 133 | 0.75 | 12.32 | 99.8 |  | 32
LV15 | 15 | 7500 | 75 | 62 | 125 | 133.8 | 0.975 | 16.1 | 130.4 |  | 32
LV15 | 15 | 7500 | 80 | 62 | 125 | 144 | 0.974 | 17.32 | 140.3 |  | 32
LV15 | 15 | 7500 | 85 | 62 | 125 | 153.9 | 0.974 | 18.51 | 149.9 |  | 32
LV15 | 15 | 7500 | 90 | 62 | 125 | 163.9 | 0.974 | 19.7 | 159.6 |  | 32
LV15 | 15 | 7500 | 70 | 67 | 125 | 146.4 | 0.477 | 8.63 | 69.9 |  | 32
LV15 | 15 | 7500 | 75 | 67 | 125 | 147.6 | 0.682 | 12.43 | 100.7 |  | 32
LV15 | 15 | 7500 | 80 | 67 | 125 | 147.6 | 0.896 | 16.33 | 132.3 |  | 32
LV15 | 15 | 7500 | 85 | 67 | 125 | 153.9 | 0.974 | 18.51 | 149.9 |  | 32
LV15 | 15 | 7500 | 90 | 67 | 125 | 163.8 | 0.974 | 19.69 | 159.5 |  | 32
LV15 | 15 | 7500 | 75 | 72 | 125 | 162 | 0.438 | 8.77 | 71 |  | 32
LV15 | 15 | 7500 | 80 | 72 | 125 | 162.1 | 0.634 | 12.68 | 102.7 |  | 32
LV15 | 15 | 7500 | 85 | 72 | 125 | 161.8 | 0.828 | 16.53 | 133.9 |  | 32
LV15 | 15 | 7500 | 90 | 72 | 125 | 163.8 | 0.974 | 19.7 | 159.6 |  | 32
LV15 | 15 | 7500 | 80 | 77 | 125 | 177.3 | 0.399 | 8.74 | 70.8 |  | 32
LV15 | 15 | 7500 | 85 | 77 | 125 | 176.6 | 0.584 | 12.74 | 103.2 |  | 32
LV15 | 15 | 7500 | 90 | 77 | 125 | 176.4 | 0.76 | 16.56 | 134.1 |  | 32
LV18 | 17.5 | 4375 | 65 | 57 | 75 | 182.3 | 0.631 | 24.36 | 115.1 |  | 33
LV18 | 17.5 | 4375 | 70 | 57 | 75 | 182.9 | 0.748 | 28.95 | 136.8 |  | 33
LV18 | 17.5 | 4375 | 75 | 57 | 75 | 183.4 | 0.864 | 33.54 | 158.5 |  | 33
LV18 | 17.5 | 4375 | 80 | 57 | 75 | 183.8 | 0.971 | 37.78 | 178.5 |  | 33
LV18 | 17.5 | 4375 | 85 | 57 | 75 | 193.6 | 0.971 | 39.79 | 188 |  | 33
LV18 | 17.5 | 4375 | 90 | 57 | 75 | 202.9 | 0.971 | 41.71 | 197.1 |  | 33
LV18 | 17.5 | 4375 | 65 | 62 | 75 | 199.2 | 0.476 | 20.06 | 94.8 |  | 33
LV18 | 17.5 | 4375 | 70 | 62 | 75 | 199.7 | 0.583 | 24.63 | 116.4 |  | 33
LV18 | 17.5 | 4375 | 75 | 62 | 75 | 200.2 | 0.689 | 29.21 | 138 |  | 33
LV18 | 17.5 | 4375 | 80 | 62 | 75 | 200.6 | 0.787 | 33.4 | 157.8 |  | 33
LV18 | 17.5 | 4375 | 85 | 62 | 75 | 200.9 | 0.893 | 37.99 | 179.5 |  | 33
LV18 | 17.5 | 4375 | 90 | 62 | 75 | 203 | 0.971 | 41.74 | 197.2 |  | 33
LV18 | 17.5 | 4375 | 70 | 67 | 75 | 216.9 | 0.437 | 20.06 | 94.8 |  | 33
LV18 | 17.5 | 4375 | 75 | 67 | 75 | 217.4 | 0.534 | 24.57 | 116.1 |  | 33
LV18 | 17.5 | 4375 | 80 | 67 | 75 | 217.9 | 0.631 | 29.1 | 137.5 |  | 33
LV18 | 17.5 | 4375 | 85 | 67 | 75 | 218.3 | 0.728 | 33.65 | 159 |  | 33
LV18 | 17.5 | 4375 | 90 | 67 | 75 | 218.3 | 0.825 | 38.14 | 180.2 |  | 33
LV18 | 17.5 | 4375 | 75 | 72 | 75 | 235.9 | 0.398 | 19.87 | 93.9 |  | 33
LV18 | 17.5 | 4375 | 80 | 72 | 75 | 236.3 | 0.486 | 24.3 | 114.8 |  | 33
LV18 | 17.5 | 4375 | 85 | 72 | 75 | 236.4 | 0.573 | 28.68 | 135.5 |  | 33
LV18 | 17.5 | 4375 | 90 | 72 | 75 | 236.4 | 0.67 | 33.52 | 158.4 |  | 33
LV18 | 17.5 | 4375 | 80 | 77 | 75 | 255.6 | 0.359 | 19.43 | 91.8 |  | 33
LV18 | 17.5 | 4375 | 85 | 77 | 75 | 255.3 | 0.447 | 24.13 | 114 |  | 33
LV18 | 17.5 | 4375 | 90 | 77 | 75 | 255.2 | 0.524 | 28.32 | 133.8 |  | 33
LV18 | 17.5 | 4375 | 65 | 57 | 85 | 173.6 | 0.641 | 23.56 | 111.3 |  | 33
LV18 | 17.5 | 4375 | 70 | 57 | 85 | 174.5 | 0.758 | 27.98 | 132.2 |  | 33
LV18 | 17.5 | 4375 | 75 | 57 | 85 | 175 | 0.874 | 32.36 | 152.9 |  | 33
LV18 | 17.5 | 4375 | 80 | 57 | 85 | 176.6 | 0.971 | 36.3 | 171.5 |  | 33
LV18 | 17.5 | 4375 | 85 | 57 | 85 | 185.9 | 0.971 | 38.22 | 180.6 |  | 33
LV18 | 17.5 | 4375 | 90 | 57 | 85 | 195.3 | 0.971 | 40.13 | 189.6 |  | 33
LV18 | 17.5 | 4375 | 65 | 62 | 85 | 189.8 | 0.476 | 19.11 | 90.3 |  | 33
LV18 | 17.5 | 4375 | 70 | 62 | 85 | 190.4 | 0.583 | 23.49 | 111 |  | 33
LV18 | 17.5 | 4375 | 75 | 62 | 85 | 190.9 | 0.689 | 27.85 | 131.6 |  | 33
LV18 | 17.5 | 4375 | 80 | 62 | 85 | 191.3 | 0.806 | 32.63 | 154.2 |  | 33
LV18 | 17.5 | 4375 | 85 | 62 | 85 | 191.5 | 0.913 | 36.99 | 174.8 |  | 33
LV18 | 17.5 | 4375 | 90 | 62 | 85 | 195.3 | 0.971 | 40.13 | 189.6 |  | 33
LV18 | 17.5 | 4375 | 70 | 67 | 85 | 207.5 | 0.437 | 19.2 | 90.7 |  | 33
LV18 | 17.5 | 4375 | 75 | 67 | 85 | 207.8 | 0.534 | 23.49 | 111 |  | 33
LV18 | 17.5 | 4375 | 80 | 67 | 85 | 208.1 | 0.631 | 27.81 | 131.4 |  | 33
LV18 | 17.5 | 4375 | 85 | 67 | 85 | 208.4 | 0.738 | 32.55 | 153.8 |  | 33
LV18 | 17.5 | 4375 | 90 | 67 | 85 | 208.7 | 0.835 | 36.89 | 174.3 |  | 33
LV18 | 17.5 | 4375 | 75 | 72 | 85 | 225.2 | 0.398 | 18.98 | 89.7 |  | 33
LV18 | 17.5 | 4375 | 80 | 72 | 85 | 225.5 | 0.486 | 23.17 | 109.5 |  | 33
LV18 | 17.5 | 4375 | 85 | 72 | 85 | 225.7 | 0.583 | 27.83 | 131.5 |  | 33
LV18 | 17.5 | 4375 | 90 | 72 | 85 | 225.7 | 0.68 | 32.47 | 153.4 |  | 33
LV18 | 17.5 | 4375 | 80 | 77 | 85 | 243.9 | 0.359 | 18.54 | 87.6 |  | 33
LV18 | 17.5 | 4375 | 85 | 77 | 85 | 244 | 0.447 | 23.07 | 109 |  | 33
LV18 | 17.5 | 4375 | 90 | 77 | 85 | 243.7 | 0.534 | 27.56 | 130.2 |  | 33
LV18 | 17.5 | 4375 | 65 | 57 | 95 | 164.5 | 0.641 | 22.31 | 105.4 |  | 34
LV18 | 17.5 | 4375 | 70 | 57 | 95 | 165.3 | 0.767 | 26.84 | 126.8 |  | 34
LV18 | 17.5 | 4375 | 75 | 57 | 95 | 165.8 | 0.893 | 31.34 | 148.1 |  | 34
LV18 | 17.5 | 4375 | 80 | 57 | 95 | 168.7 | 0.971 | 34.67 | 163.8 |  | 34
LV18 | 17.5 | 4375 | 85 | 57 | 95 | 177.9 | 0.971 | 36.57 | 172.8 |  | 34
LV18 | 17.5 | 4375 | 90 | 57 | 95 | 186.8 | 0.971 | 38.39 | 181.4 |  | 34
LV18 | 17.5 | 4375 | 65 | 62 | 95 | 180.1 | 0.476 | 18.14 | 85.7 |  | 34
LV18 | 17.5 | 4375 | 70 | 62 | 95 | 180.8 | 0.592 | 22.67 | 107.1 |  | 34
LV18 | 17.5 | 4375 | 75 | 62 | 95 | 181.2 | 0.699 | 26.81 | 126.7 |  | 34
LV18 | 17.5 | 4375 | 80 | 62 | 95 | 181.7 | 0.816 | 31.37 | 148.2 |  | 34
LV18 | 17.5 | 4375 | 85 | 62 | 95 | 181.3 | 0.932 | 35.77 | 169 |  | 34
LV18 | 17.5 | 4375 | 90 | 62 | 95 | 187 | 0.971 | 38.43 | 181.6 |  | 34
LV18 | 17.5 | 4375 | 70 | 67 | 95 | 196.9 | 0.437 | 18.22 | 86.1 |  | 34
LV18 | 17.5 | 4375 | 75 | 67 | 95 | 197.2 | 0.544 | 22.71 | 107.3 |  | 34
LV18 | 17.5 | 4375 | 80 | 67 | 95 | 197.5 | 0.641 | 26.79 | 126.6 |  | 34
LV18 | 17.5 | 4375 | 85 | 67 | 95 | 197.8 | 0.748 | 31.3 | 147.9 |  | 34
LV18 | 17.5 | 4375 | 90 | 67 | 95 | 197.9 | 0.854 | 35.79 | 169.1 |  | 34
LV18 | 17.5 | 4375 | 75 | 72 | 95 | 214.1 | 0.398 | 18.03 | 85.2 |  | 34
LV18 | 17.5 | 4375 | 80 | 72 | 95 | 214.2 | 0.495 | 22.46 | 106.1 |  | 34
LV18 | 17.5 | 4375 | 85 | 72 | 95 | 214.2 | 0.592 | 26.86 | 126.9 |  | 34
LV18 | 17.5 | 4375 | 90 | 72 | 95 | 214.1 | 0.689 | 31.24 | 147.6 |  | 34
LV18 | 17.5 | 4375 | 80 | 77 | 95 | 231.7 | 0.359 | 17.61 | 83.2 |  | 34
LV18 | 17.5 | 4375 | 85 | 77 | 95 | 231.7 | 0.457 | 22.39 | 105.8 |  | 34
LV18 | 17.5 | 4375 | 90 | 77 | 95 | 231.4 | 0.544 | 26.65 | 125.9 |  | 34
LV18 | 17.5 | 4375 | 65 | 57 | 105 | 155 | 0.65 | 21.33 | 100.8 |  | 34
LV18 | 17.5 | 4375 | 70 | 57 | 105 | 155.5 | 0.777 | 25.57 | 120.8 |  | 34
LV18 | 17.5 | 4375 | 75 | 57 | 105 | 155.9 | 0.913 | 30.12 | 142.3 |  | 34
LV18 | 17.5 | 4375 | 80 | 57 | 105 | 160.4 | 0.971 | 32.97 | 155.8 |  | 34
LV18 | 17.5 | 4375 | 85 | 57 | 105 | 169.1 | 0.972 | 34.77 | 164.3 |  | 34
LV18 | 17.5 | 4375 | 90 | 57 | 105 | 177.9 | 0.971 | 36.55 | 172.7 |  | 34
LV18 | 17.5 | 4375 | 65 | 62 | 105 | 169.8 | 0.476 | 17.1 | 80.8 |  | 34
LV18 | 17.5 | 4375 | 70 | 62 | 105 | 170.3 | 0.592 | 21.35 | 100.9 |  | 34
LV18 | 17.5 | 4375 | 75 | 62 | 105 | 170.6 | 0.719 | 25.95 | 122.6 |  | 34
LV18 | 17.5 | 4375 | 80 | 62 | 105 | 171 | 0.836 | 30.24 | 142.9 |  | 34
LV18 | 17.5 | 4375 | 85 | 62 | 105 | 170.3 | 0.952 | 34.31 | 162.1 |  | 34
LV18 | 17.5 | 4375 | 90 | 62 | 105 | 177.9 | 0.971 | 36.57 | 172.8 |  | 34
LV18 | 17.5 | 4375 | 70 | 67 | 105 | 185.6 | 0.437 | 17.16 | 81.1 |  | 34
LV18 | 17.5 | 4375 | 75 | 67 | 105 | 186 | 0.544 | 21.42 | 101.2 |  | 34
LV18 | 17.5 | 4375 | 80 | 67 | 105 | 186.2 | 0.651 | 25.65 | 121.2 |  | 34
LV18 | 17.5 | 4375 | 85 | 67 | 105 | 185.9 | 0.768 | 30.2 | 142.7 |  | 34
LV18 | 17.5 | 4375 | 90 | 67 | 105 | 186.3 | 0.874 | 34.46 | 162.8 |  | 34
LV18 | 17.5 | 4375 | 75 | 72 | 105 | 202.1 | 0.398 | 17.04 | 80.5 |  | 34
LV18 | 17.5 | 4375 | 80 | 72 | 105 | 202.1 | 0.495 | 21.19 | 100.1 |  | 34
LV18 | 17.5 | 4375 | 85 | 72 | 105 | 201.9 | 0.602 | 25.74 | 121.6 |  | 34
LV18 | 17.5 | 4375 | 90 | 72 | 105 | 201.7 | 0.709 | 30.26 | 143 |  | 34
LV18 | 17.5 | 4375 | 80 | 77 | 105 | 218.7 | 0.359 | 16.63 | 78.6 |  | 34
LV18 | 17.5 | 4375 | 85 | 77 | 105 | 218.6 | 0.457 | 21.12 | 99.8 |  | 34
LV18 | 17.5 | 4375 | 90 | 77 | 105 | 218.3 | 0.553 | 25.57 | 120.8 |  | 34
LV18 | 17.5 | 4375 | 65 | 57 | 115 | 144.9 | 0.66 | 20.25 | 95.7 |  | 35
LV18 | 17.5 | 4375 | 70 | 57 | 115 | 145.4 | 0.796 | 24.51 | 115.8 |  | 35
LV18 | 17.5 | 4375 | 75 | 57 | 115 | 145.3 | 0.933 | 28.68 | 135.5 |  | 35
LV18 | 17.5 | 4375 | 80 | 57 | 115 | 151.4 | 0.971 | 31.11 | 147 |  | 35
LV18 | 17.5 | 4375 | 85 | 57 | 115 | 159.9 | 0.971 | 32.85 | 155.2 |  | 35
LV18 | 17.5 | 4375 | 90 | 57 | 115 | 168.2 | 0.971 | 34.56 | 163.3 |  | 35
LV18 | 17.5 | 4375 | 65 | 62 | 115 | 158.8 | 0.475 | 15.98 | 75.5 |  | 35
LV18 | 17.5 | 4375 | 70 | 62 | 115 | 159.2 | 0.602 | 20.3 | 95.9 |  | 35
LV18 | 17.5 | 4375 | 75 | 62 | 115 | 159.6 | 0.728 | 24.59 | 116.2 |  | 35
LV18 | 17.5 | 4375 | 80 | 62 | 115 | 160.1 | 0.854 | 28.95 | 136.8 |  | 35
LV18 | 17.5 | 4375 | 85 | 62 | 115 | 159.9 | 0.971 | 32.87 | 155.3 |  | 35
LV18 | 17.5 | 4375 | 90 | 62 | 115 | 168.3 | 0.971 | 34.58 | 163.4 |  | 35
LV18 | 17.5 | 4375 | 70 | 67 | 115 | 173.7 | 0.437 | 16.06 | 75.9 |  | 35
LV18 | 17.5 | 4375 | 75 | 67 | 115 | 174.1 | 0.554 | 20.4 | 96.4 |  | 35
LV18 | 17.5 | 4375 | 80 | 67 | 115 | 174.2 | 0.67 | 24.7 | 116.7 |  | 35
LV18 | 17.5 | 4375 | 85 | 67 | 115 | 174.2 | 0.786 | 28.99 | 137 |  | 35
LV18 | 17.5 | 4375 | 90 | 67 | 115 | 173.8 | 0.903 | 33.23 | 157 |  | 35
LV18 | 17.5 | 4375 | 75 | 72 | 115 | 189.2 | 0.398 | 15.94 | 75.3 |  | 35
LV18 | 17.5 | 4375 | 80 | 72 | 115 | 189 | 0.505 | 20.21 | 95.5 |  | 35
LV18 | 17.5 | 4375 | 85 | 72 | 115 | 188.8 | 0.612 | 24.44 | 115.5 |  | 35
LV18 | 17.5 | 4375 | 90 | 72 | 115 | 188.7 | 0.719 | 28.7 | 135.6 |  | 35
LV18 | 17.5 | 4375 | 80 | 77 | 115 | 205 | 0.369 | 16.02 | 75.7 |  | 35
LV18 | 17.5 | 4375 | 85 | 77 | 115 | 204.7 | 0.466 | 20.19 | 95.4 |  | 35
LV18 | 17.5 | 4375 | 90 | 77 | 115 | 204.2 | 0.563 | 24.34 | 115 |  | 35
LV18 | 17.5 | 4375 | 65 | 57 | 125 | 133.9 | 0.671 | 19.01 | 89.8 |  | 35
LV18 | 17.5 | 4375 | 70 | 57 | 125 | 134.5 | 0.816 | 23.22 | 109.7 |  | 35
LV18 | 17.5 | 4375 | 75 | 57 | 125 | 134.1 | 0.961 | 27.28 | 128.9 |  | 35
LV18 | 17.5 | 4375 | 80 | 57 | 125 | 141.7 | 0.972 | 29.14 | 137.7 |  | 35
LV18 | 17.5 | 4375 | 85 | 57 | 125 | 149.9 | 0.971 | 30.81 | 145.6 |  | 35
LV18 | 17.5 | 4375 | 90 | 57 | 125 | 158.1 | 0.971 | 32.49 | 153.5 |  | 35
LV18 | 17.5 | 4375 | 65 | 62 | 125 | 147.1 | 0.476 | 14.81 | 70 |  | 35
LV18 | 17.5 | 4375 | 70 | 62 | 125 | 147.6 | 0.612 | 19.11 | 90.3 |  | 35
LV18 | 17.5 | 4375 | 75 | 62 | 125 | 147.9 | 0.748 | 23.41 | 110.6 |  | 35
LV18 | 17.5 | 4375 | 80 | 62 | 125 | 147.9 | 0.884 | 27.66 | 130.7 |  | 35
LV18 | 17.5 | 4375 | 85 | 62 | 125 | 149.9 | 0.971 | 30.81 | 145.6 |  | 35
LV18 | 17.5 | 4375 | 90 | 62 | 125 | 158 | 0.971 | 32.47 | 153.4 |  | 35
LV18 | 17.5 | 4375 | 70 | 67 | 125 | 161.2 | 0.437 | 14.9 | 70.4 |  | 35
LV18 | 17.5 | 4375 | 75 | 67 | 125 | 161.4 | 0.563 | 19.24 | 90.9 |  | 35
LV18 | 17.5 | 4375 | 80 | 67 | 125 | 161.4 | 0.68 | 23.22 | 109.7 |  | 35
LV18 | 17.5 | 4375 | 85 | 67 | 125 | 161.3 | 0.806 | 27.51 | 130 |  | 35
LV18 | 17.5 | 4375 | 90 | 67 | 125 | 160.3 | 0.942 | 31.96 | 151 |  | 35
LV18 | 17.5 | 4375 | 75 | 72 | 125 | 175.5 | 0.398 | 14.79 | 69.9 |  | 35
LV18 | 17.5 | 4375 | 80 | 72 | 125 | 175.4 | 0.515 | 19.11 | 90.3 |  | 35
LV18 | 17.5 | 4375 | 85 | 72 | 125 | 175.1 | 0.631 | 23.39 | 110.5 |  | 35
LV18 | 17.5 | 4375 | 90 | 72 | 125 | 174.9 | 0.748 | 27.68 | 130.8 |  | 35
LV18 | 17.5 | 4375 | 80 | 77 | 125 | 190.6 | 0.369 | 14.88 | 70.3 |  | 35
LV18 | 17.5 | 4375 | 85 | 77 | 125 | 190 | 0.476 | 19.13 | 90.4 |  | 35
LV18 | 17.5 | 4375 | 90 | 77 | 125 | 189.4 | 0.583 | 23.37 | 110.4 |  | 35
LV18 | 17.5 | 5250 | 65 | 57 | 75 | 190.9 | 0.651 | 21.9 | 124.2 |  | 33
LV18 | 17.5 | 5250 | 70 | 57 | 75 | 191.6 | 0.777 | 26.26 | 148.9 |  | 33
LV18 | 17.5 | 5250 | 75 | 57 | 75 | 192.3 | 0.903 | 30.62 | 173.6 |  | 33
LV18 | 17.5 | 5250 | 80 | 57 | 75 | 197.1 | 0.971 | 33.76 | 191.4 |  | 33
LV18 | 17.5 | 5250 | 85 | 57 | 75 | 207.4 | 0.971 | 35.52 | 201.4 |  | 33
LV18 | 17.5 | 5250 | 90 | 57 | 75 | 217.7 | 0.971 | 37.28 | 211.4 |  | 33
LV18 | 17.5 | 5250 | 65 | 62 | 75 | 207.9 | 0.476 | 17.44 | 98.9 |  | 33
LV18 | 17.5 | 5250 | 70 | 62 | 75 | 208.6 | 0.593 | 21.8 | 123.6 |  | 33
LV18 | 17.5 | 5250 | 75 | 62 | 75 | 209.1 | 0.718 | 26.49 | 150.2 |  | 33
LV18 | 17.5 | 5250 | 80 | 62 | 75 | 209.7 | 0.835 | 30.88 | 175.1 |  | 33
LV18 | 17.5 | 5250 | 85 | 62 | 75 | 209 | 0.952 | 35.1 | 199 |  | 33
LV18 | 17.5 | 5250 | 90 | 62 | 75 | 217.8 | 0.971 | 37.3 | 211.5 |  | 33
LV18 | 17.5 | 5250 | 70 | 67 | 75 | 226.5 | 0.437 | 17.46 | 99 |  | 33
LV18 | 17.5 | 5250 | 75 | 67 | 75 | 227 | 0.544 | 21.76 | 123.4 |  | 33
LV18 | 17.5 | 5250 | 80 | 67 | 75 | 227.3 | 0.651 | 26.08 | 147.9 |  | 33
LV18 | 17.5 | 5250 | 85 | 67 | 75 | 227.5 | 0.767 | 30.78 | 174.5 |  | 33
LV18 | 17.5 | 5250 | 90 | 67 | 75 | 227.4 | 0.874 | 35.06 | 198.8 |  | 33
LV18 | 17.5 | 5250 | 75 | 72 | 75 | 245.6 | 0.398 | 17.25 | 97.8 |  | 33
LV18 | 17.5 | 5250 | 80 | 72 | 75 | 246 | 0.495 | 21.48 | 121.8 |  | 33
LV18 | 17.5 | 5250 | 85 | 72 | 75 | 246 | 0.602 | 26.12 | 148.1 |  | 33
LV18 | 17.5 | 5250 | 90 | 72 | 75 | 245.9 | 0.709 | 30.76 | 174.4 |  | 33
LV18 | 17.5 | 5250 | 80 | 77 | 75 | 265.8 | 0.359 | 16.84 | 95.5 |  | 33
LV18 | 17.5 | 5250 | 85 | 77 | 75 | 265.3 | 0.456 | 21.36 | 121.1 |  | 33
LV18 | 17.5 | 5250 | 90 | 77 | 75 | 265.3 | 0.553 | 25.89 | 146.8 |  | 33
LV18 | 17.5 | 5250 | 65 | 57 | 85 | 181.4 | 0.65 | 20.81 | 118 |  | 33
LV18 | 17.5 | 5250 | 70 | 57 | 85 | 182.1 | 0.787 | 25.27 | 143.3 |  | 33
LV18 | 17.5 | 5250 | 75 | 57 | 85 | 182.4 | 0.923 | 29.68 | 168.3 |  | 33
LV18 | 17.5 | 5250 | 80 | 57 | 85 | 188.7 | 0.971 | 32.31 | 183.2 |  | 33
LV18 | 17.5 | 5250 | 85 | 57 | 85 | 199 | 0.971 | 34.09 | 193.3 |  | 33
LV18 | 17.5 | 5250 | 90 | 57 | 85 | 209 | 0.971 | 35.8 | 203 |  | 33
LV18 | 17.5 | 5250 | 65 | 62 | 85 | 197.7 | 0.476 | 16.6 | 94.1 |  | 33
LV18 | 17.5 | 5250 | 70 | 62 | 85 | 198.3 | 0.602 | 21.06 | 119.4 |  | 33
LV18 | 17.5 | 5250 | 75 | 62 | 85 | 198.9 | 0.729 | 25.56 | 144.9 |  | 33
LV18 | 17.5 | 5250 | 80 | 62 | 85 | 199.6 | 0.845 | 29.74 | 168.6 |  | 33
LV18 | 17.5 | 5250 | 85 | 62 | 85 | 199.1 | 0.971 | 34.11 | 193.4 |  | 33
LV18 | 17.5 | 5250 | 90 | 62 | 85 | 209 | 0.971 | 35.8 | 203 |  | 33
LV18 | 17.5 | 5250 | 70 | 67 | 85 | 215.9 | 0.437 | 16.65 | 94.4 |  | 33
LV18 | 17.5 | 5250 | 75 | 67 | 85 | 216.7 | 0.554 | 21.16 | 120 |  | 33
LV18 | 17.5 | 5250 | 80 | 67 | 85 | 216.3 | 0.661 | 25.2 | 142.9 |  | 33
LV18 | 17.5 | 5250 | 85 | 67 | 85 | 216.5 | 0.777 | 29.66 | 168.2 |  | 33
LV18 | 17.5 | 5250 | 90 | 67 | 85 | 216.6 | 0.893 | 34.13 | 193.5 |  | 33
LV18 | 17.5 | 5250 | 75 | 72 | 85 | 234.3 | 0.398 | 16.46 | 93.3 |  | 33
LV18 | 17.5 | 5250 | 80 | 72 | 85 | 234.3 | 0.505 | 20.86 | 118.3 |  | 33
LV18 | 17.5 | 5250 | 85 | 72 | 85 | 234.4 | 0.612 | 25.29 | 143.4 |  | 33
LV18 | 17.5 | 5250 | 90 | 72 | 85 | 234.4 | 0.719 | 29.72 | 168.5 |  | 33
LV18 | 17.5 | 5250 | 80 | 77 | 85 | 252.9 | 0.369 | 16.46 | 93.3 |  | 33
LV18 | 17.5 | 5250 | 85 | 77 | 85 | 252.9 | 0.466 | 20.79 | 117.9 |  | 33
LV18 | 17.5 | 5250 | 90 | 77 | 85 | 252.6 | 0.563 | 25.1 | 142.3 |  | 33
LV18 | 17.5 | 5250 | 65 | 57 | 95 | 171.2 | 0.661 | 19.95 | 113.1 |  | 34
LV18 | 17.5 | 5250 | 70 | 57 | 95 | 171.9 | 0.796 | 24.14 | 136.9 |  | 34
LV18 | 17.5 | 5250 | 75 | 57 | 95 | 171.9 | 0.942 | 28.55 | 161.9 |  | 34
LV18 | 17.5 | 5250 | 80 | 57 | 95 | 180.1 | 0.971 | 30.85 | 174.9 |  | 34
LV18 | 17.5 | 5250 | 85 | 57 | 95 | 189.8 | 0.971 | 32.5 | 184.3 |  | 34
LV18 | 17.5 | 5250 | 90 | 57 | 95 | 199.5 | 0.971 | 34.16 | 193.7 |  | 34
LV18 | 17.5 | 5250 | 65 | 62 | 95 | 187.2 | 0.476 | 15.71 | 89.1 |  | 34
LV18 | 17.5 | 5250 | 70 | 62 | 95 | 187.8 | 0.602 | 19.95 | 113.1 |  | 34
LV18 | 17.5 | 5250 | 75 | 62 | 95 | 188.3 | 0.738 | 24.51 | 139 |  | 34
LV18 | 17.5 | 5250 | 80 | 62 | 95 | 188.6 | 0.864 | 28.75 | 163 |  | 34
LV18 | 17.5 | 5250 | 85 | 62 | 95 | 189.8 | 0.972 | 32.52 | 184.4 |  | 34
LV18 | 17.5 | 5250 | 90 | 62 | 95 | 199.6 | 0.971 | 34.2 | 193.9 |  | 34
LV18 | 17.5 | 5250 | 70 | 67 | 95 | 204.3 | 0.437 | 15.75 | 89.3 |  | 34
LV18 | 17.5 | 5250 | 75 | 67 | 95 | 204.6 | 0.553 | 19.96 | 113.2 |  | 34
LV18 | 17.5 | 5250 | 80 | 67 | 95 | 204.7 | 0.68 | 24.55 | 139.2 |  | 34
LV18 | 17.5 | 5250 | 85 | 67 | 95 | 204.7 | 0.797 | 28.77 | 163.1 |  | 34
LV18 | 17.5 | 5250 | 90 | 67 | 95 | 204.3 | 0.923 | 33.25 | 188.5 |  | 34
LV18 | 17.5 | 5250 | 75 | 72 | 95 | 221.7 | 0.398 | 15.57 | 88.3 |  | 34
LV18 | 17.5 | 5250 | 80 | 72 | 95 | 221.9 | 0.505 | 19.77 | 112.1 |  | 34
LV18 | 17.5 | 5250 | 85 | 72 | 95 | 221.9 | 0.621 | 24.32 | 137.9 |  | 34
LV18 | 17.5 | 5250 | 90 | 72 | 95 | 221.9 | 0.728 | 28.5 | 161.6 |  | 34
LV18 | 17.5 | 5250 | 80 | 77 | 95 | 239.7 | 0.369 | 15.61 | 88.5 |  | 34
LV18 | 17.5 | 5250 | 85 | 77 | 95 | 239.5 | 0.466 | 19.68 | 111.6 |  | 34
LV18 | 17.5 | 5250 | 90 | 77 | 95 | 239.2 | 0.573 | 24.18 | 137.1 |  | 34
LV18 | 17.5 | 5250 | 65 | 57 | 105 | 160.6 | 0.67 | 18.98 | 107.6 |  | 34
LV18 | 17.5 | 5250 | 70 | 57 | 105 | 161.5 | 0.815 | 23.23 | 131.7 |  | 34
LV18 | 17.5 | 5250 | 75 | 57 | 105 | 161.4 | 0.971 | 27.64 | 156.7 |  | 34
LV18 | 17.5 | 5250 | 80 | 57 | 105 | 170.5 | 0.971 | 29.21 | 165.6 |  | 34
LV18 | 17.5 | 5250 | 85 | 57 | 105 | 180 | 0.971 | 30.83 | 174.8 |  | 34
LV18 | 17.5 | 5250 | 90 | 57 | 105 | 189.5 | 0.971 | 32.45 | 184 |  | 34
LV18 | 17.5 | 5250 | 65 | 62 | 105 | 175.6 | 0.476 | 14.74 | 83.6 |  | 34
LV18 | 17.5 | 5250 | 70 | 62 | 105 | 176.3 | 0.611 | 19.01 | 107.8 |  | 34
LV18 | 17.5 | 5250 | 75 | 62 | 105 | 176.7 | 0.748 | 23.32 | 132.2 |  | 34
LV18 | 17.5 | 5250 | 80 | 62 | 105 | 176.8 | 0.883 | 27.55 | 156.2 |  | 34
LV18 | 17.5 | 5250 | 85 | 62 | 105 | 180 | 0.971 | 30.83 | 174.8 |  | 34
LV18 | 17.5 | 5250 | 90 | 62 | 105 | 189.4 | 0.971 | 32.43 | 183.9 |  | 34
LV18 | 17.5 | 5250 | 70 | 67 | 105 | 192 | 0.437 | 14.8 | 83.9 |  | 34
LV18 | 17.5 | 5250 | 75 | 67 | 105 | 192.2 | 0.563 | 19.1 | 108.3 |  | 34
LV18 | 17.5 | 5250 | 80 | 67 | 105 | 192.1 | 0.69 | 23.37 | 132.5 |  | 34
LV18 | 17.5 | 5250 | 85 | 67 | 105 | 192.3 | 0.816 | 27.67 | 156.9 |  | 34
LV18 | 17.5 | 5250 | 90 | 67 | 105 | 191.5 | 0.952 | 32.15 | 182.3 |  | 34
LV18 | 17.5 | 5250 | 75 | 72 | 105 | 208.7 | 0.398 | 14.66 | 83.1 |  | 34
LV18 | 17.5 | 5250 | 80 | 72 | 105 | 208.6 | 0.515 | 18.94 | 107.4 |  | 34
LV18 | 17.5 | 5250 | 85 | 72 | 105 | 208.6 | 0.631 | 23.23 | 131.7 |  | 34
LV18 | 17.5 | 5250 | 90 | 72 | 105 | 208.5 | 0.748 | 27.5 | 155.9 |  | 34
LV18 | 17.5 | 5250 | 80 | 77 | 105 | 225.8 | 0.369 | 14.69 | 83.3 |  | 34
LV18 | 17.5 | 5250 | 85 | 77 | 105 | 225.3 | 0.476 | 18.91 | 107.2 |  | 34
LV18 | 17.5 | 5250 | 90 | 77 | 105 | 224.9 | 0.583 | 23.12 | 131.1 |  | 34
LV18 | 17.5 | 5250 | 65 | 57 | 115 | 149.6 | 0.68 | 17.94 | 101.7 |  | 35
LV18 | 17.5 | 5250 | 70 | 57 | 115 | 150.1 | 0.835 | 22.12 | 125.4 |  | 35
LV18 | 17.5 | 5250 | 75 | 57 | 115 | 151.2 | 0.971 | 25.89 | 146.8 |  | 35
LV18 | 17.5 | 5250 | 80 | 57 | 115 | 160.3 | 0.971 | 27.46 | 155.7 |  | 35
LV18 | 17.5 | 5250 | 85 | 57 | 115 | 169.5 | 0.971 | 29.03 | 164.6 |  | 35
LV18 | 17.5 | 5250 | 90 | 57 | 115 | 178.6 | 0.971 | 30.58 | 173.4 |  | 35
LV18 | 17.5 | 5250 | 65 | 62 | 115 | 163.6 | 0.485 | 14 | 79.4 |  | 35
LV18 | 17.5 | 5250 | 70 | 62 | 115 | 164.2 | 0.621 | 17.99 | 102 |  | 35
LV18 | 17.5 | 5250 | 75 | 62 | 115 | 164.5 | 0.767 | 22.26 | 126.2 |  | 35
LV18 | 17.5 | 5250 | 80 | 62 | 115 | 164.3 | 0.913 | 26.46 | 150 |  | 35
LV18 | 17.5 | 5250 | 85 | 62 | 115 | 169.5 | 0.971 | 29.03 | 164.6 |  | 35
LV18 | 17.5 | 5250 | 90 | 62 | 115 | 178.6 | 0.971 | 30.58 | 173.4 |  | 35
LV18 | 17.5 | 5250 | 70 | 67 | 115 | 179.1 | 0.437 | 13.81 | 78.3 |  | 35
LV18 | 17.5 | 5250 | 75 | 67 | 115 | 179.2 | 0.573 | 18.11 | 102.7 |  | 35
LV18 | 17.5 | 5250 | 80 | 67 | 115 | 179.1 | 0.709 | 22.4 | 127 |  | 35
LV18 | 17.5 | 5250 | 85 | 67 | 115 | 179.1 | 0.845 | 26.68 | 151.3 |  | 35
LV18 | 17.5 | 5250 | 90 | 67 | 115 | 178.4 | 0.971 | 30.55 | 173.2 |  | 35
LV18 | 17.5 | 5250 | 75 | 72 | 115 | 195 | 0.398 | 13.7 | 77.7 |  | 35
LV18 | 17.5 | 5250 | 80 | 72 | 115 | 194.8 | 0.525 | 18.02 | 102.2 |  | 35
LV18 | 17.5 | 5250 | 85 | 72 | 115 | 194.6 | 0.651 | 22.33 | 126.6 |  | 35
LV18 | 17.5 | 5250 | 90 | 72 | 115 | 194.4 | 0.777 | 26.63 | 151 |  | 35
LV18 | 17.5 | 5250 | 80 | 77 | 115 | 210.9 | 0.369 | 13.72 | 77.8 |  | 35
LV18 | 17.5 | 5250 | 85 | 77 | 115 | 210.2 | 0.486 | 18.01 | 102.1 |  | 35
LV18 | 17.5 | 5250 | 90 | 77 | 115 | 210.1 | 0.602 | 22.31 | 126.5 |  | 35
LV18 | 17.5 | 5250 | 65 | 57 | 125 | 137.8 | 0.689 | 16.75 | 95 |  | 35
LV18 | 17.5 | 5250 | 70 | 57 | 125 | 138.2 | 0.855 | 20.83 | 118.1 |  | 35
LV18 | 17.5 | 5250 | 75 | 57 | 125 | 140.8 | 0.971 | 24.11 | 136.7 |  | 35
LV18 | 17.5 | 5250 | 80 | 57 | 125 | 149.6 | 0.971 | 25.63 | 145.3 |  | 35
LV18 | 17.5 | 5250 | 85 | 57 | 125 | 158.4 | 0.971 | 27.13 | 153.8 |  | 35
LV18 | 17.5 | 5250 | 90 | 57 | 125 | 166.7 | 0.971 | 28.55 | 161.9 |  | 35
LV18 | 17.5 | 5250 | 65 | 62 | 125 | 151.1 | 0.486 | 12.95 | 73.4 |  | 35
LV18 | 17.5 | 5250 | 70 | 62 | 125 | 151.5 | 0.632 | 16.88 | 95.7 |  | 35
LV18 | 17.5 | 5250 | 75 | 62 | 125 | 151.7 | 0.787 | 21.06 | 119.4 |  | 35
LV18 | 17.5 | 5250 | 80 | 62 | 125 | 151 | 0.952 | 25.34 | 143.7 |  | 35
LV18 | 17.5 | 5250 | 85 | 62 | 125 | 158.4 | 0.971 | 27.13 | 153.8 |  | 35
LV18 | 17.5 | 5250 | 90 | 62 | 125 | 167 | 0.971 | 28.61 | 162.2 |  | 35
LV18 | 17.5 | 5250 | 70 | 67 | 125 | 165.5 | 0.447 | 13.03 | 73.9 |  | 35
LV18 | 17.5 | 5250 | 75 | 67 | 125 | 165.3 | 0.583 | 16.98 | 96.3 |  | 35
LV18 | 17.5 | 5250 | 80 | 67 | 125 | 165.4 | 0.728 | 21.23 | 120.4 |  | 35
LV18 | 17.5 | 5250 | 85 | 67 | 125 | 165.2 | 0.874 | 25.47 | 144.4 |  | 35
LV18 | 17.5 | 5250 | 90 | 67 | 125 | 167.1 | 0.971 | 28.61 | 162.2 |  | 35
LV18 | 17.5 | 5250 | 75 | 72 | 125 | 180.4 | 0.408 | 12.98 | 73.6 |  | 35
LV18 | 17.5 | 5250 | 80 | 72 | 125 | 180.3 | 0.534 | 16.98 | 96.3 |  | 35
LV18 | 17.5 | 5250 | 85 | 72 | 125 | 179.8 | 0.67 | 21.25 | 120.5 |  | 35
LV18 | 17.5 | 5250 | 90 | 72 | 125 | 179.5 | 0.806 | 25.52 | 144.7 |  | 35
LV18 | 17.5 | 5250 | 80 | 77 | 125 | 196.5 | 0.369 | 12.79 | 72.5 |  | 35
LV18 | 17.5 | 5250 | 85 | 77 | 125 | 194.6 | 0.495 | 17 | 96.4 |  | 35
LV18 | 17.5 | 5250 | 90 | 77 | 125 | 193.9 | 0.621 | 21.25 | 120.5 |  | 35
LV18 | 17.5 | 6125 | 65 | 57 | 75 | 197.3 | 0.67 | 19.98 | 132.2 |  | 33
LV18 | 17.5 | 6125 | 70 | 57 | 75 | 198.2 | 0.806 | 24.16 | 159.8 |  | 33
LV18 | 17.5 | 6125 | 75 | 57 | 75 | 197.9 | 0.952 | 28.48 | 188.4 |  | 33
LV18 | 17.5 | 6125 | 80 | 57 | 75 | 207.8 | 0.971 | 30.51 | 201.8 |  | 33
LV18 | 17.5 | 6125 | 85 | 57 | 75 | 218.9 | 0.971 | 32.14 | 212.6 |  | 33
LV18 | 17.5 | 6125 | 90 | 57 | 75 | 229.8 | 0.971 | 33.74 | 223.2 |  | 33
LV18 | 17.5 | 6125 | 65 | 62 | 75 | 214.4 | 0.476 | 15.42 | 102 |  | 33
LV18 | 17.5 | 6125 | 70 | 62 | 75 | 215.2 | 0.612 | 19.91 | 131.7 |  | 33
LV18 | 17.5 | 6125 | 75 | 62 | 75 | 215.7 | 0.748 | 24.38 | 161.3 |  | 33
LV18 | 17.5 | 6125 | 80 | 62 | 75 | 215.9 | 0.874 | 28.53 | 188.7 |  | 33
LV18 | 17.5 | 6125 | 85 | 62 | 75 | 218.9 | 0.971 | 32.14 | 212.6 |  | 33
LV18 | 17.5 | 6125 | 90 | 62 | 75 | 230 | 0.971 | 33.77 | 223.4 |  | 33
LV18 | 17.5 | 6125 | 70 | 67 | 75 | 233.6 | 0.437 | 15.43 | 102.1 |  | 33
LV18 | 17.5 | 6125 | 75 | 67 | 75 | 234 | 0.563 | 19.92 | 131.8 |  | 33
LV18 | 17.5 | 6125 | 80 | 67 | 75 | 234 | 0.68 | 24.05 | 159.1 |  | 33
LV18 | 17.5 | 6125 | 85 | 67 | 75 | 234.6 | 0.806 | 28.59 | 189.1 |  | 33
LV18 | 17.5 | 6125 | 90 | 67 | 75 | 234.1 | 0.933 | 33 | 218.3 |  | 33
LV18 | 17.5 | 6125 | 75 | 72 | 75 | 253 | 0.398 | 15.22 | 100.7 |  | 33
LV18 | 17.5 | 6125 | 80 | 72 | 75 | 253.2 | 0.515 | 19.71 | 130.4 |  | 33
LV18 | 17.5 | 6125 | 85 | 72 | 75 | 253.5 | 0.631 | 24.19 | 160 |  | 33
LV18 | 17.5 | 6125 | 90 | 72 | 75 | 253.5 | 0.748 | 28.66 | 189.6 |  | 33
LV18 | 17.5 | 6125 | 80 | 77 | 75 | 273.5 | 0.369 | 15.25 | 100.9 |  | 33
LV18 | 17.5 | 6125 | 85 | 77 | 75 | 272.9 | 0.476 | 19.62 | 129.8 |  | 33
LV18 | 17.5 | 6125 | 90 | 77 | 75 | 272.8 | 0.583 | 24.04 | 159 |  | 33
LV18 | 17.5 | 6125 | 65 | 57 | 85 | 186.8 | 0.67 | 18.93 | 125.2 |  | 33
LV18 | 17.5 | 6125 | 70 | 57 | 85 | 187.8 | 0.825 | 23.43 | 155 |  | 33
LV18 | 17.5 | 6125 | 75 | 57 | 85 | 187.7 | 0.971 | 27.56 | 182.3 |  | 33
LV18 | 17.5 | 6125 | 80 | 57 | 85 | 198.8 | 0.971 | 29.19 | 193.1 |  | 33
LV18 | 17.5 | 6125 | 85 | 57 | 85 | 209.6 | 0.971 | 30.76 | 203.5 |  | 33
LV18 | 17.5 | 6125 | 90 | 57 | 85 | 220.2 | 0.971 | 32.34 | 213.9 |  | 33
LV18 | 17.5 | 6125 | 65 | 62 | 85 | 203.5 | 0.476 | 14.63 | 96.8 |  | 33
LV18 | 17.5 | 6125 | 70 | 62 | 85 | 204.5 | 0.622 | 19.21 | 127.1 |  | 33
LV18 | 17.5 | 6125 | 75 | 62 | 85 | 204.9 | 0.757 | 23.46 | 155.2 |  | 33
LV18 | 17.5 | 6125 | 80 | 62 | 85 | 205 | 0.894 | 27.69 | 183.2 |  | 33
LV18 | 17.5 | 6125 | 85 | 62 | 85 | 209.7 | 0.971 | 30.78 | 203.6 |  | 33
LV18 | 17.5 | 6125 | 90 | 62 | 85 | 220.4 | 0.971 | 32.37 | 214.1 |  | 33
LV18 | 17.5 | 6125 | 70 | 67 | 85 | 221.9 | 0.437 | 14.66 | 97 |  | 33
LV18 | 17.5 | 6125 | 75 | 67 | 85 | 222.4 | 0.563 | 18.94 | 125.3 |  | 33
LV18 | 17.5 | 6125 | 80 | 67 | 85 | 222.6 | 0.699 | 23.54 | 155.7 |  | 33
LV18 | 17.5 | 6125 | 85 | 67 | 85 | 222.8 | 0.825 | 27.8 | 183.9 |  | 33
LV18 | 17.5 | 6125 | 90 | 67 | 85 | 221.6 | 0.952 | 31.88 | 210.9 |  | 33
LV18 | 17.5 | 6125 | 75 | 72 | 85 | 240.8 | 0.398 | 14.5 | 95.9 |  | 33
LV18 | 17.5 | 6125 | 80 | 72 | 85 | 240.8 | 0.515 | 18.73 | 123.9 |  | 33
LV18 | 17.5 | 6125 | 85 | 72 | 85 | 240.9 | 0.641 | 23.34 | 154.4 |  | 33
LV18 | 17.5 | 6125 | 90 | 72 | 85 | 240.9 | 0.758 | 27.59 | 182.5 |  | 33
LV18 | 17.5 | 6125 | 80 | 77 | 85 | 259.7 | 0.369 | 14.48 | 95.8 |  | 33
LV18 | 17.5 | 6125 | 85 | 77 | 85 | 259.5 | 0.476 | 18.67 | 123.5 |  | 33
LV18 | 17.5 | 6125 | 90 | 77 | 85 | 259.4 | 0.593 | 23.24 | 153.7 |  | 33
LV18 | 17.5 | 6125 | 65 | 57 | 95 | 176 | 0.68 | 18.1 | 119.7 |  | 34
LV18 | 17.5 | 6125 | 70 | 57 | 95 | 176.8 | 0.835 | 22.33 | 147.7 |  | 34
LV18 | 17.5 | 6125 | 75 | 57 | 95 | 178.2 | 0.971 | 26.17 | 173.1 |  | 34
LV18 | 17.5 | 6125 | 80 | 57 | 95 | 188.9 | 0.971 | 27.74 | 183.5 |  | 34
LV18 | 17.5 | 6125 | 85 | 57 | 95 | 199.5 | 0.971 | 29.28 | 193.7 |  | 34
LV18 | 17.5 | 6125 | 90 | 57 | 95 | 209.8 | 0.971 | 30.79 | 203.7 |  | 34
LV18 | 17.5 | 6125 | 65 | 62 | 95 | 192.1 | 0.486 | 14.1 | 93.3 |  | 34
LV18 | 17.5 | 6125 | 70 | 62 | 95 | 192.8 | 0.621 | 18.11 | 119.8 |  | 34
LV18 | 17.5 | 6125 | 75 | 62 | 95 | 193.2 | 0.767 | 22.4 | 148.2 |  | 34
LV18 | 17.5 | 6125 | 80 | 62 | 95 | 193.1 | 0.913 | 26.65 | 176.3 |  | 34
LV18 | 17.5 | 6125 | 85 | 62 | 95 | 199.5 | 0.971 | 29.28 | 193.7 |  | 34
LV18 | 17.5 | 6125 | 90 | 62 | 95 | 209.9 | 0.971 | 30.81 | 203.8 |  | 34
LV18 | 17.5 | 6125 | 70 | 67 | 95 | 209.5 | 0.437 | 13.85 | 91.6 |  | 34
LV18 | 17.5 | 6125 | 75 | 67 | 95 | 209.9 | 0.573 | 18.19 | 120.3 |  | 34
LV18 | 17.5 | 6125 | 80 | 67 | 95 | 210.2 | 0.709 | 22.52 | 149 |  | 34
LV18 | 17.5 | 6125 | 85 | 67 | 95 | 210.3 | 0.845 | 26.86 | 177.7 |  | 34
LV18 | 17.5 | 6125 | 90 | 67 | 95 | 209.9 | 0.971 | 30.82 | 203.9 |  | 34
LV18 | 17.5 | 6125 | 75 | 72 | 95 | 227.5 | 0.408 | 14.03 | 92.8 |  | 34
LV18 | 17.5 | 6125 | 80 | 72 | 95 | 227.6 | 0.524 | 18.03 | 119.3 |  | 34
LV18 | 17.5 | 6125 | 85 | 72 | 95 | 227.5 | 0.651 | 22.37 | 148 |  | 34
LV18 | 17.5 | 6125 | 90 | 72 | 95 | 227.5 | 0.777 | 26.73 | 176.8 |  | 34
LV18 | 17.5 | 6125 | 80 | 77 | 95 | 245.8 | 0.369 | 13.71 | 90.7 |  | 34
LV18 | 17.5 | 6125 | 85 | 77 | 95 | 245.4 | 0.486 | 18.02 | 119.2 |  | 34
LV18 | 17.5 | 6125 | 90 | 77 | 95 | 245 | 0.602 | 22.3 | 147.5 |  | 34
LV18 | 17.5 | 6125 | 65 | 57 | 105 | 164.6 | 0.69 | 17.16 | 113.5 |  | 34
LV18 | 17.5 | 6125 | 70 | 57 | 105 | 165.4 | 0.854 | 21.36 | 141.3 |  | 34
LV18 | 17.5 | 6125 | 75 | 57 | 105 | 168.4 | 0.971 | 24.72 | 163.5 |  | 34
LV18 | 17.5 | 6125 | 80 | 57 | 105 | 178.5 | 0.971 | 26.21 | 173.4 |  | 34
LV18 | 17.5 | 6125 | 85 | 57 | 105 | 188.7 | 0.971 | 27.69 | 183.2 |  | 34
LV18 | 17.5 | 6125 | 90 | 57 | 105 | 198.7 | 0.971 | 29.16 | 192.9 |  | 34
LV18 | 17.5 | 6125 | 65 | 62 | 105 | 179.9 | 0.485 | 13.2 | 87.3 |  | 34
LV18 | 17.5 | 6125 | 70 | 62 | 105 | 180.4 | 0.631 | 17.22 | 113.9 |  | 34
LV18 | 17.5 | 6125 | 75 | 62 | 105 | 180.7 | 0.786 | 21.48 | 142.1 |  | 34
LV18 | 17.5 | 6125 | 80 | 62 | 105 | 180.5 | 0.942 | 25.7 | 170 |  | 34
LV18 | 17.5 | 6125 | 85 | 62 | 105 | 188.6 | 0.971 | 27.69 | 183.2 |  | 34
LV18 | 17.5 | 6125 | 90 | 62 | 105 | 198.8 | 0.971 | 29.19 | 193.1 |  | 34
LV18 | 17.5 | 6125 | 70 | 67 | 105 | 196.5 | 0.447 | 13.27 | 87.8 |  | 34
LV18 | 17.5 | 6125 | 75 | 67 | 105 | 196.8 | 0.583 | 17.34 | 114.7 |  | 34
LV18 | 17.5 | 6125 | 80 | 67 | 105 | 196.9 | 0.729 | 21.69 | 143.5 |  | 34
LV18 | 17.5 | 6125 | 85 | 67 | 105 | 196.9 | 0.864 | 25.73 | 170.2 |  | 34
LV18 | 17.5 | 6125 | 90 | 67 | 105 | 198.8 | 0.971 | 29.19 | 193.1 |  | 34
LV18 | 17.5 | 6125 | 75 | 72 | 105 | 213.6 | 0.408 | 13.17 | 87.1 |  | 34
LV18 | 17.5 | 6125 | 80 | 72 | 105 | 213.4 | 0.534 | 17.23 | 114 |  | 34
LV18 | 17.5 | 6125 | 85 | 72 | 105 | 213.3 | 0.67 | 21.6 | 142.9 |  | 34
LV18 | 17.5 | 6125 | 90 | 72 | 105 | 213.1 | 0.796 | 25.65 | 169.7 |  | 34
LV18 | 17.5 | 6125 | 80 | 77 | 105 | 230.8 | 0.369 | 12.88 | 85.2 |  | 34
LV18 | 17.5 | 6125 | 85 | 77 | 105 | 230.4 | 0.495 | 17.25 | 114.1 |  | 34
LV18 | 17.5 | 6125 | 90 | 77 | 105 | 229.8 | 0.612 | 21.25 | 140.6 |  | 34
LV18 | 17.5 | 6125 | 65 | 57 | 115 | 152.6 | 0.699 | 16.13 | 106.7 |  | 35
LV18 | 17.5 | 6125 | 70 | 57 | 115 | 153.1 | 0.884 | 20.45 | 135.3 |  | 35
LV18 | 17.5 | 6125 | 75 | 57 | 115 | 157.6 | 0.971 | 23.14 | 153.1 |  | 35
LV18 | 17.5 | 6125 | 80 | 57 | 115 | 167.4 | 0.971 | 24.58 | 162.6 |  | 35
LV18 | 17.5 | 6125 | 85 | 57 | 115 | 177.2 | 0.971 | 26 | 172 |  | 35
LV18 | 17.5 | 6125 | 90 | 57 | 115 | 186.8 | 0.971 | 27.42 | 181.4 |  | 35
LV18 | 17.5 | 6125 | 65 | 62 | 115 | 166.9 | 0.485 | 12.24 | 81 |  | 35
LV18 | 17.5 | 6125 | 70 | 62 | 115 | 167.4 | 0.651 | 16.46 | 108.9 |  | 35
LV18 | 17.5 | 6125 | 75 | 62 | 115 | 167.6 | 0.806 | 20.42 | 135.1 |  | 35
LV18 | 17.5 | 6125 | 80 | 62 | 115 | 167.5 | 0.971 | 24.58 | 162.6 |  | 35
LV18 | 17.5 | 6125 | 85 | 62 | 115 | 177.2 | 0.971 | 26.02 | 172.1 |  | 35
LV18 | 17.5 | 6125 | 90 | 62 | 115 | 186.7 | 0.971 | 27.41 | 181.3 |  | 35
LV18 | 17.5 | 6125 | 70 | 67 | 115 | 182.7 | 0.447 | 12.34 | 81.6 |  | 35
LV18 | 17.5 | 6125 | 75 | 67 | 115 | 182.9 | 0.593 | 16.39 | 108.4 |  | 35
LV18 | 17.5 | 6125 | 80 | 67 | 115 | 183.1 | 0.748 | 20.7 | 136.9 |  | 35
LV18 | 17.5 | 6125 | 85 | 67 | 115 | 182.5 | 0.894 | 24.66 | 163.1 |  | 35
LV18 | 17.5 | 6125 | 90 | 67 | 115 | 186.8 | 0.971 | 27.42 | 181.4 |  | 35
LV18 | 17.5 | 6125 | 75 | 72 | 115 | 198.9 | 0.408 | 12.26 | 81.1 |  | 35
LV18 | 17.5 | 6125 | 80 | 72 | 115 | 198.6 | 0.544 | 16.33 | 108 |  | 35
LV18 | 17.5 | 6125 | 85 | 72 | 115 | 198.3 | 0.689 | 20.67 | 136.7 |  | 35
LV18 | 17.5 | 6125 | 90 | 72 | 115 | 198.2 | 0.825 | 24.73 | 163.6 |  | 35
LV18 | 17.5 | 6125 | 80 | 77 | 115 | 215.3 | 0.369 | 12.02 | 79.5 |  | 35
LV18 | 17.5 | 6125 | 85 | 77 | 115 | 214.5 | 0.505 | 16.37 | 108.3 |  | 35
LV18 | 17.5 | 6125 | 90 | 77 | 115 | 213.8 | 0.631 | 20.41 | 135 |  | 35
LV18 | 17.5 | 6125 | 65 | 57 | 125 | 140 | 0.719 | 15.21 | 100.6 |  | 35
LV18 | 17.5 | 6125 | 70 | 57 | 125 | 140.1 | 0.913 | 19.33 | 127.9 |  | 35
LV18 | 17.5 | 6125 | 75 | 57 | 125 | 146.3 | 0.971 | 21.48 | 142.1 |  | 35
LV18 | 17.5 | 6125 | 80 | 57 | 125 | 155.7 | 0.971 | 22.86 | 151.2 |  | 35
LV18 | 17.5 | 6125 | 85 | 57 | 125 | 165 | 0.972 | 24.23 | 160.3 |  | 35
LV18 | 17.5 | 6125 | 90 | 57 | 125 | 174.2 | 0.971 | 25.58 | 169.2 |  | 35
LV18 | 17.5 | 6125 | 65 | 62 | 125 | 153.6 | 0.486 | 11.28 | 74.6 |  | 35
LV18 | 17.5 | 6125 | 70 | 62 | 125 | 153.8 | 0.661 | 15.36 | 101.6 |  | 35
LV18 | 17.5 | 6125 | 75 | 62 | 125 | 154.1 | 0.835 | 19.46 | 128.7 |  | 35
LV18 | 17.5 | 6125 | 80 | 62 | 125 | 155.7 | 0.971 | 22.86 | 151.2 |  | 35
LV18 | 17.5 | 6125 | 85 | 62 | 125 | 165 | 0.972 | 24.23 | 160.3 |  | 35
LV18 | 17.5 | 6125 | 90 | 62 | 125 | 174.1 | 0.971 | 25.55 | 169 |  | 35
LV18 | 17.5 | 6125 | 70 | 67 | 125 | 168.5 | 0.447 | 11.38 | 75.3 |  | 35
LV18 | 17.5 | 6125 | 75 | 67 | 125 | 168.5 | 0.602 | 15.34 | 101.5 |  | 35
LV18 | 17.5 | 6125 | 80 | 67 | 125 | 168.6 | 0.767 | 19.55 | 129.3 |  | 35
LV18 | 17.5 | 6125 | 85 | 67 | 125 | 167.4 | 0.932 | 23.6 | 156.1 |  | 35
LV18 | 17.5 | 6125 | 90 | 67 | 125 | 174.2 | 0.971 | 25.56 | 169.1 |  | 35
LV18 | 17.5 | 6125 | 75 | 72 | 125 | 183.6 | 0.408 | 11.32 | 74.9 |  | 35
LV18 | 17.5 | 6125 | 80 | 72 | 125 | 183 | 0.554 | 15.31 | 101.3 |  | 35
LV18 | 17.5 | 6125 | 85 | 72 | 125 | 182.7 | 0.709 | 19.58 | 129.5 |  | 35
LV18 | 17.5 | 6125 | 90 | 72 | 125 | 182.3 | 0.855 | 23.55 | 155.8 |  | 35
LV18 | 17.5 | 6125 | 80 | 77 | 125 | 198.9 | 0.379 | 11.38 | 75.3 |  | 35
LV18 | 17.5 | 6125 | 85 | 77 | 125 | 197.9 | 0.515 | 15.4 | 101.9 |  | 35
LV18 | 17.5 | 6125 | 90 | 77 | 125 | 197 | 0.651 | 19.38 | 128.2 |  | 35
LV18 | 17.5 | 7000 | 65 | 57 | 75 | 202.1 | 0.68 | 18.17 | 137.4 |  | 33
LV18 | 17.5 | 7000 | 70 | 57 | 75 | 202.9 | 0.845 | 22.67 | 171.4 |  | 33
LV18 | 17.5 | 7000 | 75 | 57 | 75 | 205 | 0.971 | 26.34 | 199.1 |  | 33
LV18 | 17.5 | 7000 | 80 | 57 | 75 | 216.8 | 0.971 | 27.86 | 210.6 |  | 33
LV18 | 17.5 | 7000 | 85 | 57 | 75 | 228.6 | 0.972 | 29.38 | 222.1 |  | 33
LV18 | 17.5 | 7000 | 90 | 57 | 75 | 240.2 | 0.971 | 30.86 | 233.3 |  | 33
LV18 | 17.5 | 7000 | 65 | 62 | 75 | 219.4 | 0.485 | 14.09 | 106.5 |  | 33
LV18 | 17.5 | 7000 | 70 | 62 | 75 | 220.2 | 0.631 | 18.39 | 139 |  | 33
LV18 | 17.5 | 7000 | 75 | 62 | 75 | 220.8 | 0.777 | 22.7 | 171.6 |  | 33
LV18 | 17.5 | 7000 | 80 | 62 | 75 | 221 | 0.923 | 26.97 | 203.9 |  | 33
LV18 | 17.5 | 7000 | 85 | 62 | 75 | 228.8 | 0.971 | 29.39 | 222.2 |  | 33
LV18 | 17.5 | 7000 | 90 | 62 | 75 | 240.3 | 0.971 | 30.86 | 233.3 |  | 33
LV18 | 17.5 | 7000 | 70 | 67 | 75 | 239.2 | 0.437 | 13.82 | 104.5 |  | 33
LV18 | 17.5 | 7000 | 75 | 67 | 75 | 239.7 | 0.573 | 18.16 | 137.3 |  | 33
LV18 | 17.5 | 7000 | 80 | 67 | 75 | 240 | 0.709 | 22.51 | 170.2 |  | 33
LV18 | 17.5 | 7000 | 85 | 67 | 75 | 240.4 | 0.845 | 26.87 | 203.1 |  | 33
LV18 | 17.5 | 7000 | 90 | 67 | 75 | 240.4 | 0.971 | 30.89 | 233.5 |  | 33
LV18 | 17.5 | 7000 | 75 | 72 | 75 | 258.7 | 0.408 | 13.96 | 105.5 |  | 33
LV18 | 17.5 | 7000 | 80 | 72 | 75 | 259 | 0.524 | 17.96 | 135.8 |  | 33
LV18 | 17.5 | 7000 | 85 | 72 | 75 | 259 | 0.66 | 22.62 | 171 |  | 33
LV18 | 17.5 | 7000 | 90 | 72 | 75 | 259 | 0.786 | 26.94 | 203.7 |  | 33
LV18 | 17.5 | 7000 | 80 | 77 | 75 | 279.4 | 0.369 | 13.64 | 103.1 |  | 33
LV18 | 17.5 | 7000 | 85 | 77 | 75 | 278.7 | 0.485 | 17.9 | 135.3 |  | 33
LV18 | 17.5 | 7000 | 90 | 77 | 75 | 278.5 | 0.602 | 22.18 | 167.7 |  | 33
LV18 | 17.5 | 7000 | 65 | 57 | 85 | 190.9 | 0.689 | 17.41 | 131.6 |  | 33
LV18 | 17.5 | 7000 | 70 | 57 | 85 | 191.7 | 0.854 | 21.67 | 163.8 |  | 33
LV18 | 17.5 | 7000 | 75 | 57 | 85 | 195.3 | 0.971 | 25.09 | 189.7 |  | 33
LV18 | 17.5 | 7000 | 80 | 57 | 85 | 207 | 0.971 | 26.59 | 201 |  | 33
LV18 | 17.5 | 7000 | 85 | 57 | 85 | 218.3 | 0.971 | 28.04 | 212 |  | 33
LV18 | 17.5 | 7000 | 90 | 57 | 85 | 229.5 | 0.971 | 29.48 | 222.9 |  | 33
LV18 | 17.5 | 7000 | 65 | 62 | 85 | 207.8 | 0.486 | 13.35 | 100.9 |  | 33
LV18 | 17.5 | 7000 | 70 | 62 | 85 | 208.9 | 0.631 | 17.45 | 131.9 |  | 33
LV18 | 17.5 | 7000 | 75 | 62 | 85 | 209.4 | 0.787 | 21.79 | 164.7 |  | 33
LV18 | 17.5 | 7000 | 80 | 62 | 85 | 209.2 | 0.942 | 26.07 | 197.1 |  | 33
LV18 | 17.5 | 7000 | 85 | 62 | 85 | 218.4 | 0.971 | 28.06 | 212.1 |  | 33
LV18 | 17.5 | 7000 | 90 | 62 | 85 | 229.6 | 0.971 | 29.5 | 223 |  | 33
LV18 | 17.5 | 7000 | 70 | 67 | 85 | 226.8 | 0.447 | 13.4 | 101.3 |  | 33
LV18 | 17.5 | 7000 | 75 | 67 | 85 | 227.3 | 0.582 | 17.51 | 132.4 |  | 33
LV18 | 17.5 | 7000 | 80 | 67 | 85 | 227.6 | 0.728 | 21.93 | 165.8 |  | 33
LV18 | 17.5 | 7000 | 85 | 67 | 85 | 227.8 | 0.864 | 26.04 | 196.9 |  | 33
LV18 | 17.5 | 7000 | 90 | 67 | 85 | 229.7 | 0.971 | 29.5 | 223 |  | 33
LV18 | 17.5 | 7000 | 75 | 72 | 85 | 245.6 | 0.408 | 13.25 | 100.2 |  | 33
LV18 | 17.5 | 7000 | 80 | 72 | 85 | 245.8 | 0.534 | 17.37 | 131.3 |  | 33
LV18 | 17.5 | 7000 | 85 | 72 | 85 | 245.7 | 0.67 | 21.79 | 164.7 |  | 33
LV18 | 17.5 | 7000 | 90 | 72 | 85 | 245.9 | 0.806 | 26.22 | 198.2 |  | 33
LV18 | 17.5 | 7000 | 80 | 77 | 85 | 265 | 0.369 | 12.94 | 97.8 |  | 33
LV18 | 17.5 | 7000 | 85 | 77 | 85 | 264.7 | 0.495 | 17.34 | 131.1 |  | 33
LV18 | 17.5 | 7000 | 90 | 77 | 85 | 264.4 | 0.612 | 21.4 | 161.8 |  | 33
LV18 | 17.5 | 7000 | 65 | 57 | 95 | 179.3 | 0.699 | 16.59 | 125.4 |  | 34
LV18 | 17.5 | 7000 | 70 | 57 | 95 | 180.3 | 0.874 | 20.85 | 157.6 |  | 34
LV18 | 17.5 | 7000 | 75 | 57 | 95 | 185.2 | 0.971 | 23.8 | 179.9 |  | 34
LV18 | 17.5 | 7000 | 80 | 57 | 95 | 196.4 | 0.971 | 25.22 | 190.7 |  | 34
LV18 | 17.5 | 7000 | 85 | 57 | 95 | 207.4 | 0.972 | 26.65 | 201.5 |  | 34
LV18 | 17.5 | 7000 | 90 | 57 | 95 | 218.4 | 0.971 | 28.06 | 212.1 |  | 34
LV18 | 17.5 | 7000 | 65 | 62 | 95 | 195.6 | 0.486 | 12.57 | 95 |  | 34
LV18 | 17.5 | 7000 | 70 | 62 | 95 | 196.4 | 0.641 | 16.65 | 125.9 |  | 34
LV18 | 17.5 | 7000 | 75 | 62 | 95 | 197 | 0.806 | 21.01 | 158.8 |  | 34
LV18 | 17.5 | 7000 | 80 | 62 | 95 | 196.6 | 0.971 | 25.25 | 190.9 |  | 34
LV18 | 17.5 | 7000 | 85 | 62 | 95 | 207.5 | 0.971 | 26.65 | 201.5 |  | 34
LV18 | 17.5 | 7000 | 90 | 62 | 95 | 218.3 | 0.971 | 28.04 | 212 |  | 34
LV18 | 17.5 | 7000 | 70 | 67 | 95 | 213.7 | 0.446 | 12.62 | 95.4 |  | 34
LV18 | 17.5 | 7000 | 75 | 67 | 95 | 214.2 | 0.592 | 16.79 | 126.9 |  | 34
LV18 | 17.5 | 7000 | 80 | 67 | 95 | 214.5 | 0.738 | 20.94 | 158.3 |  | 34
LV18 | 17.5 | 7000 | 85 | 67 | 95 | 214.2 | 0.894 | 25.32 | 191.4 |  | 34
LV18 | 17.5 | 7000 | 90 | 67 | 95 | 218.4 | 0.971 | 28.06 | 212.1 |  | 34
LV18 | 17.5 | 7000 | 75 | 72 | 95 | 231.8 | 0.408 | 12.5 | 94.5 |  | 34
LV18 | 17.5 | 7000 | 80 | 72 | 95 | 231.8 | 0.544 | 16.68 | 126.1 |  | 34
LV18 | 17.5 | 7000 | 85 | 72 | 95 | 231.7 | 0.68 | 20.83 | 157.5 |  | 34
LV18 | 17.5 | 7000 | 90 | 72 | 95 | 231.6 | 0.825 | 25.28 | 191.1 |  | 34
LV18 | 17.5 | 7000 | 80 | 77 | 95 | 250.2 | 0.369 | 12.21 | 92.3 |  | 34
LV18 | 17.5 | 7000 | 85 | 77 | 95 | 249.8 | 0.505 | 16.68 | 126.1 |  | 34
LV18 | 17.5 | 7000 | 90 | 77 | 95 | 249.4 | 0.631 | 20.82 | 157.4 |  | 34
LV18 | 17.5 | 7000 | 65 | 57 | 105 | 167.4 | 0.719 | 15.91 | 120.3 |  | 34
LV18 | 17.5 | 7000 | 70 | 57 | 105 | 167.9 | 0.893 | 19.84 | 150 |  | 34
LV18 | 17.5 | 7000 | 75 | 57 | 105 | 174.4 | 0.971 | 22.41 | 169.4 |  | 34
LV18 | 17.5 | 7000 | 80 | 57 | 105 | 185.1 | 0.971 | 23.78 | 179.8 |  | 34
LV18 | 17.5 | 7000 | 85 | 57 | 105 | 195.8 | 0.971 | 25.15 | 190.1 |  | 34
LV18 | 17.5 | 7000 | 90 | 57 | 105 | 206.3 | 0.971 | 26.51 | 200.4 |  | 34
LV18 | 17.5 | 7000 | 65 | 62 | 105 | 182.7 | 0.485 | 11.73 | 88.7 |  | 34
LV18 | 17.5 | 7000 | 70 | 62 | 105 | 183.4 | 0.66 | 16.02 | 121.1 |  | 34
LV18 | 17.5 | 7000 | 75 | 62 | 105 | 184 | 0.826 | 20.09 | 151.9 |  | 34
LV18 | 17.5 | 7000 | 80 | 62 | 105 | 184.6 | 0.971 | 23.7 | 179.2 |  | 34
LV18 | 17.5 | 7000 | 85 | 62 | 105 | 195.8 | 0.971 | 25.16 | 190.2 |  | 34
LV18 | 17.5 | 7000 | 90 | 62 | 105 | 206.3 | 0.971 | 26.51 | 200.4 |  | 34
LV18 | 17.5 | 7000 | 70 | 67 | 105 | 199.7 | 0.447 | 11.8 | 89.2 |  | 34
LV18 | 17.5 | 7000 | 75 | 67 | 105 | 200.3 | 0.602 | 15.95 | 120.6 |  | 34
LV18 | 17.5 | 7000 | 80 | 67 | 105 | 200.5 | 0.757 | 20.08 | 151.8 |  | 34
LV18 | 17.5 | 7000 | 85 | 67 | 105 | 199.8 | 0.922 | 24.38 | 184.3 |  | 34
LV18 | 17.5 | 7000 | 90 | 67 | 105 | 206.3 | 0.971 | 26.51 | 200.4 |  | 34
LV18 | 17.5 | 7000 | 75 | 72 | 105 | 217.1 | 0.408 | 11.71 | 88.5 |  | 34
LV18 | 17.5 | 7000 | 80 | 72 | 105 | 217 | 0.553 | 15.89 | 120.1 |  | 34
LV18 | 17.5 | 7000 | 85 | 72 | 105 | 216.8 | 0.699 | 20.05 | 151.6 |  | 34
LV18 | 17.5 | 7000 | 90 | 72 | 105 | 216.2 | 0.845 | 24.17 | 182.7 |  | 34
LV18 | 17.5 | 7000 | 80 | 77 | 105 | 234.6 | 0.379 | 11.76 | 88.9 |  | 34
LV18 | 17.5 | 7000 | 85 | 77 | 105 | 234 | 0.515 | 15.93 | 120.4 |  | 34
LV18 | 17.5 | 7000 | 90 | 77 | 105 | 233.3 | 0.651 | 20.08 | 151.8 |  | 34
LV18 | 17.5 | 7000 | 65 | 57 | 115 | 154.6 | 0.728 | 14.89 | 112.6 |  | 35
LV18 | 17.5 | 7000 | 70 | 57 | 115 | 154.8 | 0.922 | 18.89 | 142.8 |  | 35
LV18 | 17.5 | 7000 | 75 | 57 | 115 | 162.9 | 0.971 | 20.93 | 158.2 |  | 35
LV18 | 17.5 | 7000 | 80 | 57 | 115 | 173.2 | 0.971 | 22.25 | 168.2 |  | 35
LV18 | 17.5 | 7000 | 85 | 57 | 115 | 183.4 | 0.971 | 23.56 | 178.1 |  | 35
LV18 | 17.5 | 7000 | 90 | 57 | 115 | 193.4 | 0.971 | 24.84 | 187.8 |  | 35
LV18 | 17.5 | 7000 | 65 | 62 | 115 | 169.2 | 0.495 | 11.08 | 83.8 |  | 35
LV18 | 17.5 | 7000 | 70 | 62 | 115 | 169.8 | 0.67 | 15.05 | 113.8 |  | 35
LV18 | 17.5 | 7000 | 75 | 62 | 115 | 170.3 | 0.845 | 19.03 | 143.9 |  | 35
LV18 | 17.5 | 7000 | 80 | 62 | 115 | 173.4 | 0.971 | 22.28 | 168.4 |  | 35
LV18 | 17.5 | 7000 | 85 | 62 | 115 | 183.2 | 0.971 | 23.53 | 177.9 |  | 35
LV18 | 17.5 | 7000 | 90 | 62 | 115 | 193.4 | 0.972 | 24.85 | 187.9 |  | 35
LV18 | 17.5 | 7000 | 70 | 67 | 115 | 185.4 | 0.447 | 10.95 | 82.8 |  | 35
LV18 | 17.5 | 7000 | 75 | 67 | 115 | 185.8 | 0.612 | 15.04 | 113.7 |  | 35
LV18 | 17.5 | 7000 | 80 | 67 | 115 | 185.7 | 0.787 | 19.33 | 146.1 |  | 35
LV18 | 17.5 | 7000 | 85 | 67 | 115 | 184.1 | 0.961 | 23.41 | 177 |  | 35
LV18 | 17.5 | 7000 | 90 | 67 | 115 | 193.4 | 0.972 | 24.85 | 187.9 |  | 35
LV18 | 17.5 | 7000 | 75 | 72 | 115 | 201.7 | 0.417 | 11.14 | 84.2 |  | 35
LV18 | 17.5 | 7000 | 80 | 72 | 115 | 202 | 0.563 | 15.05 | 113.8 |  | 35
LV18 | 17.5 | 7000 | 85 | 72 | 115 | 201.4 | 0.718 | 19.14 | 144.7 |  | 35
LV18 | 17.5 | 7000 | 90 | 72 | 115 | 200.3 | 0.884 | 23.41 | 177 |  | 35
LV18 | 17.5 | 7000 | 80 | 77 | 115 | 218.3 | 0.379 | 10.94 | 82.7 |  | 35
LV18 | 17.5 | 7000 | 85 | 77 | 115 | 217.5 | 0.524 | 15.08 | 114 |  | 35
LV18 | 17.5 | 7000 | 90 | 77 | 115 | 216.7 | 0.67 | 19.21 | 145.2 |  | 35
LV18 | 17.5 | 7000 | 65 | 57 | 125 | 141.3 | 0.747 | 13.97 | 105.6 |  | 35
LV18 | 17.5 | 7000 | 70 | 57 | 125 | 141 | 0.962 | 17.94 | 135.6 |  | 35
LV18 | 17.5 | 7000 | 75 | 57 | 125 | 150.7 | 0.971 | 19.37 | 146.4 |  | 35
LV18 | 17.5 | 7000 | 80 | 57 | 125 | 160.5 | 0.971 | 20.61 | 155.8 |  | 35
LV18 | 17.5 | 7000 | 85 | 57 | 125 | 170.4 | 0.971 | 21.89 | 165.5 |  | 35
LV18 | 17.5 | 7000 | 90 | 57 | 125 | 179.9 | 0.971 | 23.11 | 174.7 |  | 35
LV18 | 17.5 | 7000 | 65 | 62 | 125 | 155.1 | 0.495 | 10.16 | 76.8 |  | 35
LV18 | 17.5 | 7000 | 70 | 62 | 125 | 155.8 | 0.689 | 14.21 | 107.4 |  | 35
LV18 | 17.5 | 7000 | 75 | 62 | 125 | 155.8 | 0.874 | 18.02 | 136.2 |  | 35
LV18 | 17.5 | 7000 | 80 | 62 | 125 | 160.6 | 0.971 | 20.63 | 156 |  | 35
LV18 | 17.5 | 7000 | 85 | 62 | 125 | 170.1 | 0.971 | 21.85 | 165.2 |  | 35
LV18 | 17.5 | 7000 | 90 | 62 | 125 | 179.9 | 0.971 | 23.11 | 174.7 |  | 35
LV18 | 17.5 | 7000 | 70 | 67 | 125 | 170.4 | 0.457 | 10.29 | 77.8 |  | 35
LV18 | 17.5 | 7000 | 75 | 67 | 125 | 170.6 | 0.631 | 14.25 | 107.7 |  | 35
LV18 | 17.5 | 7000 | 80 | 67 | 125 | 170.5 | 0.806 | 18.17 | 137.4 |  | 35
LV18 | 17.5 | 7000 | 85 | 67 | 125 | 170.2 | 0.971 | 21.87 | 165.3 |  | 35
LV18 | 17.5 | 7000 | 90 | 67 | 125 | 179.9 | 0.972 | 23.12 | 174.8 |  | 35
LV18 | 17.5 | 7000 | 75 | 72 | 125 | 186.3 | 0.418 | 10.29 | 77.8 |  | 35
LV18 | 17.5 | 7000 | 80 | 72 | 125 | 185.5 | 0.583 | 14.3 | 108.1 |  | 35
LV18 | 17.5 | 7000 | 85 | 72 | 125 | 184.6 | 0.748 | 18.27 | 138.1 |  | 35
LV18 | 17.5 | 7000 | 90 | 72 | 125 | 183.3 | 0.923 | 22.37 | 169.1 |  | 35
LV18 | 17.5 | 7000 | 80 | 77 | 125 | 202.5 | 0.379 | 10.15 | 76.7 |  | 35
LV18 | 17.5 | 7000 | 85 | 77 | 125 | 200.2 | 0.534 | 14.14 | 106.9 |  | 35
LV18 | 17.5 | 7000 | 90 | 77 | 125 | 199.2 | 0.69 | 18.17 | 137.4 |  | 35
LV18 | 17.5 | 7875 | 65 | 57 | 75 | 205.9 | 0.699 | 16.92 | 143.9 |  | 33
LV18 | 17.5 | 7875 | 70 | 57 | 75 | 206.7 | 0.874 | 21.23 | 180.6 |  | 33
LV18 | 17.5 | 7875 | 75 | 57 | 75 | 212.1 | 0.971 | 24.22 | 206 |  | 33
LV18 | 17.5 | 7875 | 80 | 57 | 75 | 224.7 | 0.971 | 25.66 | 218.2 |  | 33
LV18 | 17.5 | 7875 | 85 | 57 | 75 | 236.8 | 0.971 | 27.04 | 230 |  | 33
LV18 | 17.5 | 7875 | 90 | 57 | 75 | 249 | 0.971 | 28.43 | 241.8 |  | 33
LV18 | 17.5 | 7875 | 65 | 62 | 75 | 223.6 | 0.486 | 12.77 | 108.6 |  | 33
LV18 | 17.5 | 7875 | 70 | 62 | 75 | 224.6 | 0.641 | 16.93 | 144 |  | 33
LV18 | 17.5 | 7875 | 75 | 62 | 75 | 225.6 | 0.806 | 21.38 | 181.8 |  | 33
LV18 | 17.5 | 7875 | 80 | 62 | 75 | 225.1 | 0.961 | 25.44 | 216.4 |  | 33
LV18 | 17.5 | 7875 | 85 | 62 | 75 | 236.9 | 0.971 | 27.04 | 230 |  | 33
LV18 | 17.5 | 7875 | 90 | 62 | 75 | 249 | 0.971 | 28.43 | 241.8 |  | 33
LV18 | 17.5 | 7875 | 70 | 67 | 75 | 243.4 | 0.447 | 12.79 | 108.8 |  | 33
LV18 | 17.5 | 7875 | 75 | 67 | 75 | 243.9 | 0.592 | 16.99 | 144.5 |  | 33
LV18 | 17.5 | 7875 | 80 | 67 | 75 | 244.2 | 0.738 | 21.2 | 180.3 |  | 33
LV18 | 17.5 | 7875 | 85 | 67 | 75 | 244.6 | 0.893 | 25.69 | 218.5 |  | 33
LV18 | 17.5 | 7875 | 90 | 67 | 75 | 249 | 0.971 | 28.43 | 241.8 |  | 33
LV18 | 17.5 | 7875 | 75 | 72 | 75 | 263.3 | 0.408 | 12.63 | 107.4 |  | 33
LV18 | 17.5 | 7875 | 80 | 72 | 75 | 263.6 | 0.544 | 16.86 | 143.4 |  | 33
LV18 | 17.5 | 7875 | 85 | 72 | 75 | 263.8 | 0.68 | 21.08 | 179.3 |  | 33
LV18 | 17.5 | 7875 | 90 | 72 | 75 | 263.5 | 0.825 | 25.57 | 217.5 |  | 33
LV18 | 17.5 | 7875 | 80 | 77 | 75 | 284.4 | 0.369 | 12.33 | 104.9 |  | 33
LV18 | 17.5 | 7875 | 85 | 77 | 75 | 283.6 | 0.505 | 16.84 | 143.2 |  | 33
LV18 | 17.5 | 7875 | 90 | 77 | 75 | 283.4 | 0.631 | 21.03 | 178.9 |  | 33
LV18 | 17.5 | 7875 | 65 | 57 | 85 | 194.1 | 0.709 | 16.18 | 137.6 |  | 33
LV18 | 17.5 | 7875 | 70 | 57 | 85 | 195 | 0.893 | 20.48 | 174.2 |  | 33
LV18 | 17.5 | 7875 | 75 | 57 | 85 | 201.8 | 0.971 | 23.05 | 196 |  | 33
LV18 | 17.5 | 7875 | 80 | 57 | 85 | 214 | 0.971 | 24.43 | 207.8 |  | 33
LV18 | 17.5 | 7875 | 85 | 57 | 85 | 225.9 | 0.971 | 25.8 | 219.4 |  | 33
LV18 | 17.5 | 7875 | 90 | 57 | 85 | 237.6 | 0.971 | 27.13 | 230.7 |  | 33
LV18 | 17.5 | 7875 | 65 | 62 | 85 | 211.6 | 0.486 | 12.09 | 102.8 |  | 33
LV18 | 17.5 | 7875 | 70 | 62 | 85 | 212.6 | 0.651 | 16.26 | 138.3 |  | 33
LV18 | 17.5 | 7875 | 75 | 62 | 85 | 213.2 | 0.826 | 20.69 | 176 |  | 33
LV18 | 17.5 | 7875 | 80 | 62 | 85 | 214 | 0.971 | 24.43 | 207.8 |  | 33
LV18 | 17.5 | 7875 | 85 | 62 | 85 | 225.9 | 0.971 | 25.8 | 219.4 |  | 33
LV18 | 17.5 | 7875 | 90 | 62 | 85 | 237.7 | 0.971 | 27.14 | 230.8 |  | 33
LV18 | 17.5 | 7875 | 70 | 67 | 85 | 230.4 | 0.447 | 12.1 | 102.9 |  | 33
LV18 | 17.5 | 7875 | 75 | 67 | 85 | 230.9 | 0.602 | 16.36 | 139.1 |  | 33
LV18 | 17.5 | 7875 | 80 | 67 | 85 | 231.2 | 0.758 | 20.6 | 175.2 |  | 33
LV18 | 17.5 | 7875 | 85 | 67 | 85 | 231.1 | 0.913 | 24.81 | 211 |  | 33
LV18 | 17.5 | 7875 | 90 | 67 | 85 | 237.6 | 0.971 | 27.13 | 230.7 |  | 33
LV18 | 17.5 | 7875 | 75 | 72 | 85 | 249.8 | 0.408 | 11.98 | 101.9 |  | 33
LV18 | 17.5 | 7875 | 80 | 72 | 85 | 249.9 | 0.553 | 16.26 | 138.3 |  | 33
LV18 | 17.5 | 7875 | 85 | 72 | 85 | 249.8 | 0.699 | 20.54 | 174.7 |  | 33
LV18 | 17.5 | 7875 | 90 | 72 | 85 | 249.9 | 0.845 | 24.83 | 211.2 |  | 33
LV18 | 17.5 | 7875 | 80 | 77 | 85 | 269.2 | 0.379 | 11.99 | 102 |  | 33
LV18 | 17.5 | 7875 | 85 | 77 | 85 | 268.9 | 0.505 | 15.97 | 135.8 |  | 33
LV18 | 17.5 | 7875 | 90 | 77 | 85 | 268.7 | 0.641 | 20.25 | 172.2 |  | 33
LV18 | 17.5 | 7875 | 65 | 57 | 95 | 181.9 | 0.728 | 15.58 | 132.5 |  | 34
LV18 | 17.5 | 7875 | 70 | 57 | 95 | 182.8 | 0.913 | 19.62 | 166.9 |  | 34
LV18 | 17.5 | 7875 | 75 | 57 | 95 | 191 | 0.971 | 21.81 | 185.5 |  | 34
LV18 | 17.5 | 7875 | 80 | 57 | 95 | 202.6 | 0.971 | 23.14 | 196.8 |  | 34
LV18 | 17.5 | 7875 | 85 | 57 | 95 | 214.1 | 0.971 | 24.44 | 207.9 |  | 34
LV18 | 17.5 | 7875 | 90 | 57 | 95 | 225.6 | 0.971 | 25.75 | 219 |  | 34
LV18 | 17.5 | 7875 | 65 | 62 | 95 | 198.7 | 0.495 | 11.57 | 98.4 |  | 34
LV18 | 17.5 | 7875 | 70 | 62 | 95 | 199.6 | 0.66 | 15.5 | 131.8 |  | 34
LV18 | 17.5 | 7875 | 75 | 62 | 95 | 200.2 | 0.835 | 19.66 | 167.2 |  | 34
LV18 | 17.5 | 7875 | 80 | 62 | 95 | 202.6 | 0.971 | 23.14 | 196.8 |  | 34
LV18 | 17.5 | 7875 | 85 | 62 | 95 | 214.2 | 0.971 | 24.46 | 208 |  | 34
LV18 | 17.5 | 7875 | 90 | 62 | 95 | 225.6 | 0.971 | 25.75 | 219 |  | 34
LV18 | 17.5 | 7875 | 70 | 67 | 95 | 216.7 | 0.447 | 11.38 | 96.8 |  | 34
LV18 | 17.5 | 7875 | 75 | 67 | 95 | 217.1 | 0.612 | 15.63 | 132.9 |  | 34
LV18 | 17.5 | 7875 | 80 | 67 | 95 | 217.3 | 0.777 | 19.85 | 168.8 |  | 34
LV18 | 17.5 | 7875 | 85 | 67 | 95 | 216.9 | 0.942 | 24.02 | 204.3 |  | 34
LV18 | 17.5 | 7875 | 90 | 67 | 95 | 225.5 | 0.971 | 25.75 | 219 |  | 34
LV18 | 17.5 | 7875 | 75 | 72 | 95 | 235.2 | 0.408 | 11.28 | 95.9 |  | 34
LV18 | 17.5 | 7875 | 80 | 72 | 95 | 235.1 | 0.563 | 15.57 | 132.4 |  | 34
LV18 | 17.5 | 7875 | 85 | 72 | 95 | 235 | 0.719 | 19.86 | 168.9 |  | 34
LV18 | 17.5 | 7875 | 90 | 72 | 95 | 234.6 | 0.864 | 23.84 | 202.8 |  | 34
LV18 | 17.5 | 7875 | 80 | 77 | 95 | 253.9 | 0.379 | 11.31 | 96.2 |  | 34
LV18 | 17.5 | 7875 | 85 | 77 | 95 | 253.7 | 0.515 | 15.36 | 130.6 |  | 34
LV18 | 17.5 | 7875 | 90 | 77 | 95 | 253 | 0.66 | 19.65 | 167.1 |  | 34
LV18 | 17.5 | 7875 | 65 | 57 | 105 | 169.2 | 0.738 | 14.69 | 124.9 |  | 34
LV18 | 17.5 | 7875 | 70 | 57 | 105 | 169.8 | 0.942 | 18.8 | 159.9 |  | 34
LV18 | 17.5 | 7875 | 75 | 57 | 105 | 179.4 | 0.971 | 20.48 | 174.2 |  | 34
LV18 | 17.5 | 7875 | 80 | 57 | 105 | 190.6 | 0.971 | 21.76 | 185.1 |  | 34
LV18 | 17.5 | 7875 | 85 | 57 | 105 | 201.7 | 0.971 | 23.02 | 195.8 |  | 34
LV18 | 17.5 | 7875 | 90 | 57 | 105 | 212.7 | 0.971 | 24.28 | 206.5 |  | 34
LV18 | 17.5 | 7875 | 65 | 62 | 105 | 185.4 | 0.495 | 10.79 | 91.8 |  | 34
LV18 | 17.5 | 7875 | 70 | 62 | 105 | 185.9 | 0.68 | 14.86 | 126.4 |  | 34
LV18 | 17.5 | 7875 | 75 | 62 | 105 | 186.4 | 0.864 | 18.94 | 161.1 |  | 34
LV18 | 17.5 | 7875 | 80 | 62 | 105 | 190.6 | 0.971 | 21.76 | 185.1 |  | 34
LV18 | 17.5 | 7875 | 85 | 62 | 105 | 201.7 | 0.971 | 23.03 | 195.9 |  | 34
LV18 | 17.5 | 7875 | 90 | 62 | 105 | 212.6 | 0.971 | 24.28 | 206.5 |  | 34
LV18 | 17.5 | 7875 | 70 | 67 | 105 | 202.3 | 0.457 | 10.86 | 92.4 |  | 34
LV18 | 17.5 | 7875 | 75 | 67 | 105 | 202.5 | 0.622 | 14.8 | 125.9 |  | 34
LV18 | 17.5 | 7875 | 80 | 67 | 105 | 202.8 | 0.796 | 18.99 | 161.5 |  | 34
LV18 | 17.5 | 7875 | 85 | 67 | 105 | 201.7 | 0.971 | 23.03 | 195.9 |  | 34
LV18 | 17.5 | 7875 | 90 | 67 | 105 | 212.8 | 0.971 | 24.29 | 206.6 |  | 34
LV18 | 17.5 | 7875 | 75 | 72 | 105 | 219.9 | 0.417 | 10.79 | 91.8 |  | 34
LV18 | 17.5 | 7875 | 80 | 72 | 105 | 219.7 | 0.573 | 14.8 | 125.9 |  | 34
LV18 | 17.5 | 7875 | 85 | 72 | 105 | 219.5 | 0.738 | 19.05 | 162 |  | 34
LV18 | 17.5 | 7875 | 90 | 72 | 105 | 218.4 | 0.903 | 23.2 | 197.3 |  | 34
LV18 | 17.5 | 7875 | 80 | 77 | 105 | 237.7 | 0.379 | 10.58 | 90 |  | 34
LV18 | 17.5 | 7875 | 85 | 77 | 105 | 236.8 | 0.524 | 14.6 | 124.2 |  | 34
LV18 | 17.5 | 7875 | 90 | 77 | 105 | 236.4 | 0.68 | 18.89 | 160.7 |  | 34
LV18 | 17.5 | 7875 | 65 | 57 | 115 | 155.9 | 0.758 | 13.89 | 118.1 |  | 35
LV18 | 17.5 | 7875 | 70 | 57 | 115 | 156.4 | 0.971 | 17.86 | 151.9 |  | 35
LV18 | 17.5 | 7875 | 75 | 57 | 115 | 167.2 | 0.971 | 19.09 | 162.4 |  | 35
LV18 | 17.5 | 7875 | 80 | 57 | 115 | 177.9 | 0.971 | 20.32 | 172.8 |  | 35
LV18 | 17.5 | 7875 | 85 | 57 | 115 | 188.5 | 0.971 | 21.53 | 183.1 |  | 35
LV18 | 17.5 | 7875 | 90 | 57 | 115 | 199 | 0.971 | 22.72 | 193.2 |  | 35
LV18 | 17.5 | 7875 | 65 | 62 | 115 | 171 | 0.495 | 9.96 | 84.7 |  | 35
LV18 | 17.5 | 7875 | 70 | 62 | 115 | 171.8 | 0.69 | 13.93 | 118.5 |  | 35
LV18 | 17.5 | 7875 | 75 | 62 | 115 | 171.8 | 0.893 | 18.05 | 153.5 |  | 35
LV18 | 17.5 | 7875 | 80 | 62 | 115 | 177.8 | 0.971 | 20.31 | 172.7 |  | 35
LV18 | 17.5 | 7875 | 85 | 62 | 115 | 188.5 | 0.971 | 21.53 | 183.1 |  | 35
LV18 | 17.5 | 7875 | 90 | 62 | 115 | 199 | 0.971 | 22.73 | 193.3 |  | 35
LV18 | 17.5 | 7875 | 70 | 67 | 115 | 187.1 | 0.456 | 10.04 | 85.4 |  | 35
LV18 | 17.5 | 7875 | 75 | 67 | 115 | 187.4 | 0.641 | 14.12 | 120.1 |  | 35
LV18 | 17.5 | 7875 | 80 | 67 | 115 | 187.5 | 0.825 | 18.19 | 154.7 |  | 35
LV18 | 17.5 | 7875 | 85 | 67 | 115 | 188.5 | 0.971 | 21.52 | 183 |  | 35
LV18 | 17.5 | 7875 | 90 | 67 | 115 | 199.4 | 0.971 | 22.76 | 193.6 |  | 35
LV18 | 17.5 | 7875 | 75 | 72 | 115 | 203.8 | 0.418 | 10.01 | 85.1 |  | 35
LV18 | 17.5 | 7875 | 80 | 72 | 115 | 203.6 | 0.583 | 13.94 | 118.6 |  | 35
LV18 | 17.5 | 7875 | 85 | 72 | 115 | 203 | 0.758 | 18.08 | 153.8 |  | 35
LV18 | 17.5 | 7875 | 90 | 72 | 115 | 201.2 | 0.942 | 22.28 | 189.5 |  | 35
LV18 | 17.5 | 7875 | 80 | 77 | 115 | 220.8 | 0.389 | 10.09 | 85.8 |  | 35
LV18 | 17.5 | 7875 | 85 | 77 | 115 | 219.3 | 0.544 | 14.03 | 119.3 |  | 35
LV18 | 17.5 | 7875 | 90 | 77 | 115 | 218.9 | 0.699 | 18 | 153.1 |  | 35
LV18 | 17.5 | 7875 | 65 | 57 | 125 | 142 | 0.777 | 12.97 | 110.3 |  | 35
LV18 | 17.5 | 7875 | 70 | 57 | 125 | 143.8 | 0.971 | 16.43 | 139.7 |  | 35
LV18 | 17.5 | 7875 | 75 | 57 | 125 | 154.3 | 0.971 | 17.61 | 149.8 |  | 35
LV18 | 17.5 | 7875 | 80 | 57 | 125 | 164.5 | 0.971 | 18.78 | 159.7 |  | 35
LV18 | 17.5 | 7875 | 85 | 57 | 125 | 174.6 | 0.971 | 19.94 | 169.6 |  | 35
LV18 | 17.5 | 7875 | 90 | 57 | 125 | 184.6 | 0.971 | 21.08 | 179.3 |  | 35
LV18 | 17.5 | 7875 | 65 | 62 | 125 | 156.3 | 0.505 | 9.28 | 78.9 |  | 35
LV18 | 17.5 | 7875 | 70 | 62 | 125 | 157 | 0.709 | 13.09 | 111.3 |  | 35
LV18 | 17.5 | 7875 | 75 | 62 | 125 | 156.3 | 0.932 | 17.13 | 145.7 |  | 35
LV18 | 17.5 | 7875 | 80 | 62 | 125 | 164.5 | 0.971 | 18.79 | 159.8 |  | 35
LV18 | 17.5 | 7875 | 85 | 62 | 125 | 174.6 | 0.971 | 19.93 | 169.5 |  | 35
LV18 | 17.5 | 7875 | 90 | 62 | 125 | 184.4 | 0.971 | 21.06 | 179.1 |  | 35
LV18 | 17.5 | 7875 | 70 | 67 | 125 | 171.1 | 0.466 | 9.38 | 79.8 |  | 35
LV18 | 17.5 | 7875 | 75 | 67 | 125 | 172 | 0.651 | 13.16 | 111.9 |  | 35
LV18 | 17.5 | 7875 | 80 | 67 | 125 | 171.6 | 0.854 | 17.24 | 146.6 |  | 35
LV18 | 17.5 | 7875 | 85 | 67 | 125 | 174.6 | 0.971 | 19.94 | 169.6 |  | 35
LV18 | 17.5 | 7875 | 90 | 67 | 125 | 184.4 | 0.971 | 21.06 | 179.1 |  | 35
LV18 | 17.5 | 7875 | 75 | 72 | 125 | 186.9 | 0.428 | 9.39 | 79.9 |  | 35
LV18 | 17.5 | 7875 | 80 | 72 | 125 | 186.8 | 0.602 | 13.23 | 112.5 |  | 35
LV18 | 17.5 | 7875 | 85 | 72 | 125 | 185.8 | 0.787 | 17.19 | 146.2 |  | 35
LV18 | 17.5 | 7875 | 90 | 72 | 125 | 184.4 | 0.971 | 21.06 | 179.1 |  | 35
LV18 | 17.5 | 7875 | 80 | 77 | 125 | 203 | 0.389 | 9.28 | 78.9 |  | 35
LV18 | 17.5 | 7875 | 85 | 77 | 125 | 203.3 | 0.553 | 13.23 | 112.5 |  | 35
LV18 | 17.5 | 7875 | 90 | 77 | 125 | 200.8 | 0.729 | 17.2 | 146.3 |  | 35
LV18 | 17.5 | 8750 | 65 | 57 | 75 | 208.9 | 0.719 | 15.88 | 150.1 |  | 33
LV18 | 17.5 | 8750 | 70 | 57 | 75 | 209.9 | 0.903 | 20.06 | 189.6 |  | 33
LV18 | 17.5 | 8750 | 75 | 57 | 75 | 218.2 | 0.971 | 22.42 | 211.9 |  | 33
LV18 | 17.5 | 8750 | 80 | 57 | 75 | 231.3 | 0.971 | 23.77 | 224.6 |  | 33
LV18 | 17.5 | 8750 | 85 | 57 | 75 | 244 | 0.971 | 25.07 | 236.9 |  | 33
LV18 | 17.5 | 8750 | 90 | 57 | 75 | 256.6 | 0.971 | 26.37 | 249.2 |  | 33
LV18 | 17.5 | 8750 | 65 | 62 | 75 | 227.1 | 0.495 | 11.9 | 112.5 |  | 33
LV18 | 17.5 | 8750 | 70 | 62 | 75 | 228.5 | 0.66 | 15.97 | 150.9 |  | 33
LV18 | 17.5 | 8750 | 75 | 62 | 75 | 229.1 | 0.835 | 20.24 | 191.3 |  | 33
LV18 | 17.5 | 8750 | 80 | 62 | 75 | 231.1 | 0.971 | 23.75 | 224.4 |  | 33
LV18 | 17.5 | 8750 | 85 | 62 | 75 | 243.9 | 0.971 | 25.07 | 236.9 |  | 33
LV18 | 17.5 | 8750 | 90 | 62 | 75 | 256.6 | 0.971 | 26.37 | 249.2 |  | 33
LV18 | 17.5 | 8750 | 70 | 67 | 75 | 247.5 | 0.446 | 11.69 | 110.5 |  | 33
LV18 | 17.5 | 8750 | 75 | 67 | 75 | 247.5 | 0.612 | 16.03 | 151.5 |  | 33
LV18 | 17.5 | 8750 | 80 | 67 | 75 | 247.9 | 0.767 | 20.13 | 190.2 |  | 33
LV18 | 17.5 | 8750 | 85 | 67 | 75 | 247.5 | 0.932 | 24.41 | 230.7 |  | 33
LV18 | 17.5 | 8750 | 90 | 67 | 75 | 256.7 | 0.971 | 26.37 | 249.2 |  | 33
LV18 | 17.5 | 8750 | 75 | 72 | 75 | 267.1 | 0.408 | 11.52 | 108.9 |  | 33
LV18 | 17.5 | 8750 | 80 | 72 | 75 | 267.3 | 0.563 | 15.94 | 150.6 |  | 33
LV18 | 17.5 | 8750 | 85 | 72 | 75 | 267.5 | 0.709 | 20.06 | 189.6 |  | 33
LV18 | 17.5 | 8750 | 90 | 72 | 75 | 267.2 | 0.864 | 24.43 | 230.9 |  | 33
LV18 | 17.5 | 8750 | 80 | 77 | 75 | 289 | 0.379 | 11.58 | 109.4 |  | 33
LV18 | 17.5 | 8750 | 85 | 77 | 75 | 287.5 | 0.515 | 15.66 | 148 |  | 33
LV18 | 17.5 | 8750 | 90 | 77 | 75 | 287.1 | 0.66 | 20.06 | 189.6 |  | 33
LV18 | 17.5 | 8750 | 65 | 57 | 85 | 196.8 | 0.729 | 15.17 | 143.4 |  | 33
LV18 | 17.5 | 8750 | 70 | 57 | 85 | 197.5 | 0.933 | 19.49 | 184.2 |  | 33
LV18 | 17.5 | 8750 | 75 | 57 | 85 | 207.5 | 0.971 | 21.32 | 201.5 |  | 33
LV18 | 17.5 | 8750 | 80 | 57 | 85 | 220.1 | 0.971 | 22.61 | 213.7 |  | 33
LV18 | 17.5 | 8750 | 85 | 57 | 85 | 232.4 | 0.971 | 23.88 | 225.7 |  | 33
LV18 | 17.5 | 8750 | 90 | 57 | 85 | 244.5 | 0.971 | 25.13 | 237.5 |  | 33
LV18 | 17.5 | 8750 | 65 | 62 | 85 | 214.4 | 0.495 | 11.24 | 106.2 |  | 33
LV18 | 17.5 | 8750 | 70 | 62 | 85 | 215.6 | 0.67 | 15.29 | 144.5 |  | 33
LV18 | 17.5 | 8750 | 75 | 62 | 85 | 216.2 | 0.855 | 19.56 | 184.8 |  | 33
LV18 | 17.5 | 8750 | 80 | 62 | 85 | 219.9 | 0.971 | 22.6 | 213.6 |  | 33
LV18 | 17.5 | 8750 | 85 | 62 | 85 | 232.3 | 0.971 | 23.87 | 225.6 |  | 33
LV18 | 17.5 | 8750 | 90 | 62 | 85 | 244.6 | 0.971 | 25.13 | 237.5 |  | 33
LV18 | 17.5 | 8750 | 70 | 67 | 85 | 233.4 | 0.456 | 11.27 | 106.5 |  | 33
LV18 | 17.5 | 8750 | 75 | 67 | 85 | 234 | 0.621 | 15.39 | 145.4 |  | 33
LV18 | 17.5 | 8750 | 80 | 67 | 85 | 234.4 | 0.787 | 19.51 | 184.4 |  | 33
LV18 | 17.5 | 8750 | 85 | 67 | 85 | 233.1 | 0.961 | 23.71 | 224.1 |  | 33
LV18 | 17.5 | 8750 | 90 | 67 | 85 | 244.5 | 0.971 | 25.13 | 237.5 |  | 33
LV18 | 17.5 | 8750 | 75 | 72 | 85 | 252.7 | 0.417 | 11.16 | 105.5 |  | 33
LV18 | 17.5 | 8750 | 80 | 72 | 85 | 253.1 | 0.573 | 15.34 | 145 |  | 33
LV18 | 17.5 | 8750 | 85 | 72 | 85 | 253.1 | 0.729 | 19.51 | 184.4 |  | 33
LV18 | 17.5 | 8750 | 90 | 72 | 85 | 252.5 | 0.884 | 23.61 | 223.1 |  | 33
LV18 | 17.5 | 8750 | 80 | 77 | 85 | 272.7 | 0.379 | 10.93 | 103.3 |  | 33
LV18 | 17.5 | 8750 | 85 | 77 | 85 | 272.2 | 0.524 | 15.1 | 142.7 |  | 33
LV18 | 17.5 | 8750 | 90 | 77 | 85 | 271.7 | 0.67 | 19.27 | 182.1 |  | 33
LV18 | 17.5 | 8750 | 65 | 57 | 95 | 184.3 | 0.748 | 14.58 | 137.8 |  | 34
LV18 | 17.5 | 8750 | 70 | 57 | 95 | 184.6 | 0.952 | 18.59 | 175.7 |  | 34
LV18 | 17.5 | 8750 | 75 | 57 | 95 | 195.9 | 0.971 | 20.13 | 190.2 |  | 34
LV18 | 17.5 | 8750 | 80 | 57 | 95 | 207.9 | 0.971 | 21.37 | 201.9 |  | 34
LV18 | 17.5 | 8750 | 85 | 57 | 95 | 220.1 | 0.971 | 22.62 | 213.8 |  | 34
LV18 | 17.5 | 8750 | 90 | 57 | 95 | 231.6 | 0.972 | 23.81 | 225 |  | 34
LV18 | 17.5 | 8750 | 65 | 62 | 95 | 200.9 | 0.495 | 10.53 | 99.5 |  | 34
LV18 | 17.5 | 8750 | 70 | 62 | 95 | 201.7 | 0.69 | 14.72 | 139.1 |  | 34
LV18 | 17.5 | 8750 | 75 | 62 | 95 | 202.6 | 0.874 | 18.74 | 177.1 |  | 34
LV18 | 17.5 | 8750 | 80 | 62 | 95 | 208 | 0.971 | 21.38 | 202 |  | 34
LV18 | 17.5 | 8750 | 85 | 62 | 95 | 220.3 | 0.971 | 22.63 | 213.9 |  | 34
LV18 | 17.5 | 8750 | 90 | 62 | 95 | 231.7 | 0.971 | 23.81 | 225 |  | 34
LV18 | 17.5 | 8750 | 70 | 67 | 95 | 219.1 | 0.456 | 10.58 | 100 |  | 34
LV18 | 17.5 | 8750 | 75 | 67 | 95 | 219.6 | 0.631 | 14.67 | 138.6 |  | 34
LV18 | 17.5 | 8750 | 80 | 67 | 95 | 219.7 | 0.806 | 18.74 | 177.1 |  | 34
LV18 | 17.5 | 8750 | 85 | 67 | 95 | 219.9 | 0.971 | 22.59 | 213.5 |  | 34
LV18 | 17.5 | 8750 | 90 | 67 | 95 | 231.7 | 0.972 | 23.82 | 225.1 |  | 34
LV18 | 17.5 | 8750 | 75 | 72 | 95 | 237.8 | 0.418 | 10.51 | 99.3 |  | 34
LV18 | 17.5 | 8750 | 80 | 72 | 95 | 237.8 | 0.583 | 14.67 | 138.6 |  | 34
LV18 | 17.5 | 8750 | 85 | 72 | 95 | 237.7 | 0.748 | 18.81 | 177.8 |  | 34
LV18 | 17.5 | 8750 | 90 | 72 | 95 | 237 | 0.913 | 22.9 | 216.4 |  | 34
LV18 | 17.5 | 8750 | 80 | 77 | 95 | 256.7 | 0.379 | 10.29 | 97.2 |  | 34
LV18 | 17.5 | 8750 | 85 | 77 | 95 | 256.1 | 0.534 | 14.48 | 136.8 |  | 34
LV18 | 17.5 | 8750 | 90 | 77 | 95 | 255.4 | 0.69 | 18.63 | 176.1 |  | 34
LV18 | 17.5 | 8750 | 65 | 57 | 105 | 171 | 0.758 | 13.71 | 129.6 |  | 34
LV18 | 17.5 | 8750 | 70 | 57 | 105 | 171.7 | 0.971 | 17.64 | 166.7 |  | 34
LV18 | 17.5 | 8750 | 75 | 57 | 105 | 183.6 | 0.971 | 18.87 | 178.3 |  | 34
LV18 | 17.5 | 8750 | 80 | 57 | 105 | 195.1 | 0.971 | 20.05 | 189.5 |  | 34
LV18 | 17.5 | 8750 | 85 | 57 | 105 | 206.7 | 0.971 | 21.25 | 200.8 |  | 34
LV18 | 17.5 | 8750 | 90 | 57 | 105 | 218.1 | 0.971 | 22.41 | 211.8 |  | 34
LV18 | 17.5 | 8750 | 65 | 62 | 105 | 186.8 | 0.505 | 9.99 | 94.4 |  | 34
LV18 | 17.5 | 8750 | 70 | 62 | 105 | 187.8 | 0.699 | 13.89 | 131.3 |  | 34
LV18 | 17.5 | 8750 | 75 | 62 | 105 | 187.9 | 0.903 | 17.96 | 169.7 |  | 34
LV18 | 17.5 | 8750 | 80 | 62 | 105 | 195.2 | 0.971 | 20.06 | 189.6 |  | 34
LV18 | 17.5 | 8750 | 85 | 62 | 105 | 206.7 | 0.971 | 21.24 | 200.7 |  | 34
LV18 | 17.5 | 8750 | 90 | 62 | 105 | 218.1 | 0.971 | 22.41 | 211.8 |  | 34
LV18 | 17.5 | 8750 | 70 | 67 | 105 | 204.1 | 0.457 | 9.86 | 93.2 |  | 34
LV18 | 17.5 | 8750 | 75 | 67 | 105 | 204.6 | 0.641 | 13.88 | 131.2 |  | 34
LV18 | 17.5 | 8750 | 80 | 67 | 105 | 204.6 | 0.835 | 18.08 | 170.9 |  | 34
LV18 | 17.5 | 8750 | 85 | 67 | 105 | 206.7 | 0.971 | 21.24 | 200.7 |  | 34
LV18 | 17.5 | 8750 | 90 | 67 | 105 | 218.2 | 0.971 | 22.42 | 211.9 |  | 34
LV18 | 17.5 | 8750 | 75 | 72 | 105 | 222 | 0.418 | 9.81 | 92.7 |  | 34
LV18 | 17.5 | 8750 | 80 | 72 | 105 | 221.9 | 0.592 | 13.9 | 131.4 |  | 34
LV18 | 17.5 | 8750 | 85 | 72 | 105 | 221.5 | 0.767 | 17.98 | 169.9 |  | 34
LV18 | 17.5 | 8750 | 90 | 72 | 105 | 219.2 | 0.952 | 22.07 | 208.6 |  | 34
LV18 | 17.5 | 8750 | 80 | 77 | 105 | 239.9 | 0.388 | 9.86 | 93.2 |  | 34
LV18 | 17.5 | 8750 | 85 | 77 | 105 | 238.9 | 0.544 | 13.75 | 129.9 |  | 34
LV18 | 17.5 | 8750 | 90 | 77 | 105 | 238.2 | 0.709 | 17.87 | 168.9 |  | 34
LV18 | 17.5 | 8750 | 65 | 57 | 115 | 156.9 | 0.777 | 12.9 | 121.9 |  | 35
LV18 | 17.5 | 8750 | 70 | 57 | 115 | 159.2 | 0.971 | 16.36 | 154.6 |  | 35
LV18 | 17.5 | 8750 | 75 | 57 | 115 | 170.6 | 0.971 | 17.53 | 165.7 |  | 35
LV18 | 17.5 | 8750 | 80 | 57 | 115 | 181.8 | 0.971 | 18.69 | 176.6 |  | 35
LV18 | 17.5 | 8750 | 85 | 57 | 115 | 192.9 | 0.971 | 19.82 | 187.3 |  | 35
LV18 | 17.5 | 8750 | 90 | 57 | 115 | 203.6 | 0.972 | 20.93 | 197.8 |  | 35
LV18 | 17.5 | 8750 | 65 | 62 | 115 | 172 | 0.505 | 9.2 | 86.9 |  | 35
LV18 | 17.5 | 8750 | 70 | 62 | 115 | 172.9 | 0.719 | 13.15 | 124.3 |  | 35
LV18 | 17.5 | 8750 | 75 | 62 | 115 | 172.5 | 0.932 | 17.02 | 160.8 |  | 35
LV18 | 17.5 | 8750 | 80 | 62 | 115 | 181.9 | 0.971 | 18.69 | 176.6 |  | 35
LV18 | 17.5 | 8750 | 85 | 62 | 115 | 192.8 | 0.971 | 19.81 | 187.2 |  | 35
LV18 | 17.5 | 8750 | 90 | 62 | 115 | 203.7 | 0.971 | 20.93 | 197.8 |  | 35
LV18 | 17.5 | 8750 | 70 | 67 | 115 | 188.7 | 0.466 | 9.31 | 88 |  | 35
LV18 | 17.5 | 8750 | 75 | 67 | 115 | 188.9 | 0.66 | 13.2 | 124.7 |  | 35
LV18 | 17.5 | 8750 | 80 | 67 | 115 | 188.8 | 0.854 | 17.07 | 161.3 |  | 35
LV18 | 17.5 | 8750 | 85 | 67 | 115 | 192.7 | 0.971 | 19.8 | 187.1 |  | 35
LV18 | 17.5 | 8750 | 90 | 67 | 115 | 203.6 | 0.971 | 20.92 | 197.7 |  | 35
LV18 | 17.5 | 8750 | 75 | 72 | 115 | 205.4 | 0.427 | 9.29 | 87.8 |  | 35
LV18 | 17.5 | 8750 | 80 | 72 | 115 | 205.1 | 0.612 | 13.28 | 125.5 |  | 35
LV18 | 17.5 | 8750 | 85 | 72 | 115 | 204.6 | 0.796 | 17.24 | 162.9 |  | 35
LV18 | 17.5 | 8750 | 90 | 72 | 115 | 203.5 | 0.971 | 20.92 | 197.7 |  | 35
LV18 | 17.5 | 8750 | 80 | 77 | 115 | 222.4 | 0.388 | 9.14 | 86.4 |  | 35
LV18 | 17.5 | 8750 | 85 | 77 | 115 | 221.2 | 0.563 | 13.19 | 124.6 |  | 35
LV18 | 17.5 | 8750 | 90 | 77 | 115 | 220.2 | 0.738 | 17.2 | 162.5 |  | 35
LV18 | 17.5 | 8750 | 65 | 57 | 125 | 142.4 | 0.806 | 12.15 | 114.8 |  | 35
LV18 | 17.5 | 8750 | 70 | 57 | 125 | 146.2 | 0.971 | 15.03 | 142 |  | 35
LV18 | 17.5 | 8750 | 75 | 57 | 125 | 157.1 | 0.971 | 16.14 | 152.5 |  | 35
LV18 | 17.5 | 8750 | 80 | 57 | 125 | 167.8 | 0.971 | 17.25 | 163 |  | 35
LV18 | 17.5 | 8750 | 85 | 57 | 125 | 178.3 | 0.971 | 18.32 | 173.1 |  | 35
LV18 | 17.5 | 8750 | 90 | 57 | 125 | 188.6 | 0.971 | 19.38 | 183.1 |  | 35
LV18 | 17.5 | 8750 | 65 | 62 | 125 | 156.9 | 0.514 | 8.54 | 80.7 |  | 35
LV18 | 17.5 | 8750 | 70 | 62 | 125 | 157.6 | 0.738 | 12.31 | 116.3 |  | 35
LV18 | 17.5 | 8750 | 75 | 62 | 125 | 157 | 0.971 | 16.13 | 152.4 |  | 35
LV18 | 17.5 | 8750 | 80 | 62 | 125 | 167.7 | 0.971 | 17.23 | 162.8 |  | 35
LV18 | 17.5 | 8750 | 85 | 62 | 125 | 178.2 | 0.971 | 18.31 | 173 |  | 35
LV18 | 17.5 | 8750 | 90 | 62 | 125 | 188.5 | 0.971 | 19.38 | 183.1 |  | 35
LV18 | 17.5 | 8750 | 70 | 67 | 125 | 172.4 | 0.466 | 8.51 | 80.4 |  | 35
LV18 | 17.5 | 8750 | 75 | 67 | 125 | 172.5 | 0.68 | 12.41 | 117.3 |  | 35
LV18 | 17.5 | 8750 | 80 | 67 | 125 | 171.9 | 0.894 | 16.25 | 153.6 |  | 35
LV18 | 17.5 | 8750 | 85 | 67 | 125 | 178.2 | 0.971 | 18.32 | 173.1 |  | 35
LV18 | 17.5 | 8750 | 90 | 67 | 125 | 188.4 | 0.971 | 19.37 | 183 |  | 35
LV18 | 17.5 | 8750 | 75 | 72 | 125 | 188.3 | 0.428 | 8.52 | 80.5 |  | 35
LV18 | 17.5 | 8750 | 80 | 72 | 125 | 187.8 | 0.621 | 12.35 | 116.7 |  | 35
LV18 | 17.5 | 8750 | 85 | 72 | 125 | 186.8 | 0.825 | 16.32 | 154.2 |  | 35
LV18 | 17.5 | 8750 | 90 | 72 | 125 | 188.4 | 0.971 | 19.37 | 183 |  | 35
LV18 | 17.5 | 8750 | 80 | 77 | 125 | 204 | 0.398 | 8.59 | 81.2 |  | 35
LV18 | 17.5 | 8750 | 85 | 77 | 125 | 202.8 | 0.583 | 12.51 | 118.2 |  | 35
LV18 | 17.5 | 8750 | 90 | 77 | 125 | 201.5 | 0.767 | 16.36 | 154.6 |  | 35
LV20 | 20 | 5000 | 65 | 57 | 75 | 212.1 | 0.588 | 23.11 | 124.8 |  | 36
LV20 | 20 | 5000 | 70 | 57 | 75 | 213.2 | 0.688 | 27.15 | 146.6 |  | 36
LV20 | 20 | 5000 | 75 | 57 | 75 | 214.4 | 0.796 | 31.61 | 170.7 |  | 36
LV20 | 20 | 5000 | 80 | 57 | 75 | 215.2 | 0.896 | 35.7 | 192.8 |  | 36
LV20 | 20 | 5000 | 85 | 57 | 75 | 225.5 | 0.905 | 37.78 | 204 |  | 36
LV20 | 20 | 5000 | 90 | 57 | 75 | 237 | 0.905 | 39.7 | 214.4 |  | 36
LV20 | 20 | 5000 | 65 | 62 | 75 | 232 | 0.444 | 19.06 | 102.9 |  | 36
LV20 | 20 | 5000 | 70 | 62 | 75 | 233.1 | 0.543 | 23.43 | 126.5 |  | 36
LV20 | 20 | 5000 | 75 | 62 | 75 | 234.1 | 0.633 | 27.46 | 148.3 |  | 36
LV20 | 20 | 5000 | 80 | 62 | 75 | 235.3 | 0.724 | 31.56 | 170.4 |  | 36
LV20 | 20 | 5000 | 85 | 62 | 75 | 236.1 | 0.824 | 36.02 | 194.5 |  | 36
LV20 | 20 | 5000 | 90 | 62 | 75 | 237.1 | 0.905 | 39.74 | 214.6 |  | 36
LV20 | 20 | 5000 | 70 | 67 | 75 | 254.4 | 0.407 | 19.19 | 103.6 |  | 36
LV20 | 20 | 5000 | 75 | 67 | 75 | 255.3 | 0.489 | 23.11 | 124.8 |  | 36
LV20 | 20 | 5000 | 80 | 67 | 75 | 256.4 | 0.579 | 27.5 | 148.5 |  | 36
LV20 | 20 | 5000 | 85 | 67 | 75 | 257.1 | 0.67 | 31.89 | 172.2 |  | 36
LV20 | 20 | 5000 | 90 | 67 | 75 | 257.8 | 0.751 | 35.85 | 193.6 |  | 36
LV20 | 20 | 5000 | 75 | 72 | 75 | 277.7 | 0.371 | 19.07 | 103 |  | 36
LV20 | 20 | 5000 | 80 | 72 | 75 | 278.5 | 0.452 | 23.33 | 126 |  | 36
LV20 | 20 | 5000 | 85 | 72 | 75 | 279.1 | 0.534 | 27.59 | 149 |  | 36
LV20 | 20 | 5000 | 90 | 72 | 75 | 279.7 | 0.606 | 31.41 | 169.6 |  | 36
LV20 | 20 | 5000 | 80 | 77 | 75 | 302 | 0.335 | 18.72 | 101.1 |  | 36
LV20 | 20 | 5000 | 85 | 77 | 75 | 302.4 | 0.407 | 22.8 | 123.1 |  | 36
LV20 | 20 | 5000 | 90 | 77 | 75 | 303 | 0.488 | 27.41 | 148 |  | 36
LV20 | 20 | 5000 | 65 | 57 | 85 | 202.7 | 0.588 | 22.07 | 119.2 |  | 36
LV20 | 20 | 5000 | 70 | 57 | 85 | 203.8 | 0.697 | 26.3 | 142 |  | 36
LV20 | 20 | 5000 | 75 | 57 | 85 | 204.8 | 0.805 | 30.54 | 164.9 |  | 36
LV20 | 20 | 5000 | 80 | 57 | 85 | 205.9 | 0.905 | 34.5 | 186.3 |  | 36
LV20 | 20 | 5000 | 85 | 57 | 85 | 217.3 | 0.905 | 36.43 | 196.7 |  | 36
LV20 | 20 | 5000 | 90 | 57 | 85 | 228.8 | 0.905 | 38.35 | 207.1 |  | 36
LV20 | 20 | 5000 | 65 | 62 | 85 | 221.9 | 0.443 | 18.22 | 98.4 |  | 36
LV20 | 20 | 5000 | 70 | 62 | 85 | 223.1 | 0.543 | 22.44 | 121.2 |  | 36
LV20 | 20 | 5000 | 75 | 62 | 85 | 224.2 | 0.643 | 26.69 | 144.1 |  | 36
LV20 | 20 | 5000 | 80 | 62 | 85 | 225.3 | 0.733 | 30.57 | 165.1 |  | 36
LV20 | 20 | 5000 | 85 | 62 | 85 | 226.1 | 0.832 | 34.85 | 188.2 |  | 36
LV20 | 20 | 5000 | 90 | 62 | 85 | 228.9 | 0.905 | 38.37 | 207.2 |  | 36
LV20 | 20 | 5000 | 70 | 67 | 85 | 243.5 | 0.407 | 18.37 | 99.2 |  | 36
LV20 | 20 | 5000 | 75 | 67 | 85 | 244.5 | 0.498 | 22.54 | 121.7 |  | 36
LV20 | 20 | 5000 | 80 | 67 | 85 | 245.5 | 0.588 | 26.74 | 144.4 |  | 36
LV20 | 20 | 5000 | 85 | 67 | 85 | 246.4 | 0.67 | 30.56 | 165 |  | 36
LV20 | 20 | 5000 | 90 | 67 | 85 | 247 | 0.76 | 34.78 | 187.8 |  | 36
LV20 | 20 | 5000 | 75 | 72 | 85 | 266.1 | 0.371 | 18.28 | 98.7 |  | 36
LV20 | 20 | 5000 | 80 | 72 | 85 | 267 | 0.452 | 22.37 | 120.8 |  | 36
LV20 | 20 | 5000 | 85 | 72 | 85 | 267.7 | 0.534 | 26.46 | 142.9 |  | 36
LV20 | 20 | 5000 | 90 | 72 | 85 | 268.3 | 0.615 | 30.57 | 165.1 |  | 36
LV20 | 20 | 5000 | 80 | 77 | 85 | 289.5 | 0.335 | 17.94 | 96.9 |  | 36
LV20 | 20 | 5000 | 85 | 77 | 85 | 290.3 | 0.416 | 22.37 | 120.8 |  | 36
LV20 | 20 | 5000 | 90 | 77 | 85 | 290.6 | 0.489 | 26.3 | 142 |  | 36
LV20 | 20 | 5000 | 65 | 57 | 95 | 192.8 | 0.598 | 21.33 | 115.2 |  | 37
LV20 | 20 | 5000 | 70 | 57 | 95 | 193.9 | 0.706 | 25.35 | 136.9 |  | 37
LV20 | 20 | 5000 | 75 | 57 | 95 | 194.9 | 0.815 | 29.41 | 158.8 |  | 37
LV20 | 20 | 5000 | 80 | 57 | 95 | 197.4 | 0.905 | 33.09 | 178.7 |  | 37
LV20 | 20 | 5000 | 85 | 57 | 95 | 208.7 | 0.905 | 34.98 | 188.9 |  | 37
LV20 | 20 | 5000 | 90 | 57 | 95 | 219.9 | 0.905 | 36.85 | 199 |  | 37
LV20 | 20 | 5000 | 65 | 62 | 95 | 211.2 | 0.444 | 17.35 | 93.7 |  | 37
LV20 | 20 | 5000 | 70 | 62 | 95 | 212.5 | 0.543 | 21.37 | 115.4 |  | 37
LV20 | 20 | 5000 | 75 | 62 | 95 | 213.6 | 0.642 | 25.41 | 137.2 |  | 37
LV20 | 20 | 5000 | 80 | 62 | 95 | 214.5 | 0.751 | 29.83 | 161.1 |  | 37
LV20 | 20 | 5000 | 85 | 62 | 95 | 215.1 | 0.851 | 33.89 | 183 |  | 37
LV20 | 20 | 5000 | 90 | 62 | 95 | 220.1 | 0.905 | 36.89 | 199.2 |  | 37
LV20 | 20 | 5000 | 70 | 67 | 95 | 231.9 | 0.407 | 17.48 | 94.4 |  | 37
LV20 | 20 | 5000 | 75 | 67 | 95 | 233 | 0.498 | 21.48 | 116 |  | 37
LV20 | 20 | 5000 | 80 | 67 | 95 | 233.9 | 0.588 | 25.48 | 137.6 |  | 37
LV20 | 20 | 5000 | 85 | 67 | 95 | 234.7 | 0.688 | 29.89 | 161.4 |  | 37
LV20 | 20 | 5000 | 90 | 67 | 95 | 235.4 | 0.778 | 33.93 | 183.2 |  | 37
LV20 | 20 | 5000 | 75 | 72 | 95 | 253.6 | 0.371 | 17.43 | 94.1 |  | 37
LV20 | 20 | 5000 | 80 | 72 | 95 | 254.5 | 0.453 | 21.33 | 115.2 |  | 37
LV20 | 20 | 5000 | 85 | 72 | 95 | 255.3 | 0.543 | 25.67 | 138.6 |  | 37
LV20 | 20 | 5000 | 90 | 72 | 95 | 255.8 | 0.625 | 29.59 | 159.8 |  | 37
LV20 | 20 | 5000 | 80 | 77 | 95 | 276.3 | 0.335 | 17.13 | 92.5 |  | 37
LV20 | 20 | 5000 | 85 | 77 | 95 | 277 | 0.416 | 21.35 | 115.3 |  | 37
LV20 | 20 | 5000 | 90 | 77 | 95 | 277.5 | 0.498 | 25.57 | 138.1 |  | 37
LV20 | 20 | 5000 | 65 | 57 | 105 | 182.4 | 0.597 | 20.17 | 108.9 |  | 37
LV20 | 20 | 5000 | 70 | 57 | 105 | 183.5 | 0.715 | 24.3 | 131.2 |  | 37
LV20 | 20 | 5000 | 75 | 57 | 105 | 184.4 | 0.832 | 28.43 | 153.5 |  | 37
LV20 | 20 | 5000 | 80 | 57 | 105 | 188.5 | 0.905 | 31.59 | 170.6 |  | 37
LV20 | 20 | 5000 | 85 | 57 | 105 | 199.5 | 0.905 | 33.43 | 180.5 |  | 37
LV20 | 20 | 5000 | 90 | 57 | 105 | 210.4 | 0.905 | 35.26 | 190.4 |  | 37
LV20 | 20 | 5000 | 65 | 62 | 105 | 199.9 | 0.443 | 16.41 | 88.6 |  | 37
LV20 | 20 | 5000 | 70 | 62 | 105 | 201.1 | 0.552 | 20.56 | 111 |  | 37
LV20 | 20 | 5000 | 75 | 62 | 105 | 202.2 | 0.652 | 24.41 | 131.8 |  | 37
LV20 | 20 | 5000 | 80 | 62 | 105 | 203.1 | 0.76 | 28.59 | 154.4 |  | 37
LV20 | 20 | 5000 | 85 | 62 | 105 | 203.3 | 0.869 | 32.7 | 176.6 |  | 37
LV20 | 20 | 5000 | 90 | 62 | 105 | 210.5 | 0.905 | 35.28 | 190.5 |  | 37
LV20 | 20 | 5000 | 70 | 67 | 105 | 219.8 | 0.407 | 16.57 | 89.5 |  | 37
LV20 | 20 | 5000 | 75 | 67 | 105 | 220.8 | 0.507 | 20.72 | 111.9 |  | 37
LV20 | 20 | 5000 | 80 | 67 | 105 | 221.7 | 0.597 | 24.52 | 132.4 |  | 37
LV20 | 20 | 5000 | 85 | 67 | 105 | 222.4 | 0.697 | 28.7 | 155 |  | 37
LV20 | 20 | 5000 | 90 | 67 | 105 | 223.1 | 0.797 | 32.91 | 177.7 |  | 37
LV20 | 20 | 5000 | 75 | 72 | 105 | 240.6 | 0.371 | 16.54 | 89.3 |  | 37
LV20 | 20 | 5000 | 80 | 72 | 105 | 241.3 | 0.462 | 20.63 | 111.4 |  | 37
LV20 | 20 | 5000 | 85 | 72 | 105 | 242 | 0.552 | 24.74 | 133.6 |  | 37
LV20 | 20 | 5000 | 90 | 72 | 105 | 242.5 | 0.642 | 28.85 | 155.8 |  | 37
LV20 | 20 | 5000 | 80 | 77 | 105 | 262 | 0.335 | 16.24 | 87.7 |  | 37
LV20 | 20 | 5000 | 85 | 77 | 105 | 262.7 | 0.416 | 20.26 | 109.4 |  | 37
LV20 | 20 | 5000 | 90 | 77 | 105 | 263.1 | 0.507 | 24.69 | 133.3 |  | 37
LV20 | 20 | 5000 | 65 | 57 | 115 | 171.2 | 0.606 | 19.22 | 103.8 |  | 38
LV20 | 20 | 5000 | 70 | 57 | 115 | 172.5 | 0.724 | 23.13 | 124.9 |  | 38
LV20 | 20 | 5000 | 75 | 57 | 115 | 173.2 | 0.85 | 27.28 | 147.3 |  | 38
LV20 | 20 | 5000 | 80 | 57 | 115 | 179.1 | 0.905 | 30.02 | 162.1 |  | 38
LV20 | 20 | 5000 | 85 | 57 | 115 | 189.6 | 0.905 | 31.78 | 171.6 |  | 38
LV20 | 20 | 5000 | 90 | 57 | 115 | 200.3 | 0.905 | 33.57 | 181.3 |  | 38
LV20 | 20 | 5000 | 65 | 62 | 115 | 187.9 | 0.443 | 15.43 | 83.3 |  | 38
LV20 | 20 | 5000 | 70 | 62 | 115 | 189.2 | 0.552 | 19.33 | 104.4 |  | 38
LV20 | 20 | 5000 | 75 | 62 | 115 | 190.3 | 0.669 | 23.59 | 127.4 |  | 38
LV20 | 20 | 5000 | 80 | 62 | 115 | 191.1 | 0.778 | 27.54 | 148.7 |  | 38
LV20 | 20 | 5000 | 85 | 62 | 115 | 191.3 | 0.887 | 31.43 | 169.7 |  | 38
LV20 | 20 | 5000 | 90 | 62 | 115 | 200.3 | 0.905 | 33.57 | 181.3 |  | 38
LV20 | 20 | 5000 | 70 | 67 | 115 | 206.8 | 0.407 | 15.59 | 84.2 |  | 38
LV20 | 20 | 5000 | 75 | 67 | 115 | 207.9 | 0.507 | 19.52 | 105.4 |  | 38
LV20 | 20 | 5000 | 80 | 67 | 115 | 208.7 | 0.607 | 23.44 | 126.6 |  | 38
LV20 | 20 | 5000 | 85 | 67 | 115 | 209.3 | 0.715 | 27.72 | 149.7 |  | 38
LV20 | 20 | 5000 | 90 | 67 | 115 | 209.8 | 0.815 | 31.65 | 170.9 |  | 38
LV20 | 20 | 5000 | 75 | 72 | 115 | 226.6 | 0.371 | 15.57 | 84.1 |  | 38
LV20 | 20 | 5000 | 80 | 72 | 115 | 227.3 | 0.462 | 19.43 | 104.9 |  | 38
LV20 | 20 | 5000 | 85 | 72 | 115 | 227.8 | 0.561 | 23.67 | 127.8 |  | 38
LV20 | 20 | 5000 | 90 | 72 | 115 | 228.3 | 0.652 | 27.56 | 148.8 |  | 38
LV20 | 20 | 5000 | 80 | 77 | 115 | 246.9 | 0.335 | 15.31 | 82.7 |  | 38
LV20 | 20 | 5000 | 85 | 77 | 115 | 247.6 | 0.425 | 19.5 | 105.3 |  | 38
LV20 | 20 | 5000 | 90 | 77 | 115 | 248 | 0.516 | 23.69 | 127.9 |  | 38
LV20 | 20 | 5000 | 65 | 57 | 125 | 159.6 | 0.615 | 18.19 | 98.2 |  | 38
LV20 | 20 | 5000 | 70 | 57 | 125 | 160.7 | 0.742 | 22.07 | 119.2 |  | 38
LV20 | 20 | 5000 | 75 | 57 | 125 | 161 | 0.878 | 26.17 | 141.3 |  | 38
LV20 | 20 | 5000 | 80 | 57 | 125 | 169 | 0.905 | 28.31 | 152.9 |  | 38
LV20 | 20 | 5000 | 85 | 57 | 125 | 179.1 | 0.905 | 30.02 | 162.1 |  | 38
LV20 | 20 | 5000 | 90 | 57 | 125 | 189.3 | 0.905 | 31.72 | 171.3 |  | 38
LV20 | 20 | 5000 | 65 | 62 | 125 | 175.4 | 0.444 | 14.41 | 77.8 |  | 38
LV20 | 20 | 5000 | 70 | 62 | 125 | 176.6 | 0.561 | 18.35 | 99.1 |  | 38
LV20 | 20 | 5000 | 75 | 62 | 125 | 177.5 | 0.679 | 22.31 | 120.5 |  | 38
LV20 | 20 | 5000 | 80 | 62 | 125 | 178.3 | 0.796 | 26.3 | 142 |  | 38
LV20 | 20 | 5000 | 85 | 62 | 125 | 179.2 | 0.905 | 30.04 | 162.2 |  | 38
LV20 | 20 | 5000 | 90 | 62 | 125 | 189.4 | 0.905 | 31.74 | 171.4 |  | 38
LV20 | 20 | 5000 | 70 | 67 | 125 | 193.2 | 0.407 | 14.57 | 78.7 |  | 38
LV20 | 20 | 5000 | 75 | 67 | 125 | 194.2 | 0.516 | 18.56 | 100.2 |  | 38
LV20 | 20 | 5000 | 80 | 67 | 125 | 194.9 | 0.624 | 22.54 | 121.7 |  | 38
LV20 | 20 | 5000 | 85 | 67 | 125 | 195.5 | 0.733 | 26.54 | 143.3 |  | 38
LV20 | 20 | 5000 | 90 | 67 | 125 | 195.7 | 0.842 | 30.5 | 164.7 |  | 38
LV20 | 20 | 5000 | 75 | 72 | 125 | 211.7 | 0.371 | 14.56 | 78.6 |  | 38
LV20 | 20 | 5000 | 80 | 72 | 125 | 212.4 | 0.47 | 18.5 | 99.9 |  | 38
LV20 | 20 | 5000 | 85 | 72 | 125 | 212.9 | 0.57 | 22.48 | 121.4 |  | 38
LV20 | 20 | 5000 | 90 | 72 | 125 | 213.4 | 0.67 | 26.46 | 142.9 |  | 38
LV20 | 20 | 5000 | 80 | 77 | 125 | 231.1 | 0.344 | 14.72 | 79.5 |  | 38
LV20 | 20 | 5000 | 85 | 77 | 125 | 231.4 | 0.434 | 18.61 | 100.5 |  | 38
LV20 | 20 | 5000 | 90 | 77 | 125 | 231.8 | 0.525 | 22.54 | 121.7 |  | 38
LV20 | 20 | 6000 | 65 | 57 | 75 | 222.4 | 0.597 | 20.49 | 132.8 |  | 36
LV20 | 20 | 6000 | 70 | 57 | 75 | 223.7 | 0.715 | 24.68 | 159.9 |  | 36
LV20 | 20 | 6000 | 75 | 57 | 75 | 224.7 | 0.832 | 28.86 | 187 |  | 36
LV20 | 20 | 6000 | 80 | 57 | 75 | 229.5 | 0.905 | 32.05 | 207.7 |  | 36
LV20 | 20 | 6000 | 85 | 57 | 75 | 242.3 | 0.905 | 33.84 | 219.3 |  | 36
LV20 | 20 | 6000 | 90 | 57 | 75 | 254.8 | 0.905 | 35.59 | 230.6 |  | 36
LV20 | 20 | 6000 | 65 | 62 | 75 | 242.6 | 0.444 | 16.6 | 107.6 |  | 36
LV20 | 20 | 6000 | 70 | 62 | 75 | 243.8 | 0.552 | 20.77 | 134.6 |  | 36
LV20 | 20 | 6000 | 75 | 62 | 75 | 245 | 0.66 | 24.97 | 161.8 |  | 36
LV20 | 20 | 6000 | 80 | 62 | 75 | 241.5 | 0.769 | 28.67 | 185.8 |  | 36
LV20 | 20 | 6000 | 85 | 62 | 75 | 246.7 | 0.869 | 33.07 | 214.3 |  | 36
LV20 | 20 | 6000 | 90 | 62 | 75 | 255 | 0.905 | 35.6 | 230.7 |  | 36
LV20 | 20 | 6000 | 70 | 67 | 75 | 265.4 | 0.407 | 16.68 | 108.1 |  | 36
LV20 | 20 | 6000 | 75 | 67 | 75 | 266.7 | 0.507 | 20.85 | 135.1 |  | 36
LV20 | 20 | 6000 | 80 | 67 | 75 | 267.7 | 0.597 | 24.68 | 159.9 |  | 36
LV20 | 20 | 6000 | 85 | 67 | 75 | 268.4 | 0.697 | 28.86 | 187 |  | 36
LV20 | 20 | 6000 | 90 | 67 | 75 | 269 | 0.796 | 33.06 | 214.2 |  | 36
LV20 | 20 | 6000 | 75 | 72 | 75 | 289.4 | 0.371 | 16.57 | 107.4 |  | 36
LV20 | 20 | 6000 | 80 | 72 | 75 | 290.5 | 0.462 | 20.69 | 134.1 |  | 36
LV20 | 20 | 6000 | 85 | 72 | 75 | 291 | 0.552 | 24.8 | 160.7 |  | 36
LV20 | 20 | 6000 | 90 | 72 | 75 | 291.6 | 0.643 | 28.92 | 187.4 |  | 36
LV20 | 20 | 6000 | 80 | 77 | 75 | 314.2 | 0.335 | 16.23 | 105.2 |  | 36
LV20 | 20 | 6000 | 85 | 77 | 75 | 314.4 | 0.425 | 20.63 | 133.7 |  | 36
LV20 | 20 | 6000 | 90 | 77 | 75 | 315.2 | 0.507 | 24.65 | 159.7 |  | 36
LV20 | 20 | 6000 | 65 | 57 | 85 | 211.8 | 0.606 | 19.81 | 128.4 |  | 36
LV20 | 20 | 6000 | 70 | 57 | 85 | 213.2 | 0.724 | 23.81 | 154.3 |  | 36
LV20 | 20 | 6000 | 75 | 57 | 85 | 214.3 | 0.842 | 27.84 | 180.4 |  | 36
LV20 | 20 | 6000 | 80 | 57 | 85 | 220.6 | 0.905 | 30.8 | 199.6 |  | 36
LV20 | 20 | 6000 | 85 | 57 | 85 | 233.2 | 0.905 | 32.56 | 211 |  | 36
LV20 | 20 | 6000 | 90 | 57 | 85 | 245.5 | 0.905 | 34.29 | 222.2 |  | 36
LV20 | 20 | 6000 | 65 | 62 | 85 | 231.5 | 0.443 | 15.83 | 102.6 |  | 36
LV20 | 20 | 6000 | 70 | 62 | 85 | 233 | 0.552 | 19.85 | 128.6 |  | 36
LV20 | 20 | 6000 | 75 | 62 | 85 | 234 | 0.661 | 23.86 | 154.6 |  | 36
LV20 | 20 | 6000 | 80 | 62 | 85 | 234.9 | 0.778 | 28.21 | 182.8 |  | 36
LV20 | 20 | 6000 | 85 | 62 | 85 | 235.6 | 0.887 | 32.24 | 208.9 |  | 36
LV20 | 20 | 6000 | 90 | 62 | 85 | 245.5 | 0.905 | 34.29 | 222.2 |  | 36
LV20 | 20 | 6000 | 70 | 67 | 85 | 253.6 | 0.407 | 15.94 | 103.3 |  | 36
LV20 | 20 | 6000 | 75 | 67 | 85 | 254.8 | 0.507 | 19.92 | 129.1 |  | 36
LV20 | 20 | 6000 | 80 | 67 | 85 | 255.8 | 0.606 | 23.94 | 155.1 |  | 36
LV20 | 20 | 6000 | 85 | 67 | 85 | 256.5 | 0.715 | 28.3 | 183.4 |  | 36
LV20 | 20 | 6000 | 90 | 67 | 85 | 257.2 | 0.815 | 32.33 | 209.5 |  | 36
LV20 | 20 | 6000 | 75 | 72 | 85 | 276.7 | 0.371 | 15.83 | 102.6 |  | 36
LV20 | 20 | 6000 | 80 | 72 | 85 | 277.8 | 0.461 | 19.78 | 128.2 |  | 36
LV20 | 20 | 6000 | 85 | 72 | 85 | 278.6 | 0.561 | 24.12 | 156.3 |  | 36
LV20 | 20 | 6000 | 90 | 72 | 85 | 279.2 | 0.652 | 28.09 | 182 |  | 36
LV20 | 20 | 6000 | 80 | 77 | 85 | 300.6 | 0.335 | 15.52 | 100.6 |  | 36
LV20 | 20 | 6000 | 85 | 77 | 85 | 301.3 | 0.425 | 19.77 | 128.1 |  | 36
LV20 | 20 | 6000 | 90 | 77 | 85 | 301.7 | 0.516 | 24.01 | 155.6 |  | 36
LV20 | 20 | 6000 | 65 | 57 | 95 | 201 | 0.606 | 18.81 | 121.9 |  | 37
LV20 | 20 | 6000 | 70 | 57 | 95 | 202.4 | 0.733 | 22.9 | 148.4 |  | 37
LV20 | 20 | 6000 | 75 | 57 | 95 | 203.2 | 0.86 | 26.96 | 174.7 |  | 37
LV20 | 20 | 6000 | 80 | 57 | 95 | 211.2 | 0.905 | 29.51 | 191.2 |  | 37
LV20 | 20 | 6000 | 85 | 57 | 95 | 223.4 | 0.905 | 31.19 | 202.1 |  | 37
LV20 | 20 | 6000 | 90 | 57 | 95 | 235.6 | 0.905 | 32.9 | 213.2 |  | 37
LV20 | 20 | 6000 | 65 | 62 | 95 | 219.6 | 0.444 | 15.03 | 97.4 |  | 37
LV20 | 20 | 6000 | 70 | 62 | 95 | 221.1 | 0.561 | 19.15 | 124.1 |  | 37
LV20 | 20 | 6000 | 75 | 62 | 95 | 222.3 | 0.679 | 23.29 | 150.9 |  | 37
LV20 | 20 | 6000 | 80 | 62 | 95 | 223.2 | 0.788 | 27.13 | 175.8 |  | 37
LV20 | 20 | 6000 | 85 | 62 | 95 | 224.2 | 0.896 | 31 | 200.9 |  | 37
LV20 | 20 | 6000 | 90 | 62 | 95 | 235.7 | 0.905 | 32.92 | 213.3 |  | 37
LV20 | 20 | 6000 | 70 | 67 | 95 | 241 | 0.407 | 15.14 | 98.1 |  | 37
LV20 | 20 | 6000 | 75 | 67 | 95 | 242.2 | 0.516 | 19.29 | 125 |  | 37
LV20 | 20 | 6000 | 80 | 67 | 95 | 243 | 0.616 | 23.09 | 149.6 |  | 37
LV20 | 20 | 6000 | 85 | 67 | 95 | 243.8 | 0.724 | 27.24 | 176.5 |  | 37
LV20 | 20 | 6000 | 90 | 67 | 95 | 244.6 | 0.832 | 31.42 | 203.6 |  | 37
LV20 | 20 | 6000 | 75 | 72 | 95 | 263.2 | 0.371 | 15.06 | 97.6 |  | 37
LV20 | 20 | 6000 | 80 | 72 | 95 | 264.1 | 0.471 | 19.18 | 124.3 |  | 37
LV20 | 20 | 6000 | 85 | 72 | 95 | 265.1 | 0.57 | 23.32 | 151.1 |  | 37
LV20 | 20 | 6000 | 90 | 72 | 95 | 265.8 | 0.661 | 27.1 | 175.6 |  | 37
LV20 | 20 | 6000 | 80 | 77 | 95 | 286.1 | 0.344 | 15.19 | 98.4 |  | 37
LV20 | 20 | 6000 | 85 | 77 | 95 | 286.9 | 0.425 | 18.83 | 122 |  | 37
LV20 | 20 | 6000 | 90 | 77 | 95 | 287.4 | 0.516 | 22.87 | 148.2 |  | 37
LV20 | 20 | 6000 | 65 | 57 | 105 | 189.5 | 0.615 | 17.99 | 116.6 |  | 37
LV20 | 20 | 6000 | 70 | 57 | 105 | 190.9 | 0.751 | 22.13 | 143.4 |  | 37
LV20 | 20 | 6000 | 75 | 57 | 105 | 191.5 | 0.878 | 25.94 | 168.1 |  | 37
LV20 | 20 | 6000 | 80 | 57 | 105 | 201.1 | 0.905 | 28.09 | 182 |  | 37
LV20 | 20 | 6000 | 85 | 57 | 105 | 213 | 0.905 | 29.75 | 192.8 |  | 37
LV20 | 20 | 6000 | 90 | 57 | 105 | 224.9 | 0.905 | 31.4 | 203.5 |  | 37
LV20 | 20 | 6000 | 65 | 62 | 105 | 207.2 | 0.444 | 14.18 | 91.9 |  | 37
LV20 | 20 | 6000 | 70 | 62 | 105 | 208.7 | 0.57 | 18.36 | 119 |  | 37
LV20 | 20 | 6000 | 75 | 62 | 105 | 209.9 | 0.687 | 22.27 | 144.3 |  | 37
LV20 | 20 | 6000 | 80 | 62 | 105 | 210.7 | 0.805 | 26.19 | 169.7 |  | 37
LV20 | 20 | 6000 | 85 | 62 | 105 | 213.1 | 0.905 | 29.77 | 192.9 |  | 37
LV20 | 20 | 6000 | 90 | 62 | 105 | 225.1 | 0.905 | 31.45 | 203.8 |  | 37
LV20 | 20 | 6000 | 70 | 67 | 105 | 227.7 | 0.407 | 14.31 | 92.7 |  | 37
LV20 | 20 | 6000 | 75 | 67 | 105 | 228.9 | 0.516 | 18.21 | 118 |  | 37
LV20 | 20 | 6000 | 80 | 67 | 105 | 229.7 | 0.624 | 22.13 | 143.4 |  | 37
LV20 | 20 | 6000 | 85 | 67 | 105 | 230.3 | 0.742 | 26.37 | 170.9 |  | 37
LV20 | 20 | 6000 | 90 | 67 | 105 | 231 | 0.851 | 30.32 | 196.5 |  | 37
LV20 | 20 | 6000 | 75 | 72 | 105 | 248.9 | 0.371 | 14.24 | 92.3 |  | 37
LV20 | 20 | 6000 | 80 | 72 | 105 | 249.9 | 0.471 | 18.15 | 117.6 |  | 37
LV20 | 20 | 6000 | 85 | 72 | 105 | 250.7 | 0.579 | 22.41 | 145.2 |  | 37
LV20 | 20 | 6000 | 90 | 72 | 105 | 251.4 | 0.679 | 26.33 | 170.6 |  | 37
LV20 | 20 | 6000 | 80 | 77 | 105 | 270.6 | 0.344 | 14.37 | 93.1 |  | 37
LV20 | 20 | 6000 | 85 | 77 | 105 | 271.4 | 0.434 | 18.19 | 117.9 |  | 37
LV20 | 20 | 6000 | 90 | 77 | 105 | 272.3 | 0.525 | 22.05 | 142.9 |  | 37
LV20 | 20 | 6000 | 65 | 57 | 115 | 177.4 | 0.625 | 17.1 | 110.8 |  | 38
LV20 | 20 | 6000 | 70 | 57 | 115 | 178.6 | 0.76 | 20.96 | 135.8 |  | 38
LV20 | 20 | 6000 | 75 | 57 | 115 | 179.6 | 0.896 | 24.83 | 160.9 |  | 38
LV20 | 20 | 6000 | 80 | 57 | 115 | 190.5 | 0.905 | 26.6 | 172.4 |  | 38
LV20 | 20 | 6000 | 85 | 57 | 115 | 201.9 | 0.905 | 28.21 | 182.8 |  | 38
LV20 | 20 | 6000 | 90 | 57 | 115 | 213.4 | 0.905 | 29.8 | 193.1 |  | 38
LV20 | 20 | 6000 | 65 | 62 | 115 | 194.2 | 0.443 | 13.29 | 86.1 |  | 38
LV20 | 20 | 6000 | 70 | 62 | 115 | 195.7 | 0.57 | 17.22 | 111.6 |  | 38
LV20 | 20 | 6000 | 75 | 62 | 115 | 196.7 | 0.697 | 21.16 | 137.1 |  | 38
LV20 | 20 | 6000 | 80 | 62 | 115 | 197.5 | 0.823 | 25.09 | 162.6 |  | 38
LV20 | 20 | 6000 | 85 | 62 | 115 | 202 | 0.905 | 28.21 | 182.8 |  | 38
LV20 | 20 | 6000 | 90 | 62 | 115 | 213.6 | 0.905 | 29.83 | 193.3 |  | 38
LV20 | 20 | 6000 | 70 | 67 | 115 | 213.6 | 0.407 | 13.43 | 87 |  | 38
LV20 | 20 | 6000 | 75 | 67 | 115 | 214.7 | 0.525 | 17.39 | 112.7 |  | 38
LV20 | 20 | 6000 | 80 | 67 | 115 | 215.5 | 0.643 | 21.37 | 138.5 |  | 38
LV20 | 20 | 6000 | 85 | 67 | 115 | 216.2 | 0.76 | 25.37 | 164.4 |  | 38
LV20 | 20 | 6000 | 90 | 67 | 115 | 216.4 | 0.878 | 29.31 | 189.9 |  | 38
LV20 | 20 | 6000 | 75 | 72 | 115 | 233.9 | 0.371 | 13.4 | 86.8 |  | 38
LV20 | 20 | 6000 | 80 | 72 | 115 | 234.9 | 0.48 | 17.39 | 112.7 |  | 38
LV20 | 20 | 6000 | 85 | 72 | 115 | 235.4 | 0.588 | 21.37 | 138.5 |  | 38
LV20 | 20 | 6000 | 90 | 72 | 115 | 235.9 | 0.697 | 25.37 | 164.4 |  | 38
LV20 | 20 | 6000 | 80 | 77 | 115 | 254.4 | 0.344 | 13.5 | 87.5 |  | 38
LV20 | 20 | 6000 | 85 | 77 | 115 | 255 | 0.444 | 17.45 | 113.1 |  | 38
LV20 | 20 | 6000 | 90 | 77 | 115 | 255.4 | 0.543 | 21.4 | 138.7 |  | 38
LV20 | 20 | 6000 | 65 | 57 | 125 | 164.8 | 0.633 | 16.11 | 104.4 |  | 38
LV20 | 20 | 6000 | 70 | 57 | 125 | 165.9 | 0.778 | 19.92 | 129.1 |  | 38
LV20 | 20 | 6000 | 75 | 57 | 125 | 168 | 0.905 | 23.47 | 152.1 |  | 38
LV20 | 20 | 6000 | 80 | 57 | 125 | 179.2 | 0.905 | 25.02 | 162.1 |  | 38
LV20 | 20 | 6000 | 85 | 57 | 125 | 190.2 | 0.905 | 26.56 | 172.1 |  | 38
LV20 | 20 | 6000 | 90 | 57 | 125 | 201.2 | 0.905 | 28.1 | 182.1 |  | 38
LV20 | 20 | 6000 | 65 | 62 | 125 | 180.5 | 0.453 | 12.61 | 81.7 |  | 38
LV20 | 20 | 6000 | 70 | 62 | 125 | 182 | 0.579 | 16.27 | 105.4 |  | 38
LV20 | 20 | 6000 | 75 | 62 | 125 | 182.9 | 0.715 | 20.19 | 130.8 |  | 38
LV20 | 20 | 6000 | 80 | 62 | 125 | 183.3 | 0.851 | 24.07 | 156 |  | 38
LV20 | 20 | 6000 | 85 | 62 | 125 | 190.2 | 0.905 | 26.57 | 172.2 |  | 38
LV20 | 20 | 6000 | 90 | 62 | 125 | 201.1 | 0.905 | 28.09 | 182 |  | 38
LV20 | 20 | 6000 | 70 | 67 | 125 | 198.8 | 0.407 | 12.48 | 80.9 |  | 38
LV20 | 20 | 6000 | 75 | 67 | 125 | 199.9 | 0.534 | 16.47 | 106.7 |  | 38
LV20 | 20 | 6000 | 80 | 67 | 125 | 200.7 | 0.661 | 20.46 | 132.6 |  | 38
LV20 | 20 | 6000 | 85 | 67 | 125 | 201.4 | 0.778 | 24.18 | 156.7 |  | 38
LV20 | 20 | 6000 | 90 | 67 | 125 | 201.5 | 0.905 | 28.15 | 182.4 |  | 38
LV20 | 20 | 6000 | 75 | 72 | 125 | 217.9 | 0.371 | 12.48 | 80.9 |  | 38
LV20 | 20 | 6000 | 80 | 72 | 125 | 218.9 | 0.489 | 16.51 | 107 |  | 38
LV20 | 20 | 6000 | 85 | 72 | 125 | 219.4 | 0.606 | 20.52 | 133 |  | 38
LV20 | 20 | 6000 | 90 | 72 | 125 | 219.9 | 0.715 | 24.26 | 157.2 |  | 38
LV20 | 20 | 6000 | 80 | 77 | 125 | 236.2 | 0.344 | 12.53 | 81.2 |  | 38
LV20 | 20 | 6000 | 85 | 77 | 125 | 237.8 | 0.452 | 16.6 | 107.6 |  | 38
LV20 | 20 | 6000 | 90 | 77 | 125 | 237.9 | 0.552 | 20.28 | 131.4 |  | 38
LV20 | 20 | 7000 | 65 | 57 | 75 | 229.8 | 0.615 | 18.7 | 141.4 |  | 36
LV20 | 20 | 7000 | 70 | 57 | 75 | 231.2 | 0.742 | 22.7 | 171.6 |  | 36
LV20 | 20 | 7000 | 75 | 57 | 75 | 232.1 | 0.869 | 26.67 | 201.6 |  | 36
LV20 | 20 | 7000 | 80 | 57 | 75 | 242.5 | 0.905 | 29.02 | 219.4 |  | 36
LV20 | 20 | 7000 | 85 | 57 | 75 | 256.1 | 0.905 | 30.65 | 231.7 |  | 36
LV20 | 20 | 7000 | 90 | 57 | 75 | 269.5 | 0.905 | 32.26 | 243.9 |  | 36
LV20 | 20 | 7000 | 65 | 62 | 75 | 250.3 | 0.443 | 14.68 | 111 |  | 36
LV20 | 20 | 7000 | 70 | 62 | 75 | 252 | 0.561 | 18.7 | 141.4 |  | 36
LV20 | 20 | 7000 | 75 | 62 | 75 | 253.2 | 0.679 | 22.74 | 171.9 |  | 36
LV20 | 20 | 7000 | 80 | 62 | 75 | 254.2 | 0.797 | 26.79 | 202.5 |  | 36
LV20 | 20 | 7000 | 85 | 62 | 75 | 256.3 | 0.905 | 30.67 | 231.9 |  | 36
LV20 | 20 | 7000 | 90 | 62 | 75 | 269.6 | 0.905 | 32.28 | 244 |  | 36
LV20 | 20 | 7000 | 70 | 67 | 75 | 273.9 | 0.407 | 14.75 | 111.5 |  | 36
LV20 | 20 | 7000 | 75 | 67 | 75 | 275.2 | 0.516 | 18.78 | 142 |  | 36
LV20 | 20 | 7000 | 80 | 67 | 75 | 276.3 | 0.624 | 22.82 | 172.5 |  | 36
LV20 | 20 | 7000 | 85 | 67 | 75 | 277.2 | 0.733 | 26.88 | 203.2 |  | 36
LV20 | 20 | 7000 | 90 | 67 | 75 | 277.9 | 0.842 | 30.94 | 233.9 |  | 36
LV20 | 20 | 7000 | 75 | 72 | 75 | 298.1 | 0.371 | 14.63 | 110.6 |  | 36
LV20 | 20 | 7000 | 80 | 72 | 75 | 299.2 | 0.471 | 18.62 | 140.8 |  | 36
LV20 | 20 | 7000 | 85 | 72 | 75 | 299.9 | 0.57 | 22.62 | 171 |  | 36
LV20 | 20 | 7000 | 90 | 72 | 75 | 300.5 | 0.679 | 26.97 | 203.9 |  | 36
LV20 | 20 | 7000 | 80 | 77 | 75 | 323.5 | 0.344 | 14.71 | 111.2 |  | 36
LV20 | 20 | 7000 | 85 | 77 | 75 | 323.5 | 0.434 | 18.58 | 140.5 |  | 36
LV20 | 20 | 7000 | 90 | 77 | 75 | 324.4 | 0.525 | 22.53 | 170.3 |  | 36
LV20 | 20 | 7000 | 65 | 57 | 85 | 218.6 | 0.624 | 18.06 | 136.5 |  | 36
LV20 | 20 | 7000 | 70 | 57 | 85 | 220.1 | 0.751 | 21.87 | 165.3 |  | 36
LV20 | 20 | 7000 | 75 | 57 | 85 | 221 | 0.887 | 25.93 | 196 |  | 36
LV20 | 20 | 7000 | 80 | 57 | 85 | 232.9 | 0.905 | 27.87 | 210.7 |  | 36
LV20 | 20 | 7000 | 85 | 57 | 85 | 246.1 | 0.905 | 29.46 | 222.7 |  | 36
LV20 | 20 | 7000 | 90 | 57 | 85 | 259.3 | 0.905 | 31.04 | 234.7 |  | 36
LV20 | 20 | 7000 | 65 | 62 | 85 | 238.5 | 0.444 | 13.99 | 105.8 |  | 36
LV20 | 20 | 7000 | 70 | 62 | 85 | 240.1 | 0.57 | 18.11 | 136.9 |  | 36
LV20 | 20 | 7000 | 75 | 62 | 85 | 241.3 | 0.688 | 21.94 | 165.9 |  | 36
LV20 | 20 | 7000 | 80 | 62 | 85 | 242.2 | 0.814 | 26.08 | 197.2 |  | 36
LV20 | 20 | 7000 | 85 | 62 | 85 | 246.2 | 0.905 | 29.47 | 222.8 |  | 36
LV20 | 20 | 7000 | 90 | 62 | 85 | 259.4 | 0.905 | 31.04 | 234.7 |  | 36
LV20 | 20 | 7000 | 70 | 67 | 85 | 261.1 | 0.407 | 14.06 | 106.3 |  | 36
LV20 | 20 | 7000 | 75 | 67 | 85 | 262.3 | 0.525 | 18.21 | 137.7 |  | 36
LV20 | 20 | 7000 | 80 | 67 | 85 | 263.6 | 0.634 | 22.09 | 167 |  | 36
LV20 | 20 | 7000 | 85 | 67 | 85 | 264.5 | 0.751 | 26.28 | 198.7 |  | 36
LV20 | 20 | 7000 | 90 | 67 | 85 | 265 | 0.86 | 30.13 | 227.8 |  | 36
LV20 | 20 | 7000 | 75 | 72 | 85 | 284.4 | 0.371 | 13.96 | 105.5 |  | 36
LV20 | 20 | 7000 | 80 | 72 | 85 | 285.7 | 0.48 | 18.13 | 137.1 |  | 36
LV20 | 20 | 7000 | 85 | 72 | 85 | 286.6 | 0.579 | 21.96 | 166 |  | 36
LV20 | 20 | 7000 | 90 | 72 | 85 | 287.2 | 0.688 | 26.12 | 197.5 |  | 36
LV20 | 20 | 7000 | 80 | 77 | 85 | 308.8 | 0.344 | 14.05 | 106.2 |  | 36
LV20 | 20 | 7000 | 85 | 77 | 85 | 309.6 | 0.434 | 17.79 | 134.5 |  | 36
LV20 | 20 | 7000 | 90 | 77 | 85 | 310.1 | 0.534 | 21.9 | 165.6 |  | 36
LV20 | 20 | 7000 | 65 | 57 | 95 | 206.9 | 0.624 | 17.09 | 129.2 |  | 37
LV20 | 20 | 7000 | 70 | 57 | 95 | 208.3 | 0.77 | 21.2 | 160.3 |  | 37
LV20 | 20 | 7000 | 75 | 57 | 95 | 209.7 | 0.905 | 25.11 | 189.8 |  | 37
LV20 | 20 | 7000 | 80 | 57 | 95 | 222.3 | 0.905 | 26.61 | 201.2 |  | 37
LV20 | 20 | 7000 | 85 | 57 | 95 | 235.4 | 0.905 | 28.17 | 213 |  | 37
LV20 | 20 | 7000 | 90 | 57 | 95 | 248.3 | 0.905 | 29.72 | 224.7 |  | 37
LV20 | 20 | 7000 | 65 | 62 | 95 | 225.8 | 0.443 | 13.24 | 100.1 |  | 37
LV20 | 20 | 7000 | 70 | 62 | 95 | 227.4 | 0.579 | 17.42 | 131.7 |  | 37
LV20 | 20 | 7000 | 75 | 62 | 95 | 228.6 | 0.706 | 21.35 | 161.4 |  | 37
LV20 | 20 | 7000 | 80 | 62 | 95 | 229.5 | 0.833 | 25.28 | 191.1 |  | 37
LV20 | 20 | 7000 | 85 | 62 | 95 | 235.5 | 0.905 | 28.19 | 213.1 |  | 37
LV20 | 20 | 7000 | 90 | 62 | 95 | 248.5 | 0.905 | 29.75 | 224.9 |  | 37
LV20 | 20 | 7000 | 70 | 67 | 95 | 247.6 | 0.407 | 13.33 | 100.8 |  | 37
LV20 | 20 | 7000 | 75 | 67 | 95 | 249 | 0.525 | 17.29 | 130.7 |  | 37
LV20 | 20 | 7000 | 80 | 67 | 95 | 250 | 0.642 | 21.24 | 160.6 |  | 37
LV20 | 20 | 7000 | 85 | 67 | 95 | 251 | 0.76 | 25.24 | 190.8 |  | 37
LV20 | 20 | 7000 | 90 | 67 | 95 | 251.2 | 0.878 | 29.17 | 220.5 |  | 37
LV20 | 20 | 7000 | 75 | 72 | 95 | 270.2 | 0.371 | 13.27 | 100.3 |  | 37
LV20 | 20 | 7000 | 80 | 72 | 95 | 271.4 | 0.48 | 17.22 | 130.2 |  | 37
LV20 | 20 | 7000 | 85 | 72 | 95 | 272.2 | 0.588 | 21.18 | 160.1 |  | 37
LV20 | 20 | 7000 | 90 | 72 | 95 | 272.7 | 0.706 | 25.46 | 192.5 |  | 37
LV20 | 20 | 7000 | 80 | 77 | 95 | 293.4 | 0.344 | 13.35 | 100.9 |  | 37
LV20 | 20 | 7000 | 85 | 77 | 95 | 294.2 | 0.443 | 17.25 | 130.4 |  | 37
LV20 | 20 | 7000 | 90 | 77 | 95 | 294.8 | 0.543 | 21.18 | 160.1 |  | 37
LV20 | 20 | 7000 | 65 | 57 | 105 | 194.6 | 0.634 | 16.31 | 123.3 |  | 37
LV20 | 20 | 7000 | 70 | 57 | 105 | 195.9 | 0.778 | 20.17 | 152.5 |  | 37
LV20 | 20 | 7000 | 75 | 57 | 105 | 198.8 | 0.905 | 23.8 | 179.9 |  | 37
LV20 | 20 | 7000 | 80 | 57 | 105 | 211.3 | 0.905 | 25.29 | 191.2 |  | 37
LV20 | 20 | 7000 | 85 | 57 | 105 | 224 | 0.905 | 26.81 | 202.7 |  | 37
LV20 | 20 | 7000 | 90 | 57 | 105 | 236.7 | 0.905 | 28.33 | 214.2 |  | 37
LV20 | 20 | 7000 | 65 | 62 | 105 | 212.5 | 0.453 | 12.72 | 96.2 |  | 37
LV20 | 20 | 7000 | 70 | 62 | 105 | 214.2 | 0.579 | 16.42 | 124.1 |  | 37
LV20 | 20 | 7000 | 75 | 62 | 105 | 215.3 | 0.715 | 20.36 | 153.9 |  | 37
LV20 | 20 | 7000 | 80 | 62 | 105 | 216.1 | 0.851 | 24.31 | 183.8 |  | 37
LV20 | 20 | 7000 | 85 | 62 | 105 | 224.1 | 0.905 | 26.83 | 202.8 |  | 37
LV20 | 20 | 7000 | 90 | 62 | 105 | 236.6 | 0.905 | 28.32 | 214.1 |  | 37
LV20 | 20 | 7000 | 70 | 67 | 105 | 233.4 | 0.407 | 12.57 | 95 |  | 37
LV20 | 20 | 7000 | 75 | 67 | 105 | 234.8 | 0.534 | 16.59 | 125.4 |  | 37
LV20 | 20 | 7000 | 80 | 67 | 105 | 235.8 | 0.661 | 20.61 | 155.8 |  | 37
LV20 | 20 | 7000 | 85 | 67 | 105 | 236.7 | 0.778 | 24.37 | 184.2 |  | 37
LV20 | 20 | 7000 | 90 | 67 | 105 | 237.4 | 0.896 | 28.13 | 212.7 |  | 37
LV20 | 20 | 7000 | 75 | 72 | 105 | 255.1 | 0.38 | 12.83 | 97 |  | 37
LV20 | 20 | 7000 | 80 | 72 | 105 | 256 | 0.489 | 16.55 | 125.1 |  | 37
LV20 | 20 | 7000 | 85 | 72 | 105 | 256.7 | 0.606 | 20.58 | 155.6 |  | 37
LV20 | 20 | 7000 | 90 | 72 | 105 | 257.4 | 0.715 | 24.34 | 184 |  | 37
LV20 | 20 | 7000 | 80 | 77 | 105 | 277.2 | 0.344 | 12.61 | 95.3 |  | 37
LV20 | 20 | 7000 | 85 | 77 | 105 | 277.9 | 0.453 | 16.64 | 125.8 |  | 37
LV20 | 20 | 7000 | 90 | 77 | 105 | 278.4 | 0.552 | 20.33 | 153.7 |  | 37
LV20 | 20 | 7000 | 65 | 57 | 115 | 181.6 | 0.643 | 15.44 | 116.7 |  | 38
LV20 | 20 | 7000 | 70 | 57 | 115 | 182.9 | 0.797 | 19.27 | 145.7 |  | 38
LV20 | 20 | 7000 | 75 | 57 | 115 | 187.4 | 0.905 | 22.43 | 169.6 |  | 38
LV20 | 20 | 7000 | 80 | 57 | 115 | 199.6 | 0.905 | 23.9 | 180.7 |  | 38
LV20 | 20 | 7000 | 85 | 57 | 115 | 211.9 | 0.905 | 25.37 | 191.8 |  | 38
LV20 | 20 | 7000 | 90 | 57 | 115 | 224.1 | 0.905 | 26.83 | 202.8 |  | 38
LV20 | 20 | 7000 | 65 | 62 | 115 | 198.7 | 0.452 | 11.89 | 89.9 |  | 38
LV20 | 20 | 7000 | 70 | 62 | 115 | 200.2 | 0.588 | 15.58 | 117.8 |  | 38
LV20 | 20 | 7000 | 75 | 62 | 115 | 201.2 | 0.733 | 19.51 | 147.5 |  | 38
LV20 | 20 | 7000 | 80 | 62 | 115 | 202 | 0.878 | 23.45 | 177.3 |  | 38
LV20 | 20 | 7000 | 85 | 62 | 115 | 211.9 | 0.905 | 25.37 | 191.8 |  | 38
LV20 | 20 | 7000 | 90 | 62 | 115 | 224.2 | 0.905 | 26.84 | 202.9 |  | 38
LV20 | 20 | 7000 | 70 | 67 | 115 | 218.5 | 0.416 | 12.02 | 90.9 |  | 38
LV20 | 20 | 7000 | 75 | 67 | 115 | 219.9 | 0.543 | 15.79 | 119.4 |  | 38
LV20 | 20 | 7000 | 80 | 67 | 115 | 220.9 | 0.67 | 19.58 | 148 |  | 38
LV20 | 20 | 7000 | 85 | 67 | 115 | 221.5 | 0.805 | 23.6 | 178.4 |  | 38
LV20 | 20 | 7000 | 90 | 67 | 115 | 224.3 | 0.905 | 26.85 | 203 |  | 38
LV20 | 20 | 7000 | 75 | 72 | 115 | 238.9 | 0.38 | 12.01 | 90.8 |  | 38
LV20 | 20 | 7000 | 80 | 72 | 115 | 240 | 0.498 | 15.81 | 119.5 |  | 38
LV20 | 20 | 7000 | 85 | 72 | 115 | 240.6 | 0.615 | 19.58 | 148 |  | 38
LV20 | 20 | 7000 | 90 | 72 | 115 | 241.1 | 0.742 | 23.66 | 178.9 |  | 38
LV20 | 20 | 7000 | 80 | 77 | 115 | 259.9 | 0.344 | 11.83 | 89.4 |  | 38
LV20 | 20 | 7000 | 85 | 77 | 115 | 260.7 | 0.453 | 15.61 | 118 |  | 38
LV20 | 20 | 7000 | 90 | 77 | 115 | 261 | 0.57 | 19.68 | 148.8 |  | 38
LV20 | 20 | 7000 | 65 | 57 | 125 | 168.1 | 0.66 | 14.68 | 111 |  | 38
LV20 | 20 | 7000 | 70 | 57 | 125 | 169.2 | 0.823 | 18.43 | 139.3 |  | 38
LV20 | 20 | 7000 | 75 | 57 | 125 | 175.5 | 0.905 | 21.01 | 158.8 |  | 38
LV20 | 20 | 7000 | 80 | 57 | 125 | 187.3 | 0.905 | 22.42 | 169.5 |  | 38
LV20 | 20 | 7000 | 85 | 57 | 125 | 199 | 0.905 | 23.82 | 180.1 |  | 38
LV20 | 20 | 7000 | 90 | 57 | 125 | 210.7 | 0.905 | 25.21 | 190.6 |  | 38
LV20 | 20 | 7000 | 65 | 62 | 125 | 184.2 | 0.452 | 11.02 | 83.3 |  | 38
LV20 | 20 | 7000 | 70 | 62 | 125 | 185.6 | 0.606 | 14.88 | 112.5 |  | 38
LV20 | 20 | 7000 | 75 | 62 | 125 | 186.6 | 0.751 | 18.54 | 140.2 |  | 38
LV20 | 20 | 7000 | 80 | 62 | 125 | 187.6 | 0.905 | 22.45 | 169.7 |  | 38
LV20 | 20 | 7000 | 85 | 62 | 125 | 199.1 | 0.905 | 23.82 | 180.1 |  | 38
LV20 | 20 | 7000 | 90 | 62 | 125 | 210.7 | 0.905 | 25.22 | 190.7 |  | 38
LV20 | 20 | 7000 | 70 | 67 | 125 | 202.9 | 0.416 | 11.18 | 84.5 |  | 38
LV20 | 20 | 7000 | 75 | 67 | 125 | 204.2 | 0.552 | 14.91 | 112.7 |  | 38
LV20 | 20 | 7000 | 80 | 67 | 125 | 205.1 | 0.688 | 18.66 | 141.1 |  | 38
LV20 | 20 | 7000 | 85 | 67 | 125 | 205.5 | 0.833 | 22.63 | 171.1 |  | 38
LV20 | 20 | 7000 | 90 | 67 | 125 | 210.8 | 0.905 | 25.22 | 190.7 |  | 38
LV20 | 20 | 7000 | 75 | 72 | 125 | 222.1 | 0.38 | 11.16 | 84.4 |  | 38
LV20 | 20 | 7000 | 80 | 72 | 125 | 223 | 0.507 | 14.95 | 113 |  | 38
LV20 | 20 | 7000 | 85 | 72 | 125 | 223.6 | 0.633 | 18.73 | 141.6 |  | 38
LV20 | 20 | 7000 | 90 | 72 | 125 | 224 | 0.76 | 22.53 | 170.3 |  | 38
LV20 | 20 | 7000 | 80 | 77 | 125 | 241.9 | 0.344 | 11.01 | 83.2 |  | 38
LV20 | 20 | 7000 | 85 | 77 | 125 | 242.4 | 0.462 | 14.8 | 111.9 |  | 38
LV20 | 20 | 7000 | 90 | 77 | 125 | 242.4 | 0.588 | 18.86 | 142.6 |  | 38
LV20 | 20 | 8000 | 65 | 57 | 75 | 235.6 | 0.634 | 17.28 | 149.3 |  | 36
LV20 | 20 | 8000 | 70 | 57 | 75 | 237.1 | 0.769 | 21.11 | 182.4 |  | 36
LV20 | 20 | 8000 | 75 | 57 | 75 | 239.1 | 0.905 | 25.05 | 216.4 |  | 36
LV20 | 20 | 8000 | 80 | 57 | 75 | 253.5 | 0.905 | 26.55 | 229.4 |  | 36
LV20 | 20 | 8000 | 85 | 57 | 75 | 267.7 | 0.905 | 28.04 | 242.3 |  | 36
LV20 | 20 | 8000 | 90 | 57 | 75 | 281.9 | 0.905 | 29.53 | 255.1 |  | 36
LV20 | 20 | 8000 | 65 | 62 | 75 | 256.6 | 0.452 | 13.44 | 116.1 |  | 36
LV20 | 20 | 8000 | 70 | 62 | 75 | 258.2 | 0.579 | 17.3 | 149.5 |  | 36
LV20 | 20 | 8000 | 75 | 62 | 75 | 259.6 | 0.706 | 21.22 | 183.3 |  | 36
LV20 | 20 | 8000 | 80 | 62 | 75 | 260.9 | 0.842 | 25.42 | 219.6 |  | 36
LV20 | 20 | 8000 | 85 | 62 | 75 | 267.8 | 0.905 | 28.04 | 242.3 |  | 36
LV20 | 20 | 8000 | 90 | 62 | 75 | 281.9 | 0.905 | 29.53 | 255.1 |  | 36
LV20 | 20 | 8000 | 70 | 67 | 75 | 280.2 | 0.407 | 13.21 | 114.1 |  | 36
LV20 | 20 | 8000 | 75 | 67 | 75 | 281.8 | 0.534 | 17.42 | 150.5 |  | 36
LV20 | 20 | 8000 | 80 | 67 | 75 | 283.1 | 0.652 | 21.35 | 184.5 |  | 36
LV20 | 20 | 8000 | 85 | 67 | 75 | 284.1 | 0.769 | 25.29 | 218.5 |  | 36
LV20 | 20 | 8000 | 90 | 67 | 75 | 284.2 | 0.887 | 29.17 | 252 |  | 36
LV20 | 20 | 8000 | 75 | 72 | 75 | 304.8 | 0.371 | 13.09 | 113.1 |  | 36
LV20 | 20 | 8000 | 80 | 72 | 75 | 306 | 0.489 | 17.31 | 149.6 |  | 36
LV20 | 20 | 8000 | 85 | 72 | 75 | 306.8 | 0.597 | 21.22 | 183.3 |  | 36
LV20 | 20 | 8000 | 90 | 72 | 75 | 307.5 | 0.706 | 25.13 | 217.1 |  | 36
LV20 | 20 | 8000 | 80 | 77 | 75 | 330.7 | 0.344 | 13.16 | 113.7 |  | 36
LV20 | 20 | 8000 | 85 | 77 | 75 | 330.8 | 0.443 | 16.98 | 146.7 |  | 36
LV20 | 20 | 8000 | 90 | 77 | 75 | 331.6 | 0.552 | 21.18 | 183 |  | 36
LV20 | 20 | 8000 | 65 | 57 | 85 | 223.8 | 0.634 | 16.41 | 141.8 |  | 36
LV20 | 20 | 8000 | 70 | 57 | 85 | 225.3 | 0.787 | 20.53 | 177.4 |  | 36
LV20 | 20 | 8000 | 75 | 57 | 85 | 228.8 | 0.905 | 23.96 | 207 |  | 36
LV20 | 20 | 8000 | 80 | 57 | 85 | 242.9 | 0.905 | 25.44 | 219.8 |  | 36
LV20 | 20 | 8000 | 85 | 57 | 85 | 256.9 | 0.905 | 26.91 | 232.5 |  | 36
LV20 | 20 | 8000 | 90 | 57 | 85 | 270.8 | 0.905 | 28.37 | 245.1 |  | 36
LV20 | 20 | 8000 | 65 | 62 | 85 | 243.8 | 0.452 | 12.77 | 110.3 |  | 36
LV20 | 20 | 8000 | 70 | 62 | 85 | 245.6 | 0.588 | 16.72 | 144.5 |  | 36
LV20 | 20 | 8000 | 75 | 62 | 85 | 246.9 | 0.724 | 20.69 | 178.8 |  | 36
LV20 | 20 | 8000 | 80 | 62 | 85 | 248 | 0.851 | 24.42 | 211 |  | 36
LV20 | 20 | 8000 | 85 | 62 | 85 | 257 | 0.905 | 26.92 | 232.6 |  | 36
LV20 | 20 | 8000 | 90 | 62 | 85 | 270.9 | 0.905 | 28.38 | 245.2 |  | 36
LV20 | 20 | 8000 | 70 | 67 | 85 | 266.9 | 0.407 | 12.58 | 108.7 |  | 36
LV20 | 20 | 8000 | 75 | 67 | 85 | 268.4 | 0.534 | 16.59 | 143.3 |  | 36
LV20 | 20 | 8000 | 80 | 67 | 85 | 269.7 | 0.66 | 20.61 | 178.1 |  | 36
LV20 | 20 | 8000 | 85 | 67 | 85 | 270.8 | 0.787 | 24.68 | 213.2 |  | 36
LV20 | 20 | 8000 | 90 | 67 | 85 | 271.3 | 0.905 | 28.41 | 245.5 |  | 36
LV20 | 20 | 8000 | 75 | 72 | 85 | 290.5 | 0.38 | 12.78 | 110.4 |  | 36
LV20 | 20 | 8000 | 80 | 72 | 85 | 291.9 | 0.489 | 16.5 | 142.6 |  | 36
LV20 | 20 | 8000 | 85 | 72 | 85 | 292.8 | 0.606 | 20.54 | 177.5 |  | 36
LV20 | 20 | 8000 | 90 | 72 | 85 | 293.5 | 0.724 | 24.59 | 212.5 |  | 36
LV20 | 20 | 8000 | 80 | 77 | 85 | 315.1 | 0.344 | 12.55 | 108.4 |  | 36
LV20 | 20 | 8000 | 85 | 77 | 85 | 316 | 0.453 | 16.55 | 143 |  | 36
LV20 | 20 | 8000 | 90 | 77 | 85 | 316.4 | 0.561 | 20.54 | 177.5 |  | 36
LV20 | 20 | 8000 | 65 | 57 | 95 | 211.3 | 0.643 | 15.72 | 135.8 |  | 37
LV20 | 20 | 8000 | 70 | 57 | 95 | 212.7 | 0.796 | 19.61 | 169.4 |  | 37
LV20 | 20 | 8000 | 75 | 57 | 95 | 217.9 | 0.905 | 22.82 | 197.2 |  | 37
LV20 | 20 | 8000 | 80 | 57 | 95 | 231.6 | 0.905 | 24.26 | 209.6 |  | 37
LV20 | 20 | 8000 | 85 | 57 | 95 | 245.4 | 0.905 | 25.71 | 222.1 |  | 37
LV20 | 20 | 8000 | 90 | 57 | 95 | 259 | 0.905 | 27.13 | 234.4 |  | 37
LV20 | 20 | 8000 | 65 | 62 | 95 | 230.4 | 0.452 | 12.06 | 104.2 |  | 37
LV20 | 20 | 8000 | 70 | 62 | 95 | 232.2 | 0.588 | 15.81 | 136.6 |  | 37
LV20 | 20 | 8000 | 75 | 62 | 95 | 233.6 | 0.733 | 19.81 | 171.2 |  | 37
LV20 | 20 | 8000 | 80 | 62 | 95 | 234.5 | 0.878 | 23.83 | 205.9 |  | 37
LV20 | 20 | 8000 | 85 | 62 | 95 | 245.6 | 0.905 | 25.72 | 222.2 |  | 37
LV20 | 20 | 8000 | 90 | 62 | 95 | 259.2 | 0.905 | 27.15 | 234.6 |  | 37
LV20 | 20 | 8000 | 70 | 67 | 95 | 252.7 | 0.416 | 12.18 | 105.2 |  | 37
LV20 | 20 | 8000 | 75 | 67 | 95 | 254.3 | 0.543 | 15.98 | 138.1 |  | 37
LV20 | 20 | 8000 | 80 | 67 | 95 | 255.4 | 0.67 | 19.79 | 171 |  | 37
LV20 | 20 | 8000 | 85 | 67 | 95 | 256.1 | 0.806 | 23.88 | 206.3 |  | 37
LV20 | 20 | 8000 | 90 | 67 | 95 | 259.2 | 0.905 | 27.15 | 234.6 |  | 37
LV20 | 20 | 8000 | 75 | 72 | 95 | 275.5 | 0.38 | 12.12 | 104.7 |  | 37
LV20 | 20 | 8000 | 80 | 72 | 95 | 276.7 | 0.498 | 15.94 | 137.7 |  | 37
LV20 | 20 | 8000 | 85 | 72 | 95 | 277.8 | 0.615 | 19.78 | 170.9 |  | 37
LV20 | 20 | 8000 | 90 | 72 | 95 | 278.3 | 0.742 | 23.9 | 206.5 |  | 37
LV20 | 20 | 8000 | 80 | 77 | 95 | 298.9 | 0.344 | 11.9 | 102.8 |  | 37
LV20 | 20 | 8000 | 85 | 77 | 95 | 300 | 0.452 | 15.71 | 135.7 |  | 37
LV20 | 20 | 8000 | 90 | 77 | 95 | 300.4 | 0.57 | 19.83 | 171.3 |  | 37
LV20 | 20 | 8000 | 65 | 57 | 105 | 198.2 | 0.652 | 14.95 | 129.2 |  | 37
LV20 | 20 | 8000 | 70 | 57 | 105 | 199.6 | 0.814 | 18.81 | 162.5 |  | 37
LV20 | 20 | 8000 | 75 | 57 | 105 | 206.3 | 0.905 | 21.61 | 186.7 |  | 37
LV20 | 20 | 8000 | 80 | 57 | 105 | 219.7 | 0.905 | 23.01 | 198.8 |  | 37
LV20 | 20 | 8000 | 85 | 57 | 105 | 233.2 | 0.905 | 24.42 | 211 |  | 37
LV20 | 20 | 8000 | 90 | 57 | 105 | 246.6 | 0.905 | 25.82 | 223.1 |  | 37
LV20 | 20 | 8000 | 65 | 62 | 105 | 216.4 | 0.452 | 11.33 | 97.9 |  | 37
LV20 | 20 | 8000 | 70 | 62 | 105 | 218.2 | 0.597 | 15.08 | 130.3 |  | 37
LV20 | 20 | 8000 | 75 | 62 | 105 | 219.6 | 0.751 | 19.1 | 165 |  | 37
LV20 | 20 | 8000 | 80 | 62 | 105 | 220.7 | 0.896 | 22.88 | 197.7 |  | 37
LV20 | 20 | 8000 | 85 | 62 | 105 | 233.3 | 0.905 | 24.43 | 211.1 |  | 37
LV20 | 20 | 8000 | 90 | 62 | 105 | 246.5 | 0.905 | 25.81 | 223 |  | 37
LV20 | 20 | 8000 | 70 | 67 | 105 | 237.7 | 0.416 | 11.45 | 98.9 |  | 37
LV20 | 20 | 8000 | 75 | 67 | 105 | 239.3 | 0.552 | 15.29 | 132.1 |  | 37
LV20 | 20 | 8000 | 80 | 67 | 105 | 240.4 | 0.688 | 19.13 | 165.3 |  | 37
LV20 | 20 | 8000 | 85 | 67 | 105 | 241.3 | 0.823 | 23 | 198.7 |  | 37
LV20 | 20 | 8000 | 90 | 67 | 105 | 246.6 | 0.905 | 25.83 | 223.2 |  | 37
LV20 | 20 | 8000 | 75 | 72 | 105 | 259.6 | 0.38 | 11.42 | 98.7 |  | 37
LV20 | 20 | 8000 | 80 | 72 | 105 | 260.8 | 0.507 | 15.3 | 132.2 |  | 37
LV20 | 20 | 8000 | 85 | 72 | 105 | 261.5 | 0.634 | 19.18 | 165.7 |  | 37
LV20 | 20 | 8000 | 90 | 72 | 105 | 262.2 | 0.76 | 23.07 | 199.3 |  | 37
LV20 | 20 | 8000 | 80 | 77 | 105 | 281.7 | 0.344 | 11.22 | 96.9 |  | 37
LV20 | 20 | 8000 | 85 | 77 | 105 | 282.7 | 0.462 | 15.1 | 130.5 |  | 37
LV20 | 20 | 8000 | 90 | 77 | 105 | 283.3 | 0.579 | 18.99 | 164.1 |  | 37
LV20 | 20 | 8000 | 65 | 57 | 115 | 184.5 | 0.67 | 14.31 | 123.6 |  | 38
LV20 | 20 | 8000 | 70 | 57 | 115 | 185.8 | 0.842 | 18.1 | 156.4 |  | 38
LV20 | 20 | 8000 | 75 | 57 | 115 | 194.2 | 0.905 | 20.35 | 175.8 |  | 38
LV20 | 20 | 8000 | 80 | 57 | 115 | 207.1 | 0.905 | 21.69 | 187.4 |  | 38
LV20 | 20 | 8000 | 85 | 57 | 115 | 220.1 | 0.905 | 23.04 | 199.1 |  | 38
LV20 | 20 | 8000 | 90 | 57 | 115 | 232.8 | 0.905 | 24.39 | 210.7 |  | 38
LV20 | 20 | 8000 | 65 | 62 | 115 | 201.9 | 0.452 | 10.57 | 91.3 |  | 38
LV20 | 20 | 8000 | 70 | 62 | 115 | 203.6 | 0.615 | 14.5 | 125.3 |  | 38
LV20 | 20 | 8000 | 75 | 62 | 115 | 204.9 | 0.769 | 18.24 | 157.6 |  | 38
LV20 | 20 | 8000 | 80 | 62 | 115 | 207.2 | 0.905 | 21.7 | 187.5 |  | 38
LV20 | 20 | 8000 | 85 | 62 | 115 | 220.1 | 0.905 | 23.04 | 199.1 |  | 38
LV20 | 20 | 8000 | 90 | 62 | 115 | 232.8 | 0.905 | 24.39 | 210.7 |  | 38
LV20 | 20 | 8000 | 70 | 67 | 115 | 222.1 | 0.416 | 10.69 | 92.4 |  | 38
LV20 | 20 | 8000 | 75 | 67 | 115 | 223.6 | 0.561 | 14.53 | 125.5 |  | 38
LV20 | 20 | 8000 | 80 | 67 | 115 | 224.6 | 0.706 | 18.36 | 158.6 |  | 38
LV20 | 20 | 8000 | 85 | 67 | 115 | 225 | 0.851 | 22.15 | 191.4 |  | 38
LV20 | 20 | 8000 | 90 | 67 | 115 | 233 | 0.905 | 24.41 | 210.9 |  | 38
LV20 | 20 | 8000 | 75 | 72 | 115 | 242.8 | 0.38 | 10.68 | 92.3 |  | 38
LV20 | 20 | 8000 | 80 | 72 | 115 | 244 | 0.516 | 14.56 | 125.8 |  | 38
LV20 | 20 | 8000 | 85 | 72 | 115 | 244.6 | 0.652 | 18.45 | 159.4 |  | 38
LV20 | 20 | 8000 | 90 | 72 | 115 | 245.1 | 0.778 | 22.08 | 190.8 |  | 38
LV20 | 20 | 8000 | 80 | 77 | 115 | 264 | 0.353 | 10.79 | 93.2 |  | 38
LV20 | 20 | 8000 | 85 | 77 | 115 | 264.8 | 0.471 | 14.42 | 124.6 |  | 38
LV20 | 20 | 8000 | 90 | 77 | 115 | 265.2 | 0.597 | 18.33 | 158.4 |  | 38
LV20 | 20 | 8000 | 65 | 57 | 125 | 170.3 | 0.679 | 13.38 | 115.6 |  | 38
LV20 | 20 | 8000 | 70 | 57 | 125 | 171.5 | 0.859 | 17.06 | 147.4 |  | 38
LV20 | 20 | 8000 | 75 | 57 | 125 | 181.4 | 0.905 | 19 | 164.2 |  | 38
LV20 | 20 | 8000 | 80 | 57 | 125 | 193.8 | 0.905 | 20.3 | 175.4 |  | 38
LV20 | 20 | 8000 | 85 | 57 | 125 | 206.2 | 0.905 | 21.6 | 186.6 |  | 38
LV20 | 20 | 8000 | 90 | 57 | 125 | 218.6 | 0.905 | 22.89 | 197.8 |  | 38
LV20 | 20 | 8000 | 65 | 62 | 125 | 186.7 | 0.462 | 9.98 | 86.2 |  | 38
LV20 | 20 | 8000 | 70 | 62 | 125 | 188.4 | 0.624 | 13.61 | 117.6 |  | 38
LV20 | 20 | 8000 | 75 | 62 | 125 | 189.5 | 0.787 | 17.27 | 149.2 |  | 38
LV20 | 20 | 8000 | 80 | 62 | 125 | 193.8 | 0.905 | 20.3 | 175.4 |  | 38
LV20 | 20 | 8000 | 85 | 62 | 125 | 206.2 | 0.905 | 21.6 | 186.6 |  | 38
LV20 | 20 | 8000 | 90 | 62 | 125 | 218.5 | 0.905 | 22.88 | 197.7 |  | 38
LV20 | 20 | 8000 | 70 | 67 | 125 | 205.7 | 0.425 | 10.13 | 87.5 |  | 38
LV20 | 20 | 8000 | 75 | 67 | 125 | 207.1 | 0.57 | 13.67 | 118.1 |  | 38
LV20 | 20 | 8000 | 80 | 67 | 125 | 207.9 | 0.724 | 17.42 | 150.5 |  | 38
LV20 | 20 | 8000 | 85 | 67 | 125 | 208 | 0.887 | 21.34 | 184.4 |  | 38
LV20 | 20 | 8000 | 90 | 67 | 125 | 218.7 | 0.905 | 22.91 | 197.9 |  | 38
LV20 | 20 | 8000 | 75 | 72 | 125 | 225.2 | 0.389 | 10.14 | 87.6 |  | 38
LV20 | 20 | 8000 | 80 | 72 | 125 | 226.3 | 0.525 | 13.75 | 118.8 |  | 38
LV20 | 20 | 8000 | 85 | 72 | 125 | 226.8 | 0.67 | 17.58 | 151.9 |  | 38
LV20 | 20 | 8000 | 90 | 72 | 125 | 227 | 0.815 | 21.4 | 184.9 |  | 38
LV20 | 20 | 8000 | 80 | 77 | 125 | 246.2 | 0.353 | 10.06 | 86.9 |  | 38
LV20 | 20 | 8000 | 85 | 77 | 125 | 245.8 | 0.48 | 13.65 | 117.9 |  | 38
LV20 | 20 | 8000 | 90 | 77 | 125 | 245.9 | 0.615 | 17.51 | 151.3 |  | 38
LV20 | 20 | 9000 | 65 | 57 | 75 | 240.3 | 0.643 | 15.88 | 154.4 |  | 36
LV20 | 20 | 9000 | 70 | 57 | 75 | 241.8 | 0.797 | 19.81 | 192.6 |  | 36
LV20 | 20 | 9000 | 75 | 57 | 75 | 247.6 | 0.905 | 23.06 | 224.1 |  | 36
LV20 | 20 | 9000 | 80 | 57 | 75 | 262.7 | 0.905 | 24.45 | 237.7 |  | 36
LV20 | 20 | 9000 | 85 | 57 | 75 | 277.6 | 0.905 | 25.84 | 251.2 |  | 36
LV20 | 20 | 9000 | 90 | 57 | 75 | 292.5 | 0.905 | 27.23 | 264.7 |  | 36
LV20 | 20 | 9000 | 65 | 62 | 75 | 261.6 | 0.453 | 12.18 | 118.4 |  | 36
LV20 | 20 | 9000 | 70 | 62 | 75 | 263.4 | 0.588 | 15.94 | 154.9 |  | 36
LV20 | 20 | 9000 | 75 | 62 | 75 | 264.9 | 0.733 | 19.97 | 194.1 |  | 36
LV20 | 20 | 9000 | 80 | 62 | 75 | 266 | 0.878 | 24.02 | 233.5 |  | 36
LV20 | 20 | 9000 | 85 | 62 | 75 | 277.6 | 0.905 | 25.84 | 251.2 |  | 36
LV20 | 20 | 9000 | 90 | 62 | 75 | 292.6 | 0.905 | 27.24 | 264.8 |  | 36
LV20 | 20 | 9000 | 70 | 67 | 75 | 285.4 | 0.416 | 12.22 | 118.8 |  | 36
LV20 | 20 | 9000 | 75 | 67 | 75 | 287 | 0.543 | 16.03 | 155.8 |  | 36
LV20 | 20 | 9000 | 80 | 67 | 75 | 288.2 | 0.679 | 20.12 | 195.6 |  | 36
LV20 | 20 | 9000 | 85 | 67 | 75 | 289.4 | 0.805 | 23.98 | 233.1 |  | 36
LV20 | 20 | 9000 | 90 | 67 | 75 | 292.7 | 0.905 | 27.25 | 264.9 |  | 36
LV20 | 20 | 9000 | 75 | 72 | 75 | 310.3 | 0.38 | 12.13 | 117.9 |  | 36
LV20 | 20 | 9000 | 80 | 72 | 75 | 311.7 | 0.498 | 15.97 | 155.2 |  | 36
LV20 | 20 | 9000 | 85 | 72 | 75 | 312.5 | 0.615 | 19.78 | 192.3 |  | 36
LV20 | 20 | 9000 | 90 | 72 | 75 | 313.2 | 0.742 | 23.91 | 232.4 |  | 36
LV20 | 20 | 9000 | 80 | 77 | 75 | 336.4 | 0.344 | 11.9 | 115.7 |  | 36
LV20 | 20 | 9000 | 85 | 77 | 75 | 336.6 | 0.462 | 15.99 | 155.4 |  | 36
LV20 | 20 | 9000 | 90 | 77 | 75 | 337.4 | 0.57 | 19.79 | 192.4 |  | 36
LV20 | 20 | 9000 | 65 | 57 | 85 | 227.9 | 0.652 | 15.28 | 148.5 |  | 36
LV20 | 20 | 9000 | 70 | 57 | 85 | 229.5 | 0.815 | 19.24 | 187 |  | 36
LV20 | 20 | 9000 | 75 | 57 | 85 | 236.6 | 0.905 | 22.03 | 214.1 |  | 36
LV20 | 20 | 9000 | 80 | 57 | 85 | 251.4 | 0.905 | 23.41 | 227.5 |  | 36
LV20 | 20 | 9000 | 85 | 57 | 85 | 266.1 | 0.905 | 24.77 | 240.8 |  | 36
LV20 | 20 | 9000 | 90 | 57 | 85 | 280.6 | 0.905 | 26.13 | 254 |  | 36
LV20 | 20 | 9000 | 65 | 62 | 85 | 248.2 | 0.452 | 11.55 | 112.3 |  | 36
LV20 | 20 | 9000 | 70 | 62 | 85 | 250.2 | 0.598 | 15.38 | 149.5 |  | 36
LV20 | 20 | 9000 | 75 | 62 | 85 | 251.6 | 0.751 | 19.44 | 189 |  | 36
LV20 | 20 | 9000 | 80 | 62 | 85 | 252.8 | 0.896 | 23.3 | 226.5 |  | 36
LV20 | 20 | 9000 | 85 | 62 | 85 | 266.2 | 0.905 | 24.78 | 240.9 |  | 36
LV20 | 20 | 9000 | 90 | 62 | 85 | 280.7 | 0.905 | 26.13 | 254 |  | 36
LV20 | 20 | 9000 | 70 | 67 | 85 | 271.4 | 0.416 | 11.63 | 113 |  | 36
LV20 | 20 | 9000 | 75 | 67 | 85 | 272.9 | 0.552 | 15.5 | 150.7 |  | 36
LV20 | 20 | 9000 | 80 | 67 | 85 | 274.2 | 0.688 | 19.4 | 188.6 |  | 36
LV20 | 20 | 9000 | 85 | 67 | 85 | 275.4 | 0.824 | 23.33 | 226.8 |  | 36
LV20 | 20 | 9000 | 90 | 67 | 85 | 280.7 | 0.905 | 26.13 | 254 |  | 36
LV20 | 20 | 9000 | 75 | 72 | 85 | 295.3 | 0.38 | 11.54 | 112.2 |  | 36
LV20 | 20 | 9000 | 80 | 72 | 85 | 296.9 | 0.507 | 15.48 | 150.5 |  | 36
LV20 | 20 | 9000 | 85 | 72 | 85 | 297.9 | 0.633 | 19.41 | 188.7 |  | 36
LV20 | 20 | 9000 | 90 | 72 | 85 | 298.5 | 0.76 | 23.34 | 226.9 |  | 36
LV20 | 20 | 9000 | 80 | 77 | 85 | 320.2 | 0.344 | 11.33 | 110.1 |  | 36
LV20 | 20 | 9000 | 85 | 77 | 85 | 321.3 | 0.462 | 15.26 | 148.3 |  | 36
LV20 | 20 | 9000 | 90 | 77 | 85 | 321.7 | 0.579 | 19.17 | 186.3 |  | 36
LV20 | 20 | 9000 | 65 | 57 | 95 | 214.6 | 0.661 | 14.59 | 141.8 |  | 37
LV20 | 20 | 9000 | 70 | 57 | 95 | 216.4 | 0.833 | 18.54 | 180.2 |  | 37
LV20 | 20 | 9000 | 75 | 57 | 95 | 225 | 0.905 | 20.95 | 203.6 |  | 37
LV20 | 20 | 9000 | 80 | 57 | 95 | 239.4 | 0.905 | 22.28 | 216.6 |  | 37
LV20 | 20 | 9000 | 85 | 57 | 95 | 253.8 | 0.905 | 23.63 | 229.7 |  | 37
LV20 | 20 | 9000 | 90 | 57 | 95 | 268 | 0.905 | 24.96 | 242.6 |  | 37
LV20 | 20 | 9000 | 65 | 62 | 95 | 234.2 | 0.453 | 10.91 | 106 |  | 37
LV20 | 20 | 9000 | 70 | 62 | 95 | 236.2 | 0.606 | 14.73 | 143.2 |  | 37
LV20 | 20 | 9000 | 75 | 62 | 95 | 237.7 | 0.76 | 18.59 | 180.7 |  | 37
LV20 | 20 | 9000 | 80 | 62 | 95 | 239.6 | 0.905 | 22.3 | 216.8 |  | 37
LV20 | 20 | 9000 | 85 | 62 | 95 | 253.9 | 0.905 | 23.64 | 229.8 |  | 37
LV20 | 20 | 9000 | 90 | 62 | 95 | 268.1 | 0.905 | 24.96 | 242.6 |  | 37
LV20 | 20 | 9000 | 70 | 67 | 95 | 256.5 | 0.416 | 10.99 | 106.8 |  | 37
LV20 | 20 | 9000 | 75 | 67 | 95 | 258.1 | 0.561 | 14.9 | 144.8 |  | 37
LV20 | 20 | 9000 | 80 | 67 | 95 | 259.3 | 0.697 | 18.59 | 180.7 |  | 37
LV20 | 20 | 9000 | 85 | 67 | 95 | 260.2 | 0.842 | 22.53 | 219 |  | 37
LV20 | 20 | 9000 | 90 | 67 | 95 | 268.2 | 0.905 | 24.97 | 242.7 |  | 37
LV20 | 20 | 9000 | 75 | 72 | 95 | 279.7 | 0.38 | 10.94 | 106.3 |  | 37
LV20 | 20 | 9000 | 80 | 72 | 95 | 281 | 0.516 | 14.92 | 145 |  | 37
LV20 | 20 | 9000 | 85 | 72 | 95 | 282 | 0.643 | 18.64 | 181.2 |  | 37
LV20 | 20 | 9000 | 90 | 72 | 95 | 282.6 | 0.778 | 22.62 | 219.9 |  | 37
LV20 | 20 | 9000 | 80 | 77 | 95 | 303.4 | 0.353 | 11.02 | 107.1 |  | 37
LV20 | 20 | 9000 | 85 | 77 | 95 | 304.6 | 0.471 | 14.75 | 143.4 |  | 37
LV20 | 20 | 9000 | 90 | 77 | 95 | 305.1 | 0.598 | 18.76 | 182.3 |  | 37
LV20 | 20 | 9000 | 65 | 57 | 105 | 201 | 0.679 | 14.03 | 136.4 |  | 37
LV20 | 20 | 9000 | 70 | 57 | 105 | 202.6 | 0.851 | 17.74 | 172.4 |  | 37
LV20 | 20 | 9000 | 75 | 57 | 105 | 212.8 | 0.905 | 19.81 | 192.6 |  | 37
LV20 | 20 | 9000 | 80 | 57 | 105 | 226.7 | 0.905 | 21.11 | 205.2 |  | 37
LV20 | 20 | 9000 | 85 | 57 | 105 | 240.7 | 0.905 | 22.42 | 217.9 |  | 37
LV20 | 20 | 9000 | 90 | 57 | 105 | 254.5 | 0.905 | 23.69 | 230.3 |  | 37
LV20 | 20 | 9000 | 65 | 62 | 105 | 219.6 | 0.461 | 10.42 | 101.3 |  | 37
LV20 | 20 | 9000 | 70 | 62 | 105 | 221.6 | 0.616 | 14.03 | 136.4 |  | 37
LV20 | 20 | 9000 | 75 | 62 | 105 | 223 | 0.778 | 17.86 | 173.6 |  | 37
LV20 | 20 | 9000 | 80 | 62 | 105 | 226.7 | 0.905 | 21.11 | 205.2 |  | 37
LV20 | 20 | 9000 | 85 | 62 | 105 | 240.8 | 0.905 | 22.42 | 217.9 |  | 37
LV20 | 20 | 9000 | 90 | 62 | 105 | 254.6 | 0.905 | 23.7 | 230.4 |  | 37
LV20 | 20 | 9000 | 70 | 67 | 105 | 240.8 | 0.417 | 10.32 | 100.3 |  | 37
LV20 | 20 | 9000 | 75 | 67 | 105 | 242.6 | 0.57 | 14.23 | 138.3 |  | 37
LV20 | 20 | 9000 | 80 | 67 | 105 | 243.7 | 0.715 | 17.92 | 174.2 |  | 37
LV20 | 20 | 9000 | 85 | 67 | 105 | 244.5 | 0.869 | 21.85 | 212.4 |  | 37
LV20 | 20 | 9000 | 90 | 67 | 105 | 254.8 | 0.905 | 23.72 | 230.6 |  | 37
LV20 | 20 | 9000 | 75 | 72 | 105 | 263.1 | 0.38 | 10.29 | 100 |  | 37
LV20 | 20 | 9000 | 80 | 72 | 105 | 264.4 | 0.525 | 14.28 | 138.8 |  | 37
LV20 | 20 | 9000 | 85 | 72 | 105 | 265.2 | 0.661 | 18.02 | 175.2 |  | 37
LV20 | 20 | 9000 | 90 | 72 | 105 | 265.9 | 0.796 | 21.78 | 211.7 |  | 37
LV20 | 20 | 9000 | 80 | 77 | 105 | 285.8 | 0.353 | 10.38 | 100.9 |  | 37
LV20 | 20 | 9000 | 85 | 77 | 105 | 286.6 | 0.48 | 14.15 | 137.5 |  | 37
LV20 | 20 | 9000 | 90 | 77 | 105 | 287.2 | 0.606 | 17.91 | 174.1 |  | 37
LV20 | 20 | 9000 | 65 | 57 | 115 | 186.8 | 0.688 | 13.22 | 128.5 |  | 38
LV20 | 20 | 9000 | 70 | 57 | 115 | 188.3 | 0.878 | 17.01 | 165.3 |  | 38
LV20 | 20 | 9000 | 75 | 57 | 115 | 199.9 | 0.905 | 18.61 | 180.9 |  | 38
LV20 | 20 | 9000 | 80 | 57 | 115 | 213.4 | 0.905 | 19.87 | 193.1 |  | 38
LV20 | 20 | 9000 | 85 | 57 | 115 | 226.9 | 0.905 | 21.12 | 205.3 |  | 38
LV20 | 20 | 9000 | 90 | 57 | 115 | 240.2 | 0.905 | 22.37 | 217.4 |  | 38
LV20 | 20 | 9000 | 65 | 62 | 115 | 204.4 | 0.462 | 9.71 | 94.4 |  | 38
LV20 | 20 | 9000 | 70 | 62 | 115 | 206.4 | 0.633 | 13.45 | 130.7 |  | 38
LV20 | 20 | 9000 | 75 | 62 | 115 | 207.8 | 0.806 | 17.22 | 167.4 |  | 38
LV20 | 20 | 9000 | 80 | 62 | 115 | 213.4 | 0.905 | 19.87 | 193.1 |  | 38
LV20 | 20 | 9000 | 85 | 62 | 115 | 227 | 0.905 | 21.13 | 205.4 |  | 38
LV20 | 20 | 9000 | 90 | 62 | 115 | 240.4 | 0.905 | 22.39 | 217.6 |  | 38
LV20 | 20 | 9000 | 70 | 67 | 115 | 224.6 | 0.425 | 9.83 | 95.5 |  | 38
LV20 | 20 | 9000 | 75 | 67 | 115 | 226.2 | 0.579 | 13.48 | 131 |  | 38
LV20 | 20 | 9000 | 80 | 67 | 115 | 227.3 | 0.742 | 17.36 | 168.7 |  | 38
LV20 | 20 | 9000 | 85 | 67 | 115 | 227.8 | 0.896 | 21 | 204.1 |  | 38
LV20 | 20 | 9000 | 90 | 67 | 115 | 240.3 | 0.905 | 22.37 | 217.4 |  | 38
LV20 | 20 | 9000 | 75 | 72 | 115 | 245.7 | 0.389 | 9.84 | 95.6 |  | 38
LV20 | 20 | 9000 | 80 | 72 | 115 | 246.8 | 0.534 | 13.56 | 131.8 |  | 38
LV20 | 20 | 9000 | 85 | 72 | 115 | 247.5 | 0.679 | 17.28 | 168 |  | 38
LV20 | 20 | 9000 | 90 | 72 | 115 | 247.8 | 0.824 | 21 | 204.1 |  | 38
LV20 | 20 | 9000 | 80 | 77 | 115 | 267.2 | 0.353 | 9.7 | 94.3 |  | 38
LV20 | 20 | 9000 | 85 | 77 | 115 | 267.9 | 0.489 | 13.47 | 130.9 |  | 38
LV20 | 20 | 9000 | 90 | 77 | 115 | 268.3 | 0.624 | 17.23 | 167.5 |  | 38
LV20 | 20 | 9000 | 65 | 57 | 125 | 172 | 0.706 | 12.49 | 121.4 |  | 38
LV20 | 20 | 9000 | 70 | 57 | 125 | 173.5 | 0.905 | 16.15 | 157 |  | 38
LV20 | 20 | 9000 | 75 | 57 | 125 | 186.3 | 0.905 | 17.35 | 168.6 |  | 38
LV20 | 20 | 9000 | 80 | 57 | 125 | 199.3 | 0.905 | 18.55 | 180.3 |  | 38
LV20 | 20 | 9000 | 85 | 57 | 125 | 212.1 | 0.905 | 19.74 | 191.9 |  | 38
LV20 | 20 | 9000 | 90 | 57 | 125 | 224.9 | 0.905 | 20.94 | 203.5 |  | 38
LV20 | 20 | 9000 | 65 | 62 | 125 | 188.6 | 0.471 | 9.14 | 88.8 |  | 38
LV20 | 20 | 9000 | 70 | 62 | 125 | 190.5 | 0.643 | 12.59 | 122.4 |  | 38
LV20 | 20 | 9000 | 75 | 62 | 125 | 191.5 | 0.832 | 16.4 | 159.4 |  | 38
LV20 | 20 | 9000 | 80 | 62 | 125 | 199.3 | 0.905 | 18.55 | 180.3 |  | 38
LV20 | 20 | 9000 | 85 | 62 | 125 | 212.1 | 0.905 | 19.75 | 192 |  | 38
LV20 | 20 | 9000 | 90 | 62 | 125 | 224.9 | 0.905 | 20.95 | 203.6 |  | 38
LV20 | 20 | 9000 | 70 | 67 | 125 | 207.6 | 0.425 | 9.08 | 88.3 |  | 38
LV20 | 20 | 9000 | 75 | 67 | 125 | 209.2 | 0.597 | 12.85 | 124.9 |  | 38
LV20 | 20 | 9000 | 80 | 67 | 125 | 210.1 | 0.76 | 16.43 | 159.7 |  | 38
LV20 | 20 | 9000 | 85 | 67 | 125 | 212.2 | 0.905 | 19.75 | 192 |  | 38
LV20 | 20 | 9000 | 90 | 67 | 125 | 225 | 0.905 | 20.95 | 203.6 |  | 38
LV20 | 20 | 9000 | 75 | 72 | 125 | 227.5 | 0.389 | 9.1 | 88.5 |  | 38
LV20 | 20 | 9000 | 80 | 72 | 125 | 228.5 | 0.543 | 12.77 | 124.1 |  | 38
LV20 | 20 | 9000 | 85 | 72 | 125 | 229.1 | 0.697 | 16.43 | 159.7 |  | 38
LV20 | 20 | 9000 | 90 | 72 | 125 | 228.8 | 0.86 | 20.24 | 196.7 |  | 38
LV20 | 20 | 9000 | 80 | 77 | 125 | 247.9 | 0.362 | 9.23 | 89.7 |  | 38
LV20 | 20 | 9000 | 85 | 77 | 125 | 248.4 | 0.498 | 12.72 | 123.6 |  | 38
LV20 | 20 | 9000 | 90 | 77 | 125 | 248.4 | 0.652 | 16.66 | 161.9 |  | 38
LV20 | 20 | 10000 | 65 | 57 | 75 | 244.2 | 0.661 | 14.94 | 161.3 |  | 36
LV20 | 20 | 10000 | 70 | 57 | 75 | 245.7 | 0.833 | 18.94 | 204.6 |  | 36
LV20 | 20 | 10000 | 75 | 57 | 75 | 255 | 0.905 | 21.37 | 230.8 |  | 36
LV20 | 20 | 10000 | 80 | 57 | 75 | 270.7 | 0.905 | 22.69 | 245 |  | 36
LV20 | 20 | 10000 | 85 | 57 | 75 | 286 | 0.905 | 23.97 | 258.9 |  | 36
LV20 | 20 | 10000 | 90 | 57 | 75 | 301.7 | 0.905 | 25.28 | 273 |  | 36
LV20 | 20 | 10000 | 65 | 62 | 75 | 265.5 | 0.452 | 11.12 | 120.1 |  | 36
LV20 | 20 | 10000 | 70 | 62 | 75 | 267.6 | 0.606 | 15.02 | 162.2 |  | 36
LV20 | 20 | 10000 | 75 | 62 | 75 | 269.1 | 0.76 | 18.94 | 204.6 |  | 36
LV20 | 20 | 10000 | 80 | 62 | 75 | 271 | 0.905 | 22.71 | 245.3 |  | 36
LV20 | 20 | 10000 | 85 | 62 | 75 | 286.2 | 0.905 | 23.98 | 259 |  | 36
LV20 | 20 | 10000 | 90 | 62 | 75 | 301.7 | 0.905 | 25.29 | 273.1 |  | 36
LV20 | 20 | 10000 | 70 | 67 | 75 | 289.7 | 0.416 | 11.17 | 120.6 |  | 36
LV20 | 20 | 10000 | 75 | 67 | 75 | 291.4 | 0.561 | 15.14 | 163.5 |  | 36
LV20 | 20 | 10000 | 80 | 67 | 75 | 292.9 | 0.697 | 18.9 | 204.1 |  | 36
LV20 | 20 | 10000 | 85 | 67 | 75 | 293.7 | 0.842 | 22.89 | 247.2 |  | 36
LV20 | 20 | 10000 | 90 | 67 | 75 | 301.8 | 0.905 | 25.29 | 273.1 |  | 36
LV20 | 20 | 10000 | 75 | 72 | 75 | 314.5 | 0.38 | 11.07 | 119.6 |  | 36
LV20 | 20 | 10000 | 80 | 72 | 75 | 316.3 | 0.516 | 15.1 | 163.1 |  | 36
LV20 | 20 | 10000 | 85 | 72 | 75 | 317.1 | 0.643 | 18.87 | 203.8 |  | 36
LV20 | 20 | 10000 | 90 | 72 | 75 | 317.8 | 0.778 | 22.9 | 247.3 |  | 36
LV20 | 20 | 10000 | 80 | 77 | 75 | 341.1 | 0.353 | 11.15 | 120.4 |  | 36
LV20 | 20 | 10000 | 85 | 77 | 75 | 341.3 | 0.471 | 14.87 | 160.6 |  | 36
LV20 | 20 | 10000 | 90 | 77 | 75 | 342 | 0.597 | 18.92 | 204.3 |  | 36
LV20 | 20 | 10000 | 65 | 57 | 85 | 231.2 | 0.67 | 14.34 | 154.9 |  | 36
LV20 | 20 | 10000 | 70 | 57 | 85 | 233.1 | 0.842 | 18.17 | 196.2 |  | 36
LV20 | 20 | 10000 | 75 | 57 | 85 | 243.3 | 0.905 | 20.39 | 220.2 |  | 36
LV20 | 20 | 10000 | 80 | 57 | 85 | 258.8 | 0.905 | 21.69 | 234.2 |  | 36
LV20 | 20 | 10000 | 85 | 57 | 85 | 274 | 0.905 | 22.96 | 248 |  | 36
LV20 | 20 | 10000 | 90 | 57 | 85 | 289.2 | 0.905 | 24.23 | 261.7 |  | 36
LV20 | 20 | 10000 | 65 | 62 | 85 | 251.6 | 0.461 | 10.75 | 116.1 |  | 36
LV20 | 20 | 10000 | 70 | 62 | 85 | 253.8 | 0.615 | 14.46 | 156.2 |  | 36
LV20 | 20 | 10000 | 75 | 62 | 85 | 255.3 | 0.778 | 18.4 | 198.7 |  | 36
LV20 | 20 | 10000 | 80 | 62 | 85 | 258.8 | 0.905 | 21.69 | 234.2 |  | 36
LV20 | 20 | 10000 | 85 | 62 | 85 | 274 | 0.905 | 22.96 | 248 |  | 36
LV20 | 20 | 10000 | 90 | 62 | 85 | 289.2 | 0.905 | 24.23 | 261.7 |  | 36
LV20 | 20 | 10000 | 70 | 67 | 85 | 275.1 | 0.416 | 10.6 | 114.5 |  | 36
LV20 | 20 | 10000 | 75 | 67 | 85 | 276.8 | 0.561 | 14.38 | 155.3 |  | 36
LV20 | 20 | 10000 | 80 | 67 | 85 | 278.2 | 0.715 | 18.42 | 198.9 |  | 36
LV20 | 20 | 10000 | 85 | 67 | 85 | 279 | 0.86 | 22.21 | 239.9 |  | 36
LV20 | 20 | 10000 | 90 | 67 | 85 | 289.3 | 0.905 | 24.24 | 261.8 |  | 36
LV20 | 20 | 10000 | 75 | 72 | 85 | 299.3 | 0.38 | 10.54 | 113.8 |  | 36
LV20 | 20 | 10000 | 80 | 72 | 85 | 300.9 | 0.516 | 14.37 | 155.2 |  | 36
LV20 | 20 | 10000 | 85 | 72 | 85 | 302 | 0.652 | 18.22 | 196.8 |  | 36
LV20 | 20 | 10000 | 90 | 72 | 85 | 302.6 | 0.796 | 22.31 | 241 |  | 36
LV20 | 20 | 10000 | 80 | 77 | 85 | 324.2 | 0.353 | 10.59 | 114.4 |  | 36
LV20 | 20 | 10000 | 85 | 77 | 85 | 325.3 | 0.48 | 14.44 | 156 |  | 36
LV20 | 20 | 10000 | 90 | 77 | 85 | 325.7 | 0.606 | 18.29 | 197.5 |  | 36
LV20 | 20 | 10000 | 65 | 57 | 95 | 217.5 | 0.679 | 13.68 | 147.7 |  | 37
LV20 | 20 | 10000 | 70 | 57 | 95 | 219.3 | 0.86 | 17.46 | 188.6 |  | 37
LV20 | 20 | 10000 | 75 | 57 | 95 | 231.1 | 0.905 | 19.37 | 209.2 |  | 37
LV20 | 20 | 10000 | 80 | 57 | 95 | 246.1 | 0.905 | 20.62 | 222.7 |  | 37
LV20 | 20 | 10000 | 85 | 57 | 95 | 261.1 | 0.905 | 21.88 | 236.3 |  | 37
LV20 | 20 | 10000 | 90 | 57 | 95 | 276 | 0.905 | 23.12 | 249.7 |  | 37
LV20 | 20 | 10000 | 65 | 62 | 95 | 237.1 | 0.461 | 10.13 | 109.4 |  | 37
LV20 | 20 | 10000 | 70 | 62 | 95 | 239.3 | 0.624 | 13.83 | 149.4 |  | 37
LV20 | 20 | 10000 | 75 | 62 | 95 | 240.9 | 0.797 | 17.77 | 191.9 |  | 37
LV20 | 20 | 10000 | 80 | 62 | 95 | 246.1 | 0.905 | 20.62 | 222.7 |  | 37
LV20 | 20 | 10000 | 85 | 62 | 95 | 261.2 | 0.905 | 21.89 | 236.4 |  | 37
LV20 | 20 | 10000 | 90 | 62 | 95 | 276 | 0.905 | 23.12 | 249.7 |  | 37
LV20 | 20 | 10000 | 70 | 67 | 95 | 259.7 | 0.425 | 10.23 | 110.5 |  | 37
LV20 | 20 | 10000 | 75 | 67 | 95 | 261.5 | 0.57 | 13.81 | 149.1 |  | 37
LV20 | 20 | 10000 | 80 | 67 | 95 | 262.7 | 0.724 | 17.61 | 190.2 |  | 37
LV20 | 20 | 10000 | 85 | 67 | 95 | 263.5 | 0.878 | 21.42 | 231.3 |  | 37
LV20 | 20 | 10000 | 90 | 67 | 95 | 276 | 0.905 | 23.13 | 249.8 |  | 37
LV20 | 20 | 10000 | 75 | 72 | 95 | 282.6 | 0.389 | 10.19 | 110 |  | 37
LV20 | 20 | 10000 | 80 | 72 | 95 | 284.5 | 0.525 | 13.82 | 149.3 |  | 37
LV20 | 20 | 10000 | 85 | 72 | 95 | 285.6 | 0.669 | 17.7 | 191.2 |  | 37
LV20 | 20 | 10000 | 90 | 72 | 95 | 286.2 | 0.814 | 21.58 | 233.1 |  | 37
LV20 | 20 | 10000 | 80 | 77 | 95 | 306.8 | 0.353 | 10.03 | 108.3 |  | 37
LV20 | 20 | 10000 | 85 | 77 | 95 | 308 | 0.489 | 13.94 | 150.5 |  | 37
LV20 | 20 | 10000 | 90 | 77 | 95 | 308.6 | 0.615 | 17.58 | 189.9 |  | 37
LV20 | 20 | 10000 | 65 | 57 | 105 | 203.4 | 0.697 | 13.12 | 141.7 |  | 37
LV20 | 20 | 10000 | 70 | 57 | 105 | 205 | 0.887 | 16.83 | 181.8 |  | 37
LV20 | 20 | 10000 | 75 | 57 | 105 | 218.2 | 0.905 | 18.29 | 197.5 |  | 37
LV20 | 20 | 10000 | 80 | 57 | 105 | 232.7 | 0.905 | 19.5 | 210.6 |  | 37
LV20 | 20 | 10000 | 85 | 57 | 105 | 247.3 | 0.905 | 20.72 | 223.8 |  | 37
LV20 | 20 | 10000 | 90 | 57 | 105 | 261.5 | 0.905 | 21.91 | 236.6 |  | 37
LV20 | 20 | 10000 | 65 | 62 | 105 | 222 | 0.462 | 9.49 | 102.5 |  | 37
LV20 | 20 | 10000 | 70 | 62 | 105 | 224.1 | 0.633 | 13.14 | 141.9 |  | 37
LV20 | 20 | 10000 | 75 | 62 | 105 | 225.8 | 0.814 | 17.03 | 183.9 |  | 37
LV20 | 20 | 10000 | 80 | 62 | 105 | 232.8 | 0.905 | 19.5 | 210.6 |  | 37
LV20 | 20 | 10000 | 85 | 62 | 105 | 247.3 | 0.905 | 20.72 | 223.8 |  | 37
LV20 | 20 | 10000 | 90 | 62 | 105 | 261.7 | 0.905 | 21.93 | 236.8 |  | 37
LV20 | 20 | 10000 | 70 | 67 | 105 | 243.5 | 0.425 | 9.59 | 103.6 |  | 37
LV20 | 20 | 10000 | 75 | 67 | 105 | 245.4 | 0.588 | 13.36 | 144.3 |  | 37
LV20 | 20 | 10000 | 80 | 67 | 105 | 246.6 | 0.751 | 17.15 | 185.2 |  | 37
LV20 | 20 | 10000 | 85 | 67 | 105 | 247.5 | 0.905 | 20.74 | 224 |  | 37
LV20 | 20 | 10000 | 90 | 67 | 105 | 261.9 | 0.905 | 21.94 | 237 |  | 37
LV20 | 20 | 10000 | 75 | 72 | 105 | 265.9 | 0.389 | 9.58 | 103.5 |  | 37
LV20 | 20 | 10000 | 80 | 72 | 105 | 267.3 | 0.534 | 13.21 | 142.7 |  | 37
LV20 | 20 | 10000 | 85 | 72 | 105 | 268.2 | 0.688 | 17.07 | 184.4 |  | 37
LV20 | 20 | 10000 | 90 | 72 | 105 | 268.5 | 0.842 | 20.93 | 226 |  | 37
LV20 | 20 | 10000 | 80 | 77 | 105 | 288.8 | 0.353 | 9.44 | 101.9 |  | 37
LV20 | 20 | 10000 | 85 | 77 | 105 | 289.4 | 0.498 | 13.34 | 144.1 |  | 37
LV20 | 20 | 10000 | 90 | 77 | 105 | 290 | 0.633 | 17.01 | 183.7 |  | 37
LV20 | 20 | 10000 | 65 | 57 | 115 | 188.6 | 0.706 | 12.32 | 133.1 |  | 38
LV20 | 20 | 10000 | 70 | 57 | 115 | 190.7 | 0.905 | 15.98 | 172.6 |  | 38
LV20 | 20 | 10000 | 75 | 57 | 115 | 204.6 | 0.905 | 17.15 | 185.2 |  | 38
LV20 | 20 | 10000 | 80 | 57 | 115 | 218.6 | 0.905 | 18.32 | 197.9 |  | 38
LV20 | 20 | 10000 | 85 | 57 | 115 | 232.6 | 0.905 | 19.49 | 210.5 |  | 38
LV20 | 20 | 10000 | 90 | 57 | 115 | 246.6 | 0.905 | 20.66 | 223.1 |  | 38
LV20 | 20 | 10000 | 65 | 62 | 115 | 206.1 | 0.471 | 8.98 | 97 |  | 38
LV20 | 20 | 10000 | 70 | 62 | 115 | 208.2 | 0.652 | 12.56 | 135.7 |  | 38
LV20 | 20 | 10000 | 75 | 62 | 115 | 209.4 | 0.833 | 16.15 | 174.4 |  | 38
LV20 | 20 | 10000 | 80 | 62 | 115 | 218.7 | 0.905 | 18.32 | 197.9 |  | 38
LV20 | 20 | 10000 | 85 | 62 | 115 | 232.7 | 0.905 | 19.5 | 210.6 |  | 38
LV20 | 20 | 10000 | 90 | 62 | 115 | 246.5 | 0.905 | 20.66 | 223.1 |  | 38
LV20 | 20 | 10000 | 70 | 67 | 115 | 226.8 | 0.425 | 8.94 | 96.5 |  | 38
LV20 | 20 | 10000 | 75 | 67 | 115 | 228.6 | 0.597 | 12.64 | 136.5 |  | 38
LV20 | 20 | 10000 | 80 | 67 | 115 | 229.6 | 0.769 | 16.35 | 176.6 |  | 38
LV20 | 20 | 10000 | 85 | 67 | 115 | 232.7 | 0.905 | 19.5 | 210.6 |  | 38
LV20 | 20 | 10000 | 90 | 67 | 115 | 246.5 | 0.905 | 20.66 | 223.1 |  | 38
LV20 | 20 | 10000 | 75 | 72 | 115 | 248 | 0.389 | 8.94 | 96.5 |  | 38
LV20 | 20 | 10000 | 80 | 72 | 115 | 249.3 | 0.552 | 12.74 | 137.6 |  | 38
LV20 | 20 | 10000 | 85 | 72 | 115 | 250 | 0.706 | 16.34 | 176.5 |  | 38
LV20 | 20 | 10000 | 90 | 72 | 115 | 249.8 | 0.869 | 20.09 | 217 |  | 38
LV20 | 20 | 10000 | 80 | 77 | 115 | 269.5 | 0.362 | 9.03 | 97.5 |  | 38
LV20 | 20 | 10000 | 85 | 77 | 115 | 270.4 | 0.507 | 12.69 | 137 |  | 38
LV20 | 20 | 10000 | 90 | 77 | 115 | 270.5 | 0.652 | 16.32 | 176.3 |  | 38
LV20 | 20 | 10000 | 65 | 57 | 125 | 173.3 | 0.724 | 11.61 | 125.4 |  | 38
LV20 | 20 | 10000 | 70 | 57 | 125 | 176.8 | 0.905 | 14.81 | 160 |  | 38
LV20 | 20 | 10000 | 75 | 57 | 125 | 190.3 | 0.905 | 15.94 | 172.2 |  | 38
LV20 | 20 | 10000 | 80 | 57 | 125 | 203.8 | 0.905 | 17.08 | 184.5 |  | 38
LV20 | 20 | 10000 | 85 | 57 | 125 | 217.1 | 0.905 | 18.19 | 196.5 |  | 38
LV20 | 20 | 10000 | 90 | 57 | 125 | 230.3 | 0.905 | 19.3 | 208.4 |  | 38
LV20 | 20 | 10000 | 65 | 62 | 125 | 189.9 | 0.47 | 8.27 | 89.3 |  | 38
LV20 | 20 | 10000 | 70 | 62 | 125 | 191.7 | 0.67 | 11.89 | 128.4 |  | 38
LV20 | 20 | 10000 | 75 | 62 | 125 | 192.9 | 0.869 | 15.52 | 167.6 |  | 38
LV20 | 20 | 10000 | 80 | 62 | 125 | 203.8 | 0.905 | 17.08 | 184.5 |  | 38
LV20 | 20 | 10000 | 85 | 62 | 125 | 217.1 | 0.905 | 18.19 | 196.5 |  | 38
LV20 | 20 | 10000 | 90 | 62 | 125 | 230.3 | 0.905 | 19.3 | 208.4 |  | 38
LV20 | 20 | 10000 | 70 | 67 | 125 | 209.3 | 0.434 | 8.42 | 90.9 |  | 38
LV20 | 20 | 10000 | 75 | 67 | 125 | 210.8 | 0.615 | 12.01 | 129.7 |  | 38
LV20 | 20 | 10000 | 80 | 67 | 125 | 211.9 | 0.796 | 15.62 | 168.7 |  | 38
LV20 | 20 | 10000 | 85 | 67 | 125 | 217.2 | 0.905 | 18.19 | 196.5 |  | 38
LV20 | 20 | 10000 | 90 | 67 | 125 | 230.4 | 0.905 | 19.31 | 208.5 |  | 38
LV20 | 20 | 10000 | 75 | 72 | 125 | 229.5 | 0.398 | 8.46 | 91.4 |  | 38
LV20 | 20 | 10000 | 80 | 72 | 125 | 230.5 | 0.561 | 11.97 | 129.3 |  | 38
LV20 | 20 | 10000 | 85 | 72 | 125 | 230.8 | 0.733 | 15.67 | 169.2 |  | 38
LV20 | 20 | 10000 | 90 | 72 | 125 | 230.7 | 0.905 | 19.33 | 208.8 |  | 38
LV20 | 20 | 10000 | 80 | 77 | 125 | 249.9 | 0.362 | 8.38 | 90.5 |  | 38
LV20 | 20 | 10000 | 85 | 77 | 125 | 249.9 | 0.516 | 11.94 | 128.9 |  | 38
LV20 | 20 | 10000 | 90 | 77 | 125 | 250 | 0.679 | 15.71 | 169.7 |  | 38
LV25 | 25 | 6250 | 65 | 57 | 75 | 258.3 | 0.612 | 23.44 | 158.2 |  | 39
LV25 | 25 | 6250 | 70 | 57 | 75 | 259.9 | 0.726 | 27.94 | 188.6 |  | 39
LV25 | 25 | 6250 | 75 | 57 | 75 | 261.2 | 0.83 | 32.1 | 216.7 |  | 39
LV25 | 25 | 6250 | 80 | 57 | 75 | 263.3 | 0.933 | 36.4 | 245.7 |  | 39
LV25 | 25 | 6250 | 85 | 57 | 75 | 276.5 | 0.942 | 38.61 | 260.6 |  | 39
LV25 | 25 | 6250 | 90 | 57 | 75 | 291.1 | 0.943 | 40.65 | 274.4 |  | 39
LV25 | 25 | 6250 | 65 | 62 | 75 | 282.4 | 0.462 | 19.32 | 130.4 |  | 39
LV25 | 25 | 6250 | 70 | 62 | 75 | 283.9 | 0.566 | 23.79 | 160.6 |  | 39
LV25 | 25 | 6250 | 75 | 62 | 75 | 285.7 | 0.66 | 27.93 | 188.5 |  | 39
LV25 | 25 | 6250 | 80 | 62 | 75 | 287.3 | 0.764 | 32.5 | 219.4 |  | 39
LV25 | 25 | 6250 | 85 | 62 | 75 | 288.6 | 0.858 | 36.67 | 247.5 |  | 39
LV25 | 25 | 6250 | 90 | 62 | 75 | 291.3 | 0.943 | 40.68 | 274.6 |  | 39
LV25 | 25 | 6250 | 70 | 67 | 75 | 309.9 | 0.424 | 19.47 | 131.4 |  | 39
LV25 | 25 | 6250 | 75 | 67 | 75 | 311.3 | 0.518 | 23.91 | 161.4 |  | 39
LV25 | 25 | 6250 | 80 | 67 | 75 | 312.7 | 0.603 | 27.94 | 188.6 |  | 39
LV25 | 25 | 6250 | 85 | 67 | 75 | 313.8 | 0.698 | 32.43 | 218.9 |  | 39
LV25 | 25 | 6250 | 90 | 67 | 75 | 314.9 | 0.792 | 36.93 | 249.3 |  | 39
LV25 | 25 | 6250 | 75 | 72 | 75 | 338.2 | 0.386 | 19.36 | 130.7 |  | 39
LV25 | 25 | 6250 | 80 | 72 | 75 | 339.4 | 0.471 | 23.69 | 159.9 |  | 39
LV25 | 25 | 6250 | 85 | 72 | 75 | 340.6 | 0.556 | 28.06 | 189.4 |  | 39
LV25 | 25 | 6250 | 90 | 72 | 75 | 341.6 | 0.641 | 32.43 | 218.9 |  | 39
LV25 | 25 | 6250 | 80 | 77 | 75 | 367.9 | 0.349 | 19.01 | 128.3 |  | 39
LV25 | 25 | 6250 | 85 | 77 | 75 | 368.6 | 0.434 | 23.67 | 159.8 |  | 39
LV25 | 25 | 6250 | 90 | 77 | 75 | 369.9 | 0.509 | 27.9 | 188.3 |  | 39
LV25 | 25 | 6250 | 65 | 57 | 85 | 246 | 0.622 | 22.67 | 153 |  | 39
LV25 | 25 | 6250 | 70 | 57 | 85 | 247.8 | 0.735 | 26.99 | 182.2 |  | 39
LV25 | 25 | 6250 | 75 | 57 | 85 | 249.3 | 0.848 | 31.33 | 211.5 |  | 39
LV25 | 25 | 6250 | 80 | 57 | 85 | 251.7 | 0.943 | 35.16 | 237.3 |  | 39
LV25 | 25 | 6250 | 85 | 57 | 85 | 266.2 | 0.943 | 37.17 | 250.9 |  | 39
LV25 | 25 | 6250 | 90 | 57 | 85 | 280.5 | 0.943 | 39.17 | 264.4 |  | 39
LV25 | 25 | 6250 | 65 | 62 | 85 | 269.8 | 0.462 | 18.46 | 124.6 |  | 39
LV25 | 25 | 6250 | 70 | 62 | 85 | 271.4 | 0.566 | 22.74 | 153.5 |  | 39
LV25 | 25 | 6250 | 75 | 62 | 85 | 272.9 | 0.669 | 27.07 | 182.7 |  | 39
LV25 | 25 | 6250 | 80 | 62 | 85 | 274.4 | 0.773 | 31.42 | 212.1 |  | 39
LV25 | 25 | 6250 | 85 | 62 | 85 | 275.7 | 0.877 | 35.81 | 241.7 |  | 39
LV25 | 25 | 6250 | 90 | 62 | 85 | 280.7 | 0.942 | 39.19 | 264.5 |  | 39
LV25 | 25 | 6250 | 70 | 67 | 85 | 295.8 | 0.424 | 18.59 | 125.5 |  | 39
LV25 | 25 | 6250 | 75 | 67 | 85 | 297.2 | 0.519 | 22.83 | 154.1 |  | 39
LV25 | 25 | 6250 | 80 | 67 | 85 | 298.7 | 0.613 | 27.11 | 183 |  | 39
LV25 | 25 | 6250 | 85 | 67 | 85 | 299.9 | 0.707 | 31.41 | 212 |  | 39
LV25 | 25 | 6250 | 90 | 67 | 85 | 301 | 0.801 | 35.72 | 241.1 |  | 39
LV25 | 25 | 6250 | 75 | 72 | 85 | 323.1 | 0.387 | 18.5 | 124.9 |  | 39
LV25 | 25 | 6250 | 80 | 72 | 85 | 324.4 | 0.471 | 22.65 | 152.9 |  | 39
LV25 | 25 | 6250 | 85 | 72 | 85 | 325.6 | 0.566 | 27.29 | 184.2 |  | 39
LV25 | 25 | 6250 | 90 | 72 | 85 | 326.7 | 0.65 | 31.48 | 212.5 |  | 39
LV25 | 25 | 6250 | 80 | 77 | 85 | 351.6 | 0.349 | 18.16 | 122.6 |  | 39
LV25 | 25 | 6250 | 85 | 77 | 85 | 353 | 0.433 | 22.67 | 153 |  | 39
LV25 | 25 | 6250 | 90 | 77 | 85 | 353.9 | 0.519 | 27.19 | 183.5 |  | 39
LV25 | 25 | 6250 | 65 | 57 | 95 | 233.4 | 0.622 | 21.51 | 145.2 |  | 40
LV25 | 25 | 6250 | 70 | 57 | 95 | 234.9 | 0.745 | 25.93 | 175 |  | 40
LV25 | 25 | 6250 | 75 | 57 | 95 | 236.6 | 0.858 | 30.06 | 202.9 |  | 40
LV25 | 25 | 6250 | 80 | 57 | 95 | 240.9 | 0.943 | 33.64 | 227.1 |  | 40
LV25 | 25 | 6250 | 85 | 57 | 95 | 254.9 | 0.943 | 35.6 | 240.3 |  | 40
LV25 | 25 | 6250 | 90 | 57 | 95 | 268.8 | 0.943 | 37.54 | 253.4 |  | 40
LV25 | 25 | 6250 | 65 | 62 | 95 | 255.7 | 0.462 | 17.5 | 118.1 |  | 40
LV25 | 25 | 6250 | 70 | 62 | 95 | 257.4 | 0.575 | 21.93 | 148 |  | 40
LV25 | 25 | 6250 | 75 | 62 | 95 | 259 | 0.679 | 26.04 | 175.8 |  | 40
LV25 | 25 | 6250 | 80 | 62 | 95 | 260.4 | 0.782 | 30.18 | 203.7 |  | 40
LV25 | 25 | 6250 | 85 | 62 | 95 | 261.1 | 0.895 | 34.64 | 233.8 |  | 40
LV25 | 25 | 6250 | 90 | 62 | 95 | 269 | 0.942 | 37.56 | 253.5 |  | 40
LV25 | 25 | 6250 | 70 | 67 | 95 | 280.8 | 0.424 | 17.64 | 119.1 |  | 40
LV25 | 25 | 6250 | 75 | 67 | 95 | 282.3 | 0.519 | 21.69 | 146.4 |  | 40
LV25 | 25 | 6250 | 80 | 67 | 95 | 283.6 | 0.622 | 26.13 | 176.4 |  | 40
LV25 | 25 | 6250 | 85 | 67 | 95 | 285 | 0.716 | 30.24 | 204.1 |  | 40
LV25 | 25 | 6250 | 90 | 67 | 95 | 286 | 0.82 | 34.74 | 234.5 |  | 40
LV25 | 25 | 6250 | 75 | 72 | 95 | 306.9 | 0.386 | 17.57 | 118.6 |  | 40
LV25 | 25 | 6250 | 80 | 72 | 95 | 308.3 | 0.481 | 21.96 | 148.2 |  | 40
LV25 | 25 | 6250 | 85 | 72 | 95 | 309.6 | 0.566 | 25.94 | 175.1 |  | 40
LV25 | 25 | 6250 | 90 | 72 | 95 | 310.6 | 0.66 | 30.36 | 204.9 |  | 40
LV25 | 25 | 6250 | 80 | 77 | 95 | 334.4 | 0.349 | 17.27 | 116.6 |  | 40
LV25 | 25 | 6250 | 85 | 77 | 95 | 335.6 | 0.434 | 21.56 | 145.5 |  | 40
LV25 | 25 | 6250 | 90 | 77 | 95 | 337 | 0.518 | 25.88 | 174.7 |  | 40
LV25 | 25 | 6250 | 65 | 57 | 105 | 219.6 | 0.632 | 20.55 | 138.7 |  | 40
LV25 | 25 | 6250 | 70 | 57 | 105 | 221.3 | 0.754 | 24.73 | 166.9 |  | 40
LV25 | 25 | 6250 | 75 | 57 | 105 | 222.6 | 0.877 | 28.92 | 195.2 |  | 40
LV25 | 25 | 6250 | 80 | 57 | 105 | 229 | 0.943 | 31.99 | 215.9 |  | 40
LV25 | 25 | 6250 | 85 | 57 | 105 | 242.6 | 0.943 | 33.88 | 228.7 |  | 40
LV25 | 25 | 6250 | 90 | 57 | 105 | 256.2 | 0.943 | 35.78 | 241.5 |  | 40
LV25 | 25 | 6250 | 65 | 62 | 105 | 240.7 | 0.462 | 16.47 | 111.2 |  | 40
LV25 | 25 | 6250 | 70 | 62 | 105 | 242.4 | 0.575 | 20.64 | 139.3 |  | 40
LV25 | 25 | 6250 | 75 | 62 | 105 | 244.2 | 0.688 | 24.89 | 168 |  | 40
LV25 | 25 | 6250 | 80 | 62 | 105 | 245.4 | 0.801 | 29.13 | 196.6 |  | 40
LV25 | 25 | 6250 | 85 | 62 | 105 | 246.1 | 0.914 | 33.33 | 225 |  | 40
LV25 | 25 | 6250 | 90 | 62 | 105 | 256.5 | 0.943 | 35.82 | 241.8 |  | 40
LV25 | 25 | 6250 | 70 | 67 | 105 | 264.8 | 0.424 | 16.64 | 112.3 |  | 40
LV25 | 25 | 6250 | 75 | 67 | 105 | 266.3 | 0.528 | 20.83 | 140.6 |  | 40
LV25 | 25 | 6250 | 80 | 67 | 105 | 267.7 | 0.632 | 25.05 | 169.1 |  | 40
LV25 | 25 | 6250 | 85 | 67 | 105 | 269 | 0.735 | 29.3 | 197.8 |  | 40
LV25 | 25 | 6250 | 90 | 67 | 105 | 270 | 0.839 | 33.56 | 226.5 |  | 40
LV25 | 25 | 6250 | 75 | 72 | 105 | 289.8 | 0.386 | 16.59 | 112 |  | 40
LV25 | 25 | 6250 | 80 | 72 | 105 | 291.1 | 0.481 | 20.74 | 140 |  | 40
LV25 | 25 | 6250 | 85 | 72 | 105 | 292.4 | 0.575 | 24.9 | 168.1 |  | 40
LV25 | 25 | 6250 | 90 | 72 | 105 | 293.3 | 0.669 | 29.08 | 196.3 |  | 40
LV25 | 25 | 6250 | 80 | 77 | 105 | 316 | 0.349 | 16.33 | 110.2 |  | 40
LV25 | 25 | 6250 | 85 | 77 | 105 | 317.1 | 0.443 | 20.81 | 140.5 |  | 40
LV25 | 25 | 6250 | 90 | 77 | 105 | 318.2 | 0.528 | 24.89 | 168 |  | 40
LV25 | 25 | 6250 | 65 | 57 | 115 | 205 | 0.632 | 19.19 | 129.5 |  | 41
LV25 | 25 | 6250 | 70 | 57 | 115 | 206.7 | 0.763 | 23.38 | 157.8 |  | 41
LV25 | 25 | 6250 | 75 | 57 | 115 | 207.6 | 0.895 | 27.54 | 185.9 |  | 41
LV25 | 25 | 6250 | 80 | 57 | 115 | 216.5 | 0.943 | 30.24 | 204.1 |  | 41
LV25 | 25 | 6250 | 85 | 57 | 115 | 229.7 | 0.943 | 32.07 | 216.5 |  | 41
LV25 | 25 | 6250 | 90 | 57 | 115 | 243 | 0.942 | 33.93 | 229 |  | 41
LV25 | 25 | 6250 | 65 | 62 | 115 | 224.9 | 0.462 | 15.39 | 103.9 |  | 41
LV25 | 25 | 6250 | 70 | 62 | 115 | 226.7 | 0.584 | 19.63 | 132.5 |  | 41
LV25 | 25 | 6250 | 75 | 62 | 115 | 228.4 | 0.697 | 23.6 | 159.3 |  | 41
LV25 | 25 | 6250 | 80 | 62 | 115 | 229.7 | 0.82 | 27.91 | 188.4 |  | 41
LV25 | 25 | 6250 | 85 | 62 | 115 | 231.3 | 0.924 | 31.66 | 213.7 |  | 41
LV25 | 25 | 6250 | 90 | 62 | 115 | 243 | 0.942 | 33.93 | 229 |  | 41
LV25 | 25 | 6250 | 70 | 67 | 115 | 247.8 | 0.424 | 15.57 | 105.1 |  | 41
LV25 | 25 | 6250 | 75 | 67 | 115 | 249.4 | 0.537 | 19.85 | 134 |  | 41
LV25 | 25 | 6250 | 80 | 67 | 115 | 250.8 | 0.641 | 23.82 | 160.8 |  | 41
LV25 | 25 | 6250 | 85 | 67 | 115 | 251.8 | 0.754 | 28.13 | 189.9 |  | 41
LV25 | 25 | 6250 | 90 | 67 | 115 | 252.9 | 0.858 | 32.13 | 216.9 |  | 41
LV25 | 25 | 6250 | 75 | 72 | 115 | 271.6 | 0.387 | 15.56 | 105 |  | 41
LV25 | 25 | 6250 | 80 | 72 | 115 | 272.8 | 0.49 | 19.81 | 133.7 |  | 41
LV25 | 25 | 6250 | 85 | 72 | 115 | 274.1 | 0.584 | 23.73 | 160.2 |  | 41
LV25 | 25 | 6250 | 90 | 72 | 115 | 274.8 | 0.688 | 28.01 | 189.1 |  | 41
LV25 | 25 | 6250 | 80 | 77 | 115 | 296.4 | 0.349 | 15.32 | 103.4 |  | 41
LV25 | 25 | 6250 | 85 | 77 | 115 | 297.4 | 0.443 | 19.53 | 131.8 |  | 41
LV25 | 25 | 6250 | 90 | 77 | 115 | 298.5 | 0.537 | 23.76 | 160.4 |  | 41
LV25 | 25 | 6250 | 65 | 57 | 125 | 189.6 | 0.641 | 18 | 121.5 |  | 41
LV25 | 25 | 6250 | 70 | 57 | 125 | 191.3 | 0.782 | 22.16 | 149.6 |  | 41
LV25 | 25 | 6250 | 75 | 57 | 125 | 192.3 | 0.914 | 26.04 | 175.8 |  | 41
LV25 | 25 | 6250 | 80 | 57 | 125 | 203.1 | 0.942 | 28.36 | 191.4 |  | 41
LV25 | 25 | 6250 | 85 | 57 | 125 | 215.8 | 0.943 | 30.15 | 203.5 |  | 41
LV25 | 25 | 6250 | 90 | 57 | 125 | 228.6 | 0.943 | 31.93 | 215.5 |  | 41
LV25 | 25 | 6250 | 65 | 62 | 125 | 208.5 | 0.462 | 14.27 | 96.3 |  | 41
LV25 | 25 | 6250 | 70 | 62 | 125 | 210.3 | 0.594 | 18.5 | 124.9 |  | 41
LV25 | 25 | 6250 | 75 | 62 | 125 | 211.7 | 0.717 | 22.47 | 151.7 |  | 41
LV25 | 25 | 6250 | 80 | 62 | 125 | 212.9 | 0.839 | 26.46 | 178.6 |  | 41
LV25 | 25 | 6250 | 85 | 62 | 125 | 216 | 0.943 | 30.16 | 203.6 |  | 41
LV25 | 25 | 6250 | 90 | 62 | 125 | 228.7 | 0.943 | 31.94 | 215.6 |  | 41
LV25 | 25 | 6250 | 70 | 67 | 125 | 229.9 | 0.424 | 14.44 | 97.5 |  | 41
LV25 | 25 | 6250 | 75 | 67 | 125 | 231.5 | 0.537 | 18.43 | 124.4 |  | 41
LV25 | 25 | 6250 | 80 | 67 | 125 | 232.8 | 0.66 | 22.76 | 153.6 |  | 41
LV25 | 25 | 6250 | 85 | 67 | 125 | 233.7 | 0.773 | 26.77 | 180.7 |  | 41
LV25 | 25 | 6250 | 90 | 67 | 125 | 234.2 | 0.886 | 30.74 | 207.5 |  | 41
LV25 | 25 | 6250 | 75 | 72 | 125 | 252.2 | 0.387 | 14.44 | 97.5 |  | 41
LV25 | 25 | 6250 | 80 | 72 | 125 | 253.3 | 0.5 | 18.76 | 126.6 |  | 41
LV25 | 25 | 6250 | 85 | 72 | 125 | 254.7 | 0.603 | 22.76 | 153.6 |  | 41
LV25 | 25 | 6250 | 90 | 72 | 125 | 255.6 | 0.707 | 26.77 | 180.7 |  | 41
LV25 | 25 | 6250 | 80 | 77 | 125 | 275.7 | 0.358 | 14.62 | 98.7 |  | 41
LV25 | 25 | 6250 | 85 | 77 | 125 | 276.7 | 0.452 | 18.55 | 125.2 |  | 41
LV25 | 25 | 6250 | 90 | 77 | 125 | 277.5 | 0.556 | 22.86 | 154.3 |  | 41
LV25 | 25 | 7500 | 65 | 57 | 75 | 270.6 | 0.632 | 21.1 | 170.9 |  | 39
LV25 | 25 | 7500 | 70 | 57 | 75 | 272.3 | 0.754 | 25.35 | 205.3 |  | 39
LV25 | 25 | 7500 | 75 | 57 | 75 | 273.7 | 0.877 | 29.62 | 239.9 |  | 39
LV25 | 25 | 7500 | 80 | 57 | 75 | 281 | 0.943 | 32.7 | 264.9 |  | 39
LV25 | 25 | 7500 | 85 | 57 | 75 | 296.7 | 0.943 | 34.53 | 279.7 |  | 39
LV25 | 25 | 7500 | 90 | 57 | 75 | 312.5 | 0.943 | 36.37 | 294.6 |  | 39
LV25 | 25 | 7500 | 65 | 62 | 75 | 295.3 | 0.462 | 16.84 | 136.4 |  | 39
LV25 | 25 | 7500 | 70 | 62 | 75 | 296.9 | 0.575 | 21.07 | 170.7 |  | 39
LV25 | 25 | 7500 | 75 | 62 | 75 | 298.5 | 0.688 | 25.36 | 205.4 |  | 39
LV25 | 25 | 7500 | 80 | 62 | 75 | 300 | 0.801 | 29.67 | 240.3 |  | 39
LV25 | 25 | 7500 | 85 | 62 | 75 | 301.2 | 0.914 | 34 | 275.4 |  | 39
LV25 | 25 | 7500 | 90 | 62 | 75 | 312.7 | 0.942 | 36.38 | 294.7 |  | 39
LV25 | 25 | 7500 | 70 | 67 | 75 | 323 | 0.424 | 16.91 | 137 |  | 39
LV25 | 25 | 7500 | 75 | 67 | 75 | 324.5 | 0.528 | 21.15 | 171.3 |  | 39
LV25 | 25 | 7500 | 80 | 67 | 75 | 325.9 | 0.631 | 25.41 | 205.8 |  | 39
LV25 | 25 | 7500 | 85 | 67 | 75 | 327.1 | 0.735 | 29.69 | 240.5 |  | 39
LV25 | 25 | 7500 | 90 | 67 | 75 | 328.2 | 0.839 | 33.99 | 275.3 |  | 39
LV25 | 25 | 7500 | 75 | 72 | 75 | 351.7 | 0.386 | 16.78 | 135.9 |  | 39
LV25 | 25 | 7500 | 80 | 72 | 75 | 353.8 | 0.481 | 21 | 170.1 |  | 39
LV25 | 25 | 7500 | 85 | 72 | 75 | 354.8 | 0.575 | 25.19 | 204 |  | 39
LV25 | 25 | 7500 | 90 | 72 | 75 | 355.7 | 0.679 | 29.8 | 241.4 |  | 39
LV25 | 25 | 7500 | 80 | 77 | 75 | 382.2 | 0.349 | 16.46 | 133.3 |  | 39
LV25 | 25 | 7500 | 85 | 77 | 75 | 382.5 | 0.443 | 20.93 | 169.5 |  | 39
LV25 | 25 | 7500 | 90 | 77 | 75 | 383.6 | 0.528 | 25 | 202.5 |  | 39
LV25 | 25 | 7500 | 65 | 57 | 85 | 257.4 | 0.631 | 20.06 | 162.5 |  | 39
LV25 | 25 | 7500 | 70 | 57 | 85 | 259.3 | 0.764 | 24.44 | 198 |  | 39
LV25 | 25 | 7500 | 75 | 57 | 85 | 260.6 | 0.886 | 28.51 | 230.9 |  | 39
LV25 | 25 | 7500 | 80 | 57 | 85 | 269.9 | 0.943 | 31.41 | 254.4 |  | 39
LV25 | 25 | 7500 | 85 | 57 | 85 | 285.3 | 0.943 | 33.2 | 268.9 |  | 39
LV25 | 25 | 7500 | 90 | 57 | 85 | 300.6 | 0.942 | 34.98 | 283.3 |  | 39
LV25 | 25 | 7500 | 65 | 62 | 85 | 281.3 | 0.462 | 16.04 | 129.9 |  | 39
LV25 | 25 | 7500 | 70 | 62 | 85 | 282.8 | 0.585 | 20.41 | 165.3 |  | 39
LV25 | 25 | 7500 | 75 | 62 | 85 | 284.6 | 0.697 | 24.51 | 198.5 |  | 39
LV25 | 25 | 7500 | 80 | 62 | 85 | 285.9 | 0.81 | 28.6 | 231.7 |  | 39
LV25 | 25 | 7500 | 85 | 62 | 85 | 287.7 | 0.924 | 32.81 | 265.8 |  | 39
LV25 | 25 | 7500 | 90 | 62 | 85 | 300.8 | 0.942 | 35 | 283.5 |  | 39
LV25 | 25 | 7500 | 70 | 67 | 85 | 308 | 0.424 | 16.12 | 130.6 |  | 39
LV25 | 25 | 7500 | 75 | 67 | 85 | 309.5 | 0.528 | 20.17 | 163.4 |  | 39
LV25 | 25 | 7500 | 80 | 67 | 85 | 310.8 | 0.641 | 24.59 | 199.2 |  | 39
LV25 | 25 | 7500 | 85 | 67 | 85 | 312 | 0.745 | 28.68 | 232.3 |  | 39
LV25 | 25 | 7500 | 90 | 67 | 85 | 313.2 | 0.858 | 33.16 | 268.6 |  | 39
LV25 | 25 | 7500 | 75 | 72 | 85 | 335.9 | 0.386 | 16.02 | 129.8 |  | 39
LV25 | 25 | 7500 | 80 | 72 | 85 | 337.3 | 0.49 | 20.41 | 165.3 |  | 39
LV25 | 25 | 7500 | 85 | 72 | 85 | 338.7 | 0.584 | 24.43 | 197.9 |  | 39
LV25 | 25 | 7500 | 90 | 72 | 85 | 339.8 | 0.688 | 28.86 | 233.8 |  | 39
LV25 | 25 | 7500 | 80 | 77 | 85 | 364.4 | 0.349 | 15.69 | 127.1 |  | 39
LV25 | 25 | 7500 | 85 | 77 | 85 | 365.6 | 0.443 | 20 | 162 |  | 39
LV25 | 25 | 7500 | 90 | 77 | 85 | 366.5 | 0.537 | 24.31 | 196.9 |  | 39
LV25 | 25 | 7500 | 65 | 57 | 95 | 243.8 | 0.641 | 19.3 | 156.3 |  | 40
LV25 | 25 | 7500 | 70 | 57 | 95 | 245.6 | 0.773 | 23.43 | 189.8 |  | 40
LV25 | 25 | 7500 | 75 | 57 | 95 | 246.7 | 0.905 | 27.56 | 223.2 |  | 40
LV25 | 25 | 7500 | 80 | 57 | 95 | 257.7 | 0.943 | 29.99 | 242.9 |  | 40
LV25 | 25 | 7500 | 85 | 57 | 95 | 272.7 | 0.942 | 31.73 | 257 |  | 40
LV25 | 25 | 7500 | 90 | 57 | 95 | 287.8 | 0.943 | 33.49 | 271.3 |  | 40
LV25 | 25 | 7500 | 65 | 62 | 95 | 266 | 0.462 | 15.17 | 122.9 |  | 40
LV25 | 25 | 7500 | 70 | 62 | 95 | 267.9 | 0.585 | 19.33 | 156.6 |  | 40
LV25 | 25 | 7500 | 75 | 62 | 95 | 269.5 | 0.707 | 23.52 | 190.5 |  | 40
LV25 | 25 | 7500 | 80 | 62 | 95 | 270.7 | 0.83 | 27.73 | 224.6 |  | 40
LV25 | 25 | 7500 | 85 | 62 | 95 | 272.8 | 0.943 | 31.75 | 257.2 |  | 40
LV25 | 25 | 7500 | 90 | 62 | 95 | 287.9 | 0.943 | 33.51 | 271.4 |  | 40
LV25 | 25 | 7500 | 70 | 67 | 95 | 291.8 | 0.424 | 15.28 | 123.8 |  | 40
LV25 | 25 | 7500 | 75 | 67 | 95 | 293.4 | 0.537 | 19.46 | 157.6 |  | 40
LV25 | 25 | 7500 | 80 | 67 | 95 | 294.7 | 0.65 | 23.67 | 191.7 |  | 40
LV25 | 25 | 7500 | 85 | 67 | 95 | 295.8 | 0.763 | 27.88 | 225.8 |  | 40
LV25 | 25 | 7500 | 90 | 67 | 95 | 297 | 0.876 | 32.14 | 260.3 |  | 40
LV25 | 25 | 7500 | 75 | 72 | 95 | 318.3 | 0.386 | 15.19 | 123 |  | 40
LV25 | 25 | 7500 | 80 | 72 | 95 | 320.2 | 0.49 | 19.38 | 157 |  | 40
LV25 | 25 | 7500 | 85 | 72 | 95 | 321.4 | 0.594 | 23.56 | 190.8 |  | 40
LV25 | 25 | 7500 | 90 | 72 | 95 | 322.4 | 0.698 | 27.77 | 224.9 |  | 40
LV25 | 25 | 7500 | 80 | 77 | 95 | 346 | 0.358 | 15.3 | 123.9 |  | 40
LV25 | 25 | 7500 | 85 | 77 | 95 | 347 | 0.452 | 19.38 | 157 |  | 40
LV25 | 25 | 7500 | 90 | 77 | 95 | 348.2 | 0.547 | 23.49 | 190.3 |  | 40
LV25 | 25 | 7500 | 65 | 57 | 105 | 228.8 | 0.65 | 18.37 | 148.8 |  | 40
LV25 | 25 | 7500 | 70 | 57 | 105 | 230.5 | 0.792 | 22.53 | 182.5 |  | 40
LV25 | 25 | 7500 | 75 | 57 | 105 | 231.9 | 0.924 | 26.44 | 214.2 |  | 40
LV25 | 25 | 7500 | 80 | 57 | 105 | 244.6 | 0.943 | 28.47 | 230.6 |  | 40
LV25 | 25 | 7500 | 85 | 57 | 105 | 259.3 | 0.943 | 30.17 | 244.4 |  | 40
LV25 | 25 | 7500 | 90 | 57 | 105 | 274.1 | 0.942 | 31.89 | 258.3 |  | 40
LV25 | 25 | 7500 | 65 | 62 | 105 | 250 | 0.462 | 14.26 | 115.5 |  | 40
LV25 | 25 | 7500 | 70 | 62 | 105 | 252 | 0.594 | 18.47 | 149.6 |  | 40
LV25 | 25 | 7500 | 75 | 62 | 105 | 253.3 | 0.726 | 22.69 | 183.8 |  | 40
LV25 | 25 | 7500 | 80 | 62 | 105 | 254.6 | 0.848 | 26.67 | 216 |  | 40
LV25 | 25 | 7500 | 85 | 62 | 105 | 259.4 | 0.943 | 30.19 | 244.5 |  | 40
LV25 | 25 | 7500 | 90 | 62 | 105 | 274.1 | 0.942 | 31.89 | 258.3 |  | 40
LV25 | 25 | 7500 | 70 | 67 | 105 | 274.7 | 0.424 | 14.38 | 116.5 |  | 40
LV25 | 25 | 7500 | 75 | 67 | 105 | 276.2 | 0.547 | 18.64 | 151 |  | 40
LV25 | 25 | 7500 | 80 | 67 | 105 | 277.5 | 0.66 | 22.6 | 183.1 |  | 40
LV25 | 25 | 7500 | 85 | 67 | 105 | 278.6 | 0.782 | 26.91 | 218 |  | 40
LV25 | 25 | 7500 | 90 | 67 | 105 | 279.6 | 0.895 | 30.9 | 250.3 |  | 40
LV25 | 25 | 7500 | 75 | 72 | 105 | 300.3 | 0.386 | 14.32 | 116 |  | 40
LV25 | 25 | 7500 | 80 | 72 | 105 | 301.8 | 0.5 | 18.62 | 150.8 |  | 40
LV25 | 25 | 7500 | 85 | 72 | 105 | 303.1 | 0.603 | 22.57 | 182.8 |  | 40
LV25 | 25 | 7500 | 90 | 72 | 105 | 304.3 | 0.716 | 26.91 | 218 |  | 40
LV25 | 25 | 7500 | 80 | 77 | 105 | 326.3 | 0.358 | 14.43 | 116.9 |  | 40
LV25 | 25 | 7500 | 85 | 77 | 105 | 327.5 | 0.453 | 18.3 | 148.2 |  | 40
LV25 | 25 | 7500 | 90 | 77 | 105 | 328.3 | 0.556 | 22.54 | 182.6 |  | 40
LV25 | 25 | 7500 | 65 | 57 | 115 | 213.2 | 0.66 | 17.37 | 140.7 |  | 41
LV25 | 25 | 7500 | 70 | 57 | 115 | 214.9 | 0.801 | 21.25 | 172.1 |  | 41
LV25 | 25 | 7500 | 75 | 57 | 115 | 216.6 | 0.943 | 25.21 | 204.2 |  | 41
LV25 | 25 | 7500 | 80 | 57 | 115 | 230.8 | 0.942 | 26.85 | 217.5 |  | 41
LV25 | 25 | 7500 | 85 | 57 | 115 | 244.8 | 0.943 | 28.49 | 230.8 |  | 41
LV25 | 25 | 7500 | 90 | 57 | 115 | 259.2 | 0.943 | 30.16 | 244.3 |  | 41
LV25 | 25 | 7500 | 65 | 62 | 115 | 233.1 | 0.471 | 13.57 | 109.9 |  | 41
LV25 | 25 | 7500 | 70 | 62 | 115 | 235.1 | 0.603 | 17.51 | 141.8 |  | 41
LV25 | 25 | 7500 | 75 | 62 | 115 | 236.6 | 0.735 | 21.47 | 173.9 |  | 41
LV25 | 25 | 7500 | 80 | 62 | 115 | 237.3 | 0.877 | 25.69 | 208.1 |  | 41
LV25 | 25 | 7500 | 85 | 62 | 115 | 245.2 | 0.943 | 28.54 | 231.2 |  | 41
LV25 | 25 | 7500 | 90 | 62 | 115 | 259.3 | 0.943 | 30.17 | 244.4 |  | 41
LV25 | 25 | 7500 | 70 | 67 | 115 | 256.6 | 0.424 | 13.44 | 108.9 |  | 41
LV25 | 25 | 7500 | 75 | 67 | 115 | 258.1 | 0.556 | 17.72 | 143.5 |  | 41
LV25 | 25 | 7500 | 80 | 67 | 115 | 259.3 | 0.679 | 21.73 | 176 |  | 41
LV25 | 25 | 7500 | 85 | 67 | 115 | 260.6 | 0.801 | 25.78 | 208.8 |  | 41
LV25 | 25 | 7500 | 90 | 67 | 115 | 261.9 | 0.924 | 29.86 | 241.9 |  | 41
LV25 | 25 | 7500 | 75 | 72 | 115 | 281.1 | 0.386 | 13.41 | 108.6 |  | 41
LV25 | 25 | 7500 | 80 | 72 | 115 | 282.6 | 0.509 | 17.75 | 143.8 |  | 41
LV25 | 25 | 7500 | 85 | 72 | 115 | 283.5 | 0.622 | 21.78 | 176.4 |  | 41
LV25 | 25 | 7500 | 90 | 72 | 115 | 284.4 | 0.735 | 25.81 | 209.1 |  | 41
LV25 | 25 | 7500 | 80 | 77 | 115 | 305.3 | 0.358 | 13.49 | 109.3 |  | 41
LV25 | 25 | 7500 | 85 | 77 | 115 | 306.5 | 0.462 | 17.47 | 141.5 |  | 41
LV25 | 25 | 7500 | 90 | 77 | 115 | 307.2 | 0.575 | 21.81 | 176.7 |  | 41
LV25 | 25 | 7500 | 65 | 57 | 125 | 196.7 | 0.669 | 16.25 | 131.6 |  | 41
LV25 | 25 | 7500 | 70 | 57 | 125 | 198.8 | 0.82 | 20.12 | 163 |  | 41
LV25 | 25 | 7500 | 75 | 57 | 125 | 202.4 | 0.943 | 23.56 | 190.8 |  | 41
LV25 | 25 | 7500 | 80 | 57 | 125 | 216.1 | 0.943 | 25.15 | 203.7 |  | 41
LV25 | 25 | 7500 | 85 | 57 | 125 | 229.6 | 0.943 | 26.73 | 216.5 |  | 41
LV25 | 25 | 7500 | 90 | 57 | 125 | 243.4 | 0.943 | 28.33 | 229.5 |  | 41
LV25 | 25 | 7500 | 65 | 62 | 125 | 215.4 | 0.471 | 12.53 | 101.5 |  | 41
LV25 | 25 | 7500 | 70 | 62 | 125 | 217.3 | 0.613 | 16.44 | 133.2 |  | 41
LV25 | 25 | 7500 | 75 | 62 | 125 | 218.7 | 0.754 | 20.36 | 164.9 |  | 41
LV25 | 25 | 7500 | 80 | 62 | 125 | 219.6 | 0.905 | 24.53 | 198.7 |  | 41
LV25 | 25 | 7500 | 85 | 62 | 125 | 229.8 | 0.943 | 26.74 | 216.6 |  | 41
LV25 | 25 | 7500 | 90 | 62 | 125 | 243.5 | 0.943 | 28.33 | 229.5 |  | 41
LV25 | 25 | 7500 | 70 | 67 | 125 | 237.2 | 0.434 | 12.7 | 102.9 |  | 41
LV25 | 25 | 7500 | 75 | 67 | 125 | 239 | 0.565 | 16.68 | 135.1 |  | 41
LV25 | 25 | 7500 | 80 | 67 | 125 | 240.4 | 0.698 | 20.7 | 167.7 |  | 41
LV25 | 25 | 7500 | 85 | 67 | 125 | 241.3 | 0.83 | 24.72 | 200.2 |  | 41
LV25 | 25 | 7500 | 90 | 67 | 125 | 243.6 | 0.943 | 28.35 | 229.6 |  | 41
LV25 | 25 | 7500 | 75 | 72 | 125 | 260.9 | 0.396 | 12.75 | 103.3 |  | 41
LV25 | 25 | 7500 | 80 | 72 | 125 | 262 | 0.518 | 16.77 | 135.8 |  | 41
LV25 | 25 | 7500 | 85 | 72 | 125 | 263 | 0.641 | 20.81 | 168.6 |  | 41
LV25 | 25 | 7500 | 90 | 72 | 125 | 263.7 | 0.763 | 24.85 | 201.3 |  | 41
LV25 | 25 | 7500 | 80 | 77 | 125 | 283.4 | 0.358 | 12.53 | 101.5 |  | 41
LV25 | 25 | 7500 | 85 | 77 | 125 | 284.2 | 0.471 | 16.54 | 134 |  | 41
LV25 | 25 | 7500 | 90 | 77 | 125 | 285 | 0.585 | 20.57 | 166.6 |  | 41
LV25 | 25 | 8750 | 65 | 57 | 75 | 279.8 | 0.641 | 18.97 | 179.3 |  | 39
LV25 | 25 | 8750 | 70 | 57 | 75 | 281.5 | 0.783 | 23.31 | 220.3 |  | 39
LV25 | 25 | 8750 | 75 | 57 | 75 | 282.8 | 0.914 | 27.37 | 258.6 |  | 39
LV25 | 25 | 8750 | 80 | 57 | 75 | 296.6 | 0.943 | 29.59 | 279.6 |  | 39
LV25 | 25 | 8750 | 85 | 57 | 75 | 313.4 | 0.943 | 31.26 | 295.4 |  | 39
LV25 | 25 | 8750 | 90 | 57 | 75 | 329.9 | 0.943 | 32.91 | 311 |  | 39
LV25 | 25 | 8750 | 65 | 62 | 75 | 304.9 | 0.462 | 14.9 | 140.8 |  | 39
LV25 | 25 | 8750 | 70 | 62 | 75 | 306.8 | 0.594 | 19.28 | 182.2 |  | 39
LV25 | 25 | 8750 | 75 | 62 | 75 | 308.2 | 0.716 | 23.37 | 220.8 |  | 39
LV25 | 25 | 8750 | 80 | 62 | 75 | 309.7 | 0.839 | 27.49 | 259.8 |  | 39
LV25 | 25 | 8750 | 85 | 62 | 75 | 313.6 | 0.943 | 31.28 | 295.6 |  | 39
LV25 | 25 | 8750 | 90 | 62 | 75 | 330.1 | 0.942 | 32.92 | 311.1 |  | 39
LV25 | 25 | 8750 | 70 | 67 | 75 | 333.1 | 0.424 | 14.95 | 141.3 |  | 39
LV25 | 25 | 8750 | 75 | 67 | 75 | 334.9 | 0.537 | 19.04 | 179.9 |  | 39
LV25 | 25 | 8750 | 80 | 67 | 75 | 336.2 | 0.66 | 23.47 | 221.8 |  | 39
LV25 | 25 | 8750 | 85 | 67 | 75 | 337.4 | 0.773 | 27.6 | 260.8 |  | 39
LV25 | 25 | 8750 | 90 | 67 | 75 | 337.9 | 0.886 | 31.68 | 299.4 |  | 39
LV25 | 25 | 8750 | 75 | 72 | 75 | 362.2 | 0.387 | 14.81 | 140 |  | 39
LV25 | 25 | 8750 | 80 | 72 | 75 | 363.6 | 0.499 | 19.22 | 181.6 |  | 39
LV25 | 25 | 8750 | 85 | 72 | 75 | 364.6 | 0.603 | 23.28 | 220 |  | 39
LV25 | 25 | 8750 | 90 | 72 | 75 | 365.5 | 0.707 | 27.34 | 258.4 |  | 39
LV25 | 25 | 8750 | 80 | 77 | 75 | 392.7 | 0.358 | 14.89 | 140.7 |  | 39
LV25 | 25 | 8750 | 85 | 77 | 75 | 393.5 | 0.452 | 18.84 | 178 |  | 39
LV25 | 25 | 8750 | 90 | 77 | 75 | 394.4 | 0.556 | 23.21 | 219.3 |  | 39
LV25 | 25 | 8750 | 65 | 57 | 85 | 266 | 0.65 | 18.31 | 173 |  | 39
LV25 | 25 | 8750 | 70 | 57 | 85 | 267.5 | 0.792 | 22.41 | 211.8 |  | 39
LV25 | 25 | 8750 | 75 | 57 | 85 | 269.8 | 0.924 | 26.37 | 249.2 |  | 39
LV25 | 25 | 8750 | 80 | 57 | 85 | 284.5 | 0.943 | 28.38 | 268.2 |  | 39
LV25 | 25 | 8750 | 85 | 57 | 85 | 300.7 | 0.943 | 30 | 283.5 |  | 39
LV25 | 25 | 8750 | 90 | 57 | 85 | 317.3 | 0.943 | 31.65 | 299.1 |  | 39
LV25 | 25 | 8750 | 65 | 62 | 85 | 290 | 0.462 | 14.17 | 133.9 |  | 39
LV25 | 25 | 8750 | 70 | 62 | 85 | 291.8 | 0.594 | 18.34 | 173.3 |  | 39
LV25 | 25 | 8750 | 75 | 62 | 85 | 293.3 | 0.726 | 22.53 | 212.9 |  | 39
LV25 | 25 | 8750 | 80 | 62 | 85 | 295 | 0.858 | 26.77 | 253 |  | 39
LV25 | 25 | 8750 | 85 | 62 | 85 | 300.9 | 0.943 | 30.02 | 283.7 |  | 39
LV25 | 25 | 8750 | 90 | 62 | 85 | 317.2 | 0.943 | 31.64 | 299 |  | 39
LV25 | 25 | 8750 | 70 | 67 | 85 | 317.1 | 0.424 | 14.23 | 134.5 |  | 39
LV25 | 25 | 8750 | 75 | 67 | 85 | 318.9 | 0.547 | 18.44 | 174.3 |  | 39
LV25 | 25 | 8750 | 80 | 67 | 85 | 320.4 | 0.669 | 22.69 | 214.4 |  | 39
LV25 | 25 | 8750 | 85 | 67 | 85 | 321.6 | 0.792 | 26.94 | 254.6 |  | 39
LV25 | 25 | 8750 | 90 | 67 | 85 | 322.4 | 0.905 | 30.88 | 291.8 |  | 39
LV25 | 25 | 8750 | 75 | 72 | 85 | 345.2 | 0.386 | 14.12 | 133.4 |  | 39
LV25 | 25 | 8750 | 80 | 72 | 85 | 346.6 | 0.499 | 18.32 | 173.1 |  | 39
LV25 | 25 | 8750 | 85 | 72 | 85 | 347.6 | 0.613 | 22.54 | 213 |  | 39
LV25 | 25 | 8750 | 90 | 72 | 85 | 348.5 | 0.726 | 26.77 | 253 |  | 39
LV25 | 25 | 8750 | 80 | 77 | 85 | 374.3 | 0.358 | 14.19 | 134.1 |  | 39
LV25 | 25 | 8750 | 85 | 77 | 85 | 375.4 | 0.462 | 18.35 | 173.4 |  | 39
LV25 | 25 | 8750 | 90 | 77 | 85 | 376.5 | 0.565 | 22.53 | 212.9 |  | 39
LV25 | 25 | 8750 | 65 | 57 | 95 | 251.1 | 0.66 | 17.53 | 165.7 |  | 40
LV25 | 25 | 8750 | 70 | 57 | 95 | 253 | 0.811 | 21.7 | 205.1 |  | 40
LV25 | 25 | 8750 | 75 | 57 | 95 | 255.3 | 0.943 | 25.47 | 240.7 |  | 40
LV25 | 25 | 8750 | 80 | 57 | 95 | 271.3 | 0.943 | 27.07 | 255.8 |  | 40
LV25 | 25 | 8750 | 85 | 57 | 95 | 287.4 | 0.943 | 28.67 | 270.9 |  | 40
LV25 | 25 | 8750 | 90 | 57 | 95 | 303.3 | 0.943 | 30.25 | 285.9 |  | 40
LV25 | 25 | 8750 | 65 | 62 | 95 | 273.9 | 0.471 | 13.66 | 129.1 |  | 40
LV25 | 25 | 8750 | 70 | 62 | 95 | 275.9 | 0.603 | 17.61 | 166.4 |  | 40
LV25 | 25 | 8750 | 75 | 62 | 95 | 277.3 | 0.745 | 21.85 | 206.5 |  | 40
LV25 | 25 | 8750 | 80 | 62 | 95 | 278.3 | 0.877 | 25.82 | 244 |  | 40
LV25 | 25 | 8750 | 85 | 62 | 95 | 287.5 | 0.943 | 28.68 | 271 |  | 40
LV25 | 25 | 8750 | 90 | 62 | 95 | 303.2 | 0.943 | 30.24 | 285.8 |  | 40
LV25 | 25 | 8750 | 70 | 67 | 95 | 300 | 0.424 | 13.46 | 127.2 |  | 40
LV25 | 25 | 8750 | 75 | 67 | 95 | 301.9 | 0.556 | 17.77 | 167.9 |  | 40
LV25 | 25 | 8750 | 80 | 67 | 95 | 303.3 | 0.679 | 21.79 | 205.9 |  | 40
LV25 | 25 | 8750 | 85 | 67 | 95 | 304.4 | 0.801 | 25.81 | 243.9 |  | 40
LV25 | 25 | 8750 | 90 | 67 | 95 | 306 | 0.924 | 29.92 | 282.7 |  | 40
LV25 | 25 | 8750 | 75 | 72 | 95 | 327.1 | 0.386 | 13.38 | 126.4 |  | 40
LV25 | 25 | 8750 | 80 | 72 | 95 | 328.4 | 0.509 | 17.68 | 167.1 |  | 40
LV25 | 25 | 8750 | 85 | 72 | 95 | 329.5 | 0.622 | 21.69 | 205 |  | 40
LV25 | 25 | 8750 | 90 | 72 | 95 | 330.6 | 0.745 | 26.05 | 246.2 |  | 40
LV25 | 25 | 8750 | 80 | 77 | 95 | 355.2 | 0.358 | 13.46 | 127.2 |  | 40
LV25 | 25 | 8750 | 85 | 77 | 95 | 356.2 | 0.462 | 17.41 | 164.5 |  | 40
LV25 | 25 | 8750 | 90 | 77 | 95 | 357.1 | 0.575 | 21.72 | 205.3 |  | 40
LV25 | 25 | 8750 | 65 | 57 | 105 | 235.4 | 0.669 | 16.67 | 157.5 |  | 40
LV25 | 25 | 8750 | 70 | 57 | 105 | 237.1 | 0.82 | 20.58 | 194.5 |  | 40
LV25 | 25 | 8750 | 75 | 57 | 105 | 241.8 | 0.943 | 24.13 | 228 |  | 40
LV25 | 25 | 8750 | 80 | 57 | 105 | 257.3 | 0.942 | 25.66 | 242.5 |  | 40
LV25 | 25 | 8750 | 85 | 57 | 105 | 272.8 | 0.943 | 27.22 | 257.2 |  | 40
LV25 | 25 | 8750 | 90 | 57 | 105 | 288.3 | 0.942 | 28.75 | 271.7 |  | 40
LV25 | 25 | 8750 | 65 | 62 | 105 | 257.1 | 0.471 | 12.83 | 121.2 |  | 40
LV25 | 25 | 8750 | 70 | 62 | 105 | 258.9 | 0.613 | 16.78 | 158.6 |  | 40
LV25 | 25 | 8750 | 75 | 62 | 105 | 260.4 | 0.754 | 20.77 | 196.3 |  | 40
LV25 | 25 | 8750 | 80 | 62 | 105 | 261.7 | 0.895 | 24.79 | 234.3 |  | 40
LV25 | 25 | 8750 | 85 | 62 | 105 | 272.7 | 0.942 | 27.2 | 257 |  | 40
LV25 | 25 | 8750 | 90 | 62 | 105 | 288.5 | 0.943 | 28.78 | 272 |  | 40
LV25 | 25 | 8750 | 70 | 67 | 105 | 282 | 0.434 | 12.94 | 122.3 |  | 40
LV25 | 25 | 8750 | 75 | 67 | 105 | 283.9 | 0.565 | 16.98 | 160.5 |  | 40
LV25 | 25 | 8750 | 80 | 67 | 105 | 285.2 | 0.698 | 21.06 | 199 |  | 40
LV25 | 25 | 8750 | 85 | 67 | 105 | 286.3 | 0.83 | 25.13 | 237.5 |  | 40
LV25 | 25 | 8750 | 90 | 67 | 105 | 288.5 | 0.942 | 28.77 | 271.9 |  | 40
LV25 | 25 | 8750 | 75 | 72 | 105 | 307.6 | 0.396 | 12.89 | 121.8 |  | 40
LV25 | 25 | 8750 | 80 | 72 | 105 | 309 | 0.518 | 16.95 | 160.2 |  | 40
LV25 | 25 | 8750 | 85 | 72 | 105 | 310.4 | 0.641 | 21.05 | 198.9 |  | 40
LV25 | 25 | 8750 | 90 | 72 | 105 | 311.1 | 0.763 | 25.13 | 237.5 |  | 40
LV25 | 25 | 8750 | 80 | 77 | 105 | 334.3 | 0.358 | 12.67 | 119.7 |  | 40
LV25 | 25 | 8750 | 85 | 77 | 105 | 335.5 | 0.471 | 16.73 | 158.1 |  | 40
LV25 | 25 | 8750 | 90 | 77 | 105 | 336.3 | 0.585 | 20.8 | 196.6 |  | 40
LV25 | 25 | 8750 | 65 | 57 | 115 | 218.9 | 0.679 | 15.72 | 148.6 |  | 41
LV25 | 25 | 8750 | 70 | 57 | 115 | 220.4 | 0.848 | 19.79 | 187 |  | 41
LV25 | 25 | 8750 | 75 | 57 | 115 | 227.4 | 0.943 | 22.69 | 214.4 |  | 41
LV25 | 25 | 8750 | 80 | 57 | 115 | 242.3 | 0.943 | 24.17 | 228.4 |  | 41
LV25 | 25 | 8750 | 85 | 57 | 115 | 257.2 | 0.943 | 25.66 | 242.5 |  | 41
LV25 | 25 | 8750 | 90 | 57 | 115 | 272.3 | 0.943 | 27.16 | 256.7 |  | 41
LV25 | 25 | 8750 | 65 | 62 | 115 | 239.4 | 0.471 | 11.94 | 112.8 |  | 41
LV25 | 25 | 8750 | 70 | 62 | 115 | 241.1 | 0.622 | 15.87 | 150 |  | 41
LV25 | 25 | 8750 | 75 | 62 | 115 | 242.6 | 0.773 | 19.84 | 187.5 |  | 41
LV25 | 25 | 8750 | 80 | 62 | 115 | 244.4 | 0.923 | 23.88 | 225.7 |  | 41
LV25 | 25 | 8750 | 85 | 62 | 115 | 257.4 | 0.943 | 25.67 | 242.6 |  | 41
LV25 | 25 | 8750 | 90 | 62 | 115 | 272.4 | 0.943 | 27.17 | 256.8 |  | 41
LV25 | 25 | 8750 | 70 | 67 | 115 | 263.2 | 0.434 | 12.07 | 114.1 |  | 41
LV25 | 25 | 8750 | 75 | 67 | 115 | 264.8 | 0.575 | 16.12 | 152.3 |  | 41
LV25 | 25 | 8750 | 80 | 67 | 115 | 266.2 | 0.707 | 19.92 | 188.2 |  | 41
LV25 | 25 | 8750 | 85 | 67 | 115 | 267.1 | 0.848 | 23.97 | 226.5 |  | 41
LV25 | 25 | 8750 | 90 | 67 | 115 | 272.4 | 0.943 | 27.17 | 256.8 |  | 41
LV25 | 25 | 8750 | 75 | 72 | 115 | 287.2 | 0.396 | 12.03 | 113.7 |  | 41
LV25 | 25 | 8750 | 80 | 72 | 115 | 288.7 | 0.528 | 16.13 | 152.4 |  | 41
LV25 | 25 | 8750 | 85 | 72 | 115 | 289.7 | 0.65 | 19.94 | 188.4 |  | 41
LV25 | 25 | 8750 | 90 | 72 | 115 | 290.5 | 0.782 | 24.05 | 227.3 |  | 41
LV25 | 25 | 8750 | 80 | 77 | 115 | 312.6 | 0.358 | 11.85 | 112 |  | 41
LV25 | 25 | 8750 | 85 | 77 | 115 | 313.6 | 0.481 | 15.95 | 150.7 |  | 41
LV25 | 25 | 8750 | 90 | 77 | 115 | 314.3 | 0.603 | 20.06 | 189.6 |  | 41
LV25 | 25 | 8750 | 65 | 57 | 125 | 201.5 | 0.698 | 14.88 | 140.6 |  | 41
LV25 | 25 | 8750 | 70 | 57 | 125 | 203.2 | 0.867 | 18.65 | 176.2 |  | 41
LV25 | 25 | 8750 | 75 | 57 | 125 | 211.9 | 0.943 | 21.14 | 199.8 |  | 41
LV25 | 25 | 8750 | 80 | 57 | 125 | 226.5 | 0.943 | 22.59 | 213.5 |  | 41
LV25 | 25 | 8750 | 85 | 57 | 125 | 240.9 | 0.943 | 24.03 | 227.1 |  | 41
LV25 | 25 | 8750 | 90 | 57 | 125 | 255.3 | 0.943 | 25.47 | 240.7 |  | 41
LV25 | 25 | 8750 | 65 | 62 | 125 | 220.7 | 0.471 | 11.01 | 104 |  | 41
LV25 | 25 | 8750 | 70 | 62 | 125 | 222.5 | 0.631 | 14.87 | 140.5 |  | 41
LV25 | 25 | 8750 | 75 | 62 | 125 | 224.1 | 0.801 | 18.99 | 179.5 |  | 41
LV25 | 25 | 8750 | 80 | 62 | 125 | 226.6 | 0.942 | 22.59 | 213.5 |  | 41
LV25 | 25 | 8750 | 85 | 62 | 125 | 241 | 0.942 | 24.03 | 227.1 |  | 41
LV25 | 25 | 8750 | 90 | 62 | 125 | 255.4 | 0.942 | 25.47 | 240.7 |  | 41
LV25 | 25 | 8750 | 70 | 67 | 125 | 243.2 | 0.434 | 11.16 | 105.5 |  | 41
LV25 | 25 | 8750 | 75 | 67 | 125 | 245 | 0.584 | 15.15 | 143.2 |  | 41
LV25 | 25 | 8750 | 80 | 67 | 125 | 246 | 0.735 | 19.14 | 180.9 |  | 41
LV25 | 25 | 8750 | 85 | 67 | 125 | 246.5 | 0.886 | 23.11 | 218.4 |  | 41
LV25 | 25 | 8750 | 90 | 67 | 125 | 255.4 | 0.942 | 25.47 | 240.7 |  | 41
LV25 | 25 | 8750 | 75 | 72 | 125 | 265.8 | 0.396 | 11.13 | 105.2 |  | 41
LV25 | 25 | 8750 | 80 | 72 | 125 | 267.2 | 0.537 | 15.2 | 143.6 |  | 41
LV25 | 25 | 8750 | 85 | 72 | 125 | 268.1 | 0.669 | 18.98 | 179.4 |  | 41
LV25 | 25 | 8750 | 90 | 72 | 125 | 268.8 | 0.811 | 23.06 | 217.9 |  | 41
LV25 | 25 | 8750 | 80 | 77 | 125 | 289.5 | 0.368 | 11.26 | 106.4 |  | 41
LV25 | 25 | 8750 | 85 | 77 | 125 | 290.2 | 0.49 | 15.06 | 142.3 |  | 41
LV25 | 25 | 8750 | 90 | 77 | 125 | 291.1 | 0.622 | 19.16 | 181.1 |  | 41
LV25 | 25 | 10000 | 65 | 57 | 75 | 286.8 | 0.66 | 17.52 | 189.2 |  | 39
LV25 | 25 | 10000 | 70 | 57 | 75 | 288.5 | 0.811 | 21.66 | 233.9 |  | 39
LV25 | 25 | 10000 | 75 | 57 | 75 | 292.1 | 0.942 | 25.49 | 275.3 |  | 39
LV25 | 25 | 10000 | 80 | 57 | 75 | 309.8 | 0.943 | 27.04 | 292 |  | 39
LV25 | 25 | 10000 | 85 | 57 | 75 | 327.1 | 0.943 | 28.55 | 308.3 |  | 39
LV25 | 25 | 10000 | 90 | 57 | 75 | 344.6 | 0.943 | 30.07 | 324.8 |  | 39
LV25 | 25 | 10000 | 65 | 62 | 75 | 312.3 | 0.471 | 13.63 | 147.2 |  | 39
LV25 | 25 | 10000 | 70 | 62 | 75 | 314.4 | 0.603 | 17.56 | 189.7 |  | 39
LV25 | 25 | 10000 | 75 | 62 | 75 | 315.9 | 0.745 | 21.78 | 235.2 |  | 39
LV25 | 25 | 10000 | 80 | 62 | 75 | 317.3 | 0.886 | 26.03 | 281.1 |  | 39
LV25 | 25 | 10000 | 85 | 62 | 75 | 327.2 | 0.943 | 28.56 | 308.4 |  | 39
LV25 | 25 | 10000 | 90 | 62 | 75 | 344.9 | 0.943 | 30.1 | 325.1 |  | 39
LV25 | 25 | 10000 | 70 | 67 | 75 | 340.6 | 0.424 | 13.38 | 144.5 |  | 39
LV25 | 25 | 10000 | 75 | 67 | 75 | 342.7 | 0.556 | 17.65 | 190.6 |  | 39
LV25 | 25 | 10000 | 80 | 67 | 75 | 344.1 | 0.688 | 21.93 | 236.8 |  | 39
LV25 | 25 | 10000 | 85 | 67 | 75 | 345.4 | 0.811 | 25.93 | 280 |  | 39
LV25 | 25 | 10000 | 90 | 67 | 75 | 347.1 | 0.924 | 29.69 | 320.6 |  | 39
LV25 | 25 | 10000 | 75 | 72 | 75 | 369.9 | 0.396 | 13.56 | 146.5 |  | 39
LV25 | 25 | 10000 | 80 | 72 | 75 | 371.7 | 0.509 | 17.52 | 189.2 |  | 39
LV25 | 25 | 10000 | 85 | 72 | 75 | 372.9 | 0.632 | 21.81 | 235.5 |  | 39
LV25 | 25 | 10000 | 90 | 72 | 75 | 373.6 | 0.745 | 25.76 | 278.2 |  | 39
LV25 | 25 | 10000 | 80 | 77 | 75 | 401 | 0.358 | 13.3 | 143.6 |  | 39
LV25 | 25 | 10000 | 85 | 77 | 75 | 401.4 | 0.471 | 17.52 | 189.2 |  | 39
LV25 | 25 | 10000 | 90 | 77 | 75 | 402.4 | 0.575 | 21.43 | 231.4 |  | 39
LV25 | 25 | 10000 | 65 | 57 | 85 | 272.5 | 0.669 | 16.89 | 182.4 |  | 39
LV25 | 25 | 10000 | 70 | 57 | 85 | 274.2 | 0.83 | 21.06 | 227.5 |  | 39
LV25 | 25 | 10000 | 75 | 57 | 85 | 279.6 | 0.942 | 24.4 | 263.5 |  | 39
LV25 | 25 | 10000 | 80 | 57 | 85 | 296.7 | 0.943 | 25.9 | 279.7 |  | 39
LV25 | 25 | 10000 | 85 | 57 | 85 | 313.8 | 0.943 | 27.39 | 295.8 |  | 39
LV25 | 25 | 10000 | 90 | 57 | 85 | 330.9 | 0.943 | 28.88 | 311.9 |  | 39
LV25 | 25 | 10000 | 65 | 62 | 85 | 296.4 | 0.471 | 12.94 | 139.7 |  | 39
LV25 | 25 | 10000 | 70 | 62 | 85 | 298.6 | 0.613 | 16.94 | 183 |  | 39
LV25 | 25 | 10000 | 75 | 62 | 85 | 300.2 | 0.754 | 20.96 | 226.4 |  | 39
LV25 | 25 | 10000 | 80 | 62 | 85 | 301.6 | 0.896 | 25.01 | 270.1 |  | 39
LV25 | 25 | 10000 | 85 | 62 | 85 | 313.9 | 0.943 | 27.4 | 295.9 |  | 39
LV25 | 25 | 10000 | 90 | 62 | 85 | 331 | 0.943 | 28.89 | 312 |  | 39
LV25 | 25 | 10000 | 70 | 67 | 85 | 324.1 | 0.434 | 13.01 | 140.5 |  | 39
LV25 | 25 | 10000 | 75 | 67 | 85 | 326 | 0.566 | 17.07 | 184.4 |  | 39
LV25 | 25 | 10000 | 80 | 67 | 85 | 327.4 | 0.698 | 21.15 | 228.4 |  | 39
LV25 | 25 | 10000 | 85 | 67 | 85 | 328.7 | 0.83 | 25.25 | 272.7 |  | 39
LV25 | 25 | 10000 | 90 | 67 | 85 | 331.1 | 0.943 | 28.9 | 312.1 |  | 39
LV25 | 25 | 10000 | 75 | 72 | 85 | 352.4 | 0.396 | 12.92 | 139.5 |  | 39
LV25 | 25 | 10000 | 80 | 72 | 85 | 354 | 0.518 | 16.99 | 183.5 |  | 39
LV25 | 25 | 10000 | 85 | 72 | 85 | 355.3 | 0.641 | 21.08 | 227.7 |  | 39
LV25 | 25 | 10000 | 90 | 72 | 85 | 356.2 | 0.764 | 25.19 | 272 |  | 39
LV25 | 25 | 10000 | 80 | 77 | 85 | 381.5 | 0.358 | 12.65 | 136.6 |  | 39
LV25 | 25 | 10000 | 85 | 77 | 85 | 383 | 0.471 | 16.71 | 180.5 |  | 39
LV25 | 25 | 10000 | 90 | 77 | 85 | 383.9 | 0.585 | 20.78 | 224.4 |  | 39
LV25 | 25 | 10000 | 65 | 57 | 95 | 257 | 0.679 | 16.15 | 174.4 |  | 40
LV25 | 25 | 10000 | 70 | 57 | 95 | 258.5 | 0.839 | 20.08 | 216.9 |  | 40
LV25 | 25 | 10000 | 75 | 57 | 95 | 266 | 0.942 | 23.21 | 250.7 |  | 40
LV25 | 25 | 10000 | 80 | 57 | 95 | 282.7 | 0.942 | 24.67 | 266.4 |  | 40
LV25 | 25 | 10000 | 85 | 57 | 95 | 299.3 | 0.943 | 26.13 | 282.2 |  | 40
LV25 | 25 | 10000 | 90 | 57 | 95 | 316.2 | 0.942 | 27.59 | 298 |  | 40
LV25 | 25 | 10000 | 65 | 62 | 95 | 279.8 | 0.471 | 12.21 | 131.9 |  | 40
LV25 | 25 | 10000 | 70 | 62 | 95 | 282 | 0.622 | 16.24 | 175.4 |  | 40
LV25 | 25 | 10000 | 75 | 62 | 95 | 283.6 | 0.773 | 20.3 | 219.2 |  | 40
LV25 | 25 | 10000 | 80 | 62 | 95 | 285.2 | 0.924 | 24.39 | 263.4 |  | 40
LV25 | 25 | 10000 | 85 | 62 | 95 | 299.5 | 0.943 | 26.14 | 282.3 |  | 40
LV25 | 25 | 10000 | 90 | 62 | 95 | 316.2 | 0.943 | 27.6 | 298.1 |  | 40
LV25 | 25 | 10000 | 70 | 67 | 95 | 306.3 | 0.434 | 12.3 | 132.8 |  | 40
LV25 | 25 | 10000 | 75 | 67 | 95 | 308.3 | 0.566 | 16.15 | 174.4 |  | 40
LV25 | 25 | 10000 | 80 | 67 | 95 | 309.6 | 0.707 | 20.26 | 218.8 |  | 40
LV25 | 25 | 10000 | 85 | 67 | 95 | 310.9 | 0.849 | 24.43 | 263.8 |  | 40
LV25 | 25 | 10000 | 90 | 67 | 95 | 316.3 | 0.942 | 27.6 | 298.1 |  | 40
LV25 | 25 | 10000 | 75 | 72 | 95 | 333.7 | 0.396 | 12.23 | 132.1 |  | 40
LV25 | 25 | 10000 | 80 | 72 | 95 | 335.3 | 0.518 | 16.09 | 173.8 |  | 40
LV25 | 25 | 10000 | 85 | 72 | 95 | 336.5 | 0.65 | 20.26 | 218.8 |  | 40
LV25 | 25 | 10000 | 90 | 72 | 95 | 337.4 | 0.782 | 24.44 | 264 |  | 40
LV25 | 25 | 10000 | 80 | 77 | 95 | 361.6 | 0.358 | 11.99 | 129.5 |  | 40
LV25 | 25 | 10000 | 85 | 77 | 95 | 362.9 | 0.481 | 16.16 | 174.5 |  | 40
LV25 | 25 | 10000 | 90 | 77 | 95 | 363.8 | 0.603 | 20.32 | 219.5 |  | 40
LV25 | 25 | 10000 | 65 | 57 | 105 | 240.5 | 0.688 | 15.32 | 165.5 |  | 40
LV25 | 25 | 10000 | 70 | 57 | 105 | 242.1 | 0.857 | 19.22 | 207.6 |  | 40
LV25 | 25 | 10000 | 75 | 57 | 105 | 251.6 | 0.942 | 21.95 | 237.1 |  | 40
LV25 | 25 | 10000 | 80 | 57 | 105 | 267.8 | 0.942 | 23.37 | 252.4 |  | 40
LV25 | 25 | 10000 | 85 | 57 | 105 | 284 | 0.943 | 24.79 | 267.7 |  | 40
LV25 | 25 | 10000 | 90 | 57 | 105 | 300.1 | 0.943 | 26.19 | 282.9 |  | 40
LV25 | 25 | 10000 | 65 | 62 | 105 | 262.2 | 0.471 | 11.44 | 123.6 |  | 40
LV25 | 25 | 10000 | 70 | 62 | 105 | 264.5 | 0.631 | 15.46 | 167 |  | 40
LV25 | 25 | 10000 | 75 | 62 | 105 | 266.5 | 0.792 | 19.54 | 211 |  | 40
LV25 | 25 | 10000 | 80 | 62 | 105 | 268.5 | 0.933 | 23.19 | 250.5 |  | 40
LV25 | 25 | 10000 | 85 | 62 | 105 | 284.1 | 0.943 | 24.8 | 267.8 |  | 40
LV25 | 25 | 10000 | 90 | 62 | 105 | 300.2 | 0.942 | 26.19 | 282.9 |  | 40
LV25 | 25 | 10000 | 70 | 67 | 105 | 287.5 | 0.434 | 11.55 | 124.7 |  | 40
LV25 | 25 | 10000 | 75 | 67 | 105 | 289.6 | 0.575 | 15.42 | 166.5 |  | 40
LV25 | 25 | 10000 | 80 | 67 | 105 | 290.6 | 0.726 | 19.53 | 210.9 |  | 40
LV25 | 25 | 10000 | 85 | 67 | 105 | 291.9 | 0.877 | 23.69 | 255.9 |  | 40
LV25 | 25 | 10000 | 90 | 67 | 105 | 300.4 | 0.943 | 26.22 | 283.2 |  | 40
LV25 | 25 | 10000 | 75 | 72 | 105 | 313.7 | 0.396 | 11.5 | 124.2 |  | 40
LV25 | 25 | 10000 | 80 | 72 | 105 | 315.3 | 0.528 | 15.41 | 166.4 |  | 40
LV25 | 25 | 10000 | 85 | 72 | 105 | 316.3 | 0.669 | 19.6 | 211.7 |  | 40
LV25 | 25 | 10000 | 90 | 72 | 105 | 317.1 | 0.801 | 23.52 | 254 |  | 40
LV25 | 25 | 10000 | 80 | 77 | 105 | 340.3 | 0.368 | 11.58 | 125.1 |  | 40
LV25 | 25 | 10000 | 85 | 77 | 105 | 341.6 | 0.49 | 15.5 | 167.4 |  | 40
LV25 | 25 | 10000 | 90 | 77 | 105 | 342.4 | 0.613 | 19.43 | 209.8 |  | 40
LV25 | 25 | 10000 | 65 | 57 | 115 | 223.2 | 0.707 | 14.61 | 157.8 |  | 41
LV25 | 25 | 10000 | 70 | 57 | 115 | 224.7 | 0.886 | 18.44 | 199.1 |  | 41
LV25 | 25 | 10000 | 75 | 57 | 115 | 236.2 | 0.942 | 20.61 | 222.6 |  | 41
LV25 | 25 | 10000 | 80 | 57 | 115 | 251.9 | 0.942 | 21.98 | 237.4 |  | 41
LV25 | 25 | 10000 | 85 | 57 | 115 | 267.6 | 0.943 | 23.36 | 252.3 |  | 41
LV25 | 25 | 10000 | 90 | 57 | 115 | 283.2 | 0.942 | 24.71 | 266.9 |  | 41
LV25 | 25 | 10000 | 65 | 62 | 115 | 243.9 | 0.481 | 10.86 | 117.3 |  | 41
LV25 | 25 | 10000 | 70 | 62 | 115 | 246.2 | 0.641 | 14.61 | 157.8 |  | 41
LV25 | 25 | 10000 | 75 | 62 | 115 | 247.7 | 0.811 | 18.59 | 200.8 |  | 41
LV25 | 25 | 10000 | 80 | 62 | 115 | 251.9 | 0.943 | 21.99 | 237.5 |  | 41
LV25 | 25 | 10000 | 85 | 62 | 115 | 267.7 | 0.942 | 23.36 | 252.3 |  | 41
LV25 | 25 | 10000 | 90 | 62 | 115 | 283.2 | 0.943 | 24.72 | 267 |  | 41
LV25 | 25 | 10000 | 70 | 67 | 115 | 267.8 | 0.434 | 10.75 | 116.1 |  | 41
LV25 | 25 | 10000 | 75 | 67 | 115 | 269.7 | 0.594 | 14.83 | 160.2 |  | 41
LV25 | 25 | 10000 | 80 | 67 | 115 | 271.1 | 0.745 | 18.69 | 201.9 |  | 41
LV25 | 25 | 10000 | 85 | 67 | 115 | 272.1 | 0.895 | 22.56 | 243.6 |  | 41
LV25 | 25 | 10000 | 90 | 67 | 115 | 283.5 | 0.943 | 24.74 | 267.2 |  | 41
LV25 | 25 | 10000 | 75 | 72 | 115 | 292.6 | 0.396 | 10.72 | 115.8 |  | 41
LV25 | 25 | 10000 | 80 | 72 | 115 | 294.1 | 0.547 | 14.89 | 160.8 |  | 41
LV25 | 25 | 10000 | 85 | 72 | 115 | 295.2 | 0.688 | 18.81 | 203.1 |  | 41
LV25 | 25 | 10000 | 90 | 72 | 115 | 295.6 | 0.829 | 22.7 | 245.2 |  | 41
LV25 | 25 | 10000 | 80 | 77 | 115 | 317.8 | 0.368 | 10.81 | 116.8 |  | 41
LV25 | 25 | 10000 | 85 | 77 | 115 | 318.9 | 0.5 | 14.75 | 159.3 |  | 41
LV25 | 25 | 10000 | 90 | 77 | 115 | 319.5 | 0.632 | 18.69 | 201.8 |  | 41
LV25 | 25 | 10000 | 65 | 57 | 125 | 205.1 | 0.716 | 13.6 | 146.9 |  | 41
LV25 | 25 | 10000 | 70 | 57 | 125 | 206.7 | 0.914 | 17.5 | 189 |  | 41
LV25 | 25 | 10000 | 75 | 57 | 125 | 220 | 0.943 | 19.2 | 207.4 |  | 41
LV25 | 25 | 10000 | 80 | 57 | 125 | 235.2 | 0.943 | 20.53 | 221.7 |  | 41
LV25 | 25 | 10000 | 85 | 57 | 125 | 250 | 0.943 | 21.82 | 235.7 |  | 41
LV25 | 25 | 10000 | 90 | 57 | 125 | 265 | 0.943 | 23.13 | 249.8 |  | 41
LV25 | 25 | 10000 | 65 | 62 | 125 | 224.7 | 0.481 | 10 | 108 |  | 41
LV25 | 25 | 10000 | 70 | 62 | 125 | 226.9 | 0.66 | 13.86 | 149.7 |  | 41
LV25 | 25 | 10000 | 75 | 62 | 125 | 228.2 | 0.839 | 17.72 | 191.4 |  | 41
LV25 | 25 | 10000 | 80 | 62 | 125 | 235.2 | 0.943 | 20.53 | 221.7 |  | 41
LV25 | 25 | 10000 | 85 | 62 | 125 | 250.1 | 0.943 | 21.83 | 235.8 |  | 41
LV25 | 25 | 10000 | 90 | 62 | 125 | 265 | 0.943 | 23.13 | 249.8 |  | 41
LV25 | 25 | 10000 | 70 | 67 | 125 | 247.2 | 0.443 | 10.14 | 109.5 |  | 41
LV25 | 25 | 10000 | 75 | 67 | 125 | 249.1 | 0.603 | 13.92 | 150.3 |  | 41
LV25 | 25 | 10000 | 80 | 67 | 125 | 250.4 | 0.773 | 17.93 | 193.6 |  | 41
LV25 | 25 | 10000 | 85 | 67 | 125 | 251.5 | 0.924 | 21.52 | 232.4 |  | 41
LV25 | 25 | 10000 | 90 | 67 | 125 | 265.1 | 0.943 | 23.14 | 249.9 |  | 41
LV25 | 25 | 10000 | 75 | 72 | 125 | 270.7 | 0.405 | 10.16 | 109.7 |  | 41
LV25 | 25 | 10000 | 80 | 72 | 125 | 272 | 0.556 | 14.01 | 151.3 |  | 41
LV25 | 25 | 10000 | 85 | 72 | 125 | 272.9 | 0.707 | 17.86 | 192.9 |  | 41
LV25 | 25 | 10000 | 90 | 72 | 125 | 272.8 | 0.867 | 21.91 | 236.6 |  | 41
LV25 | 25 | 10000 | 80 | 77 | 125 | 294.4 | 0.368 | 10.02 | 108.2 |  | 41
LV25 | 25 | 10000 | 85 | 77 | 125 | 295.2 | 0.509 | 13.91 | 150.2 |  | 41
LV25 | 25 | 10000 | 90 | 77 | 125 | 295.6 | 0.651 | 17.81 | 192.3 |  | 41
LV25 | 25 | 11250 | 65 | 57 | 75 | 292.7 | 0.679 | 16.35 | 198.6 |  | 39
LV25 | 25 | 11250 | 70 | 57 | 75 | 294.5 | 0.839 | 20.34 | 247.1 |  | 39
LV25 | 25 | 11250 | 75 | 57 | 75 | 302.6 | 0.942 | 23.47 | 285.2 |  | 39
LV25 | 25 | 11250 | 80 | 57 | 75 | 320.7 | 0.943 | 24.88 | 302.3 |  | 39
LV25 | 25 | 11250 | 85 | 57 | 75 | 338.8 | 0.942 | 26.28 | 319.3 |  | 39
LV25 | 25 | 11250 | 90 | 57 | 75 | 357.1 | 0.943 | 27.7 | 336.6 |  | 39
LV25 | 25 | 11250 | 65 | 62 | 75 | 318.5 | 0.471 | 12.35 | 150.1 |  | 39
LV25 | 25 | 11250 | 70 | 62 | 75 | 320.6 | 0.622 | 16.42 | 199.5 |  | 39
LV25 | 25 | 11250 | 75 | 62 | 75 | 322.3 | 0.773 | 20.5 | 249.1 |  | 39
LV25 | 25 | 11250 | 80 | 62 | 75 | 323.5 | 0.924 | 24.59 | 298.8 |  | 39
LV25 | 25 | 11250 | 85 | 62 | 75 | 338.9 | 0.943 | 26.3 | 319.5 |  | 39
LV25 | 25 | 11250 | 90 | 62 | 75 | 357.2 | 0.943 | 27.71 | 336.7 |  | 39
LV25 | 25 | 11250 | 70 | 67 | 75 | 346.8 | 0.434 | 12.38 | 150.4 |  | 39
LV25 | 25 | 11250 | 75 | 67 | 75 | 348.6 | 0.575 | 16.5 | 200.5 |  | 39
LV25 | 25 | 11250 | 80 | 67 | 75 | 350 | 0.707 | 20.36 | 247.4 |  | 39
LV25 | 25 | 11250 | 85 | 67 | 75 | 351.3 | 0.848 | 24.53 | 298 |  | 39
LV25 | 25 | 11250 | 90 | 67 | 75 | 357.3 | 0.943 | 27.72 | 336.8 |  | 39
LV25 | 25 | 11250 | 75 | 72 | 75 | 376.4 | 0.396 | 12.26 | 149 |  | 39
LV25 | 25 | 11250 | 80 | 72 | 75 | 378.2 | 0.528 | 16.43 | 199.6 |  | 39
LV25 | 25 | 11250 | 85 | 72 | 75 | 379.3 | 0.65 | 20.3 | 246.7 |  | 39
LV25 | 25 | 11250 | 90 | 72 | 75 | 380.2 | 0.782 | 24.49 | 297.5 |  | 39
LV25 | 25 | 11250 | 80 | 77 | 75 | 407.5 | 0.358 | 12.02 | 146 |  | 39
LV25 | 25 | 11250 | 85 | 77 | 75 | 408.3 | 0.481 | 16.16 | 196.3 |  | 39
LV25 | 25 | 11250 | 90 | 77 | 75 | 409.1 | 0.603 | 20.31 | 246.8 |  | 39
LV25 | 25 | 11250 | 65 | 57 | 85 | 277.6 | 0.688 | 15.72 | 191 |  | 39
LV25 | 25 | 11250 | 70 | 57 | 85 | 279.4 | 0.858 | 19.73 | 239.7 |  | 39
LV25 | 25 | 11250 | 75 | 57 | 85 | 289.1 | 0.943 | 22.43 | 272.5 |  | 39
LV25 | 25 | 11250 | 80 | 57 | 85 | 306.9 | 0.943 | 23.81 | 289.3 |  | 39
LV25 | 25 | 11250 | 85 | 57 | 85 | 324.8 | 0.942 | 25.19 | 306.1 |  | 39
LV25 | 25 | 11250 | 90 | 57 | 85 | 342.6 | 0.942 | 26.58 | 322.9 |  | 39
LV25 | 25 | 11250 | 65 | 62 | 85 | 302.1 | 0.471 | 11.72 | 142.4 |  | 39
LV25 | 25 | 11250 | 70 | 62 | 85 | 304.5 | 0.632 | 15.83 | 192.3 |  | 39
LV25 | 25 | 11250 | 75 | 62 | 85 | 306.4 | 0.782 | 19.73 | 239.7 |  | 39
LV25 | 25 | 11250 | 80 | 62 | 85 | 308.2 | 0.933 | 23.67 | 287.6 |  | 39
LV25 | 25 | 11250 | 85 | 62 | 85 | 324.8 | 0.943 | 25.2 | 306.2 |  | 39
LV25 | 25 | 11250 | 90 | 62 | 85 | 342.7 | 0.943 | 26.58 | 323 |  | 39
LV25 | 25 | 11250 | 70 | 67 | 85 | 329.6 | 0.434 | 11.76 | 142.9 |  | 39
LV25 | 25 | 11250 | 75 | 67 | 85 | 331.5 | 0.575 | 15.69 | 190.6 |  | 39
LV25 | 25 | 11250 | 80 | 67 | 85 | 332.7 | 0.726 | 19.88 | 241.5 |  | 39
LV25 | 25 | 11250 | 85 | 67 | 85 | 334 | 0.867 | 23.84 | 289.6 |  | 39
LV25 | 25 | 11250 | 90 | 67 | 85 | 342.6 | 0.942 | 26.58 | 322.9 |  | 39
LV25 | 25 | 11250 | 75 | 72 | 85 | 358.3 | 0.396 | 11.67 | 141.8 |  | 39
LV25 | 25 | 11250 | 80 | 72 | 85 | 359.8 | 0.528 | 15.63 | 189.9 |  | 39
LV25 | 25 | 11250 | 85 | 72 | 85 | 360.8 | 0.669 | 19.88 | 241.5 |  | 39
LV25 | 25 | 11250 | 90 | 72 | 85 | 362 | 0.801 | 23.87 | 290 |  | 39
LV25 | 25 | 11250 | 80 | 77 | 85 | 387.8 | 0.368 | 11.74 | 142.6 |  | 39
LV25 | 25 | 11250 | 85 | 77 | 85 | 389.1 | 0.49 | 15.7 | 190.7 |  | 39
LV25 | 25 | 11250 | 90 | 77 | 85 | 389.8 | 0.613 | 19.65 | 238.8 |  | 39
LV25 | 25 | 11250 | 65 | 57 | 95 | 261.4 | 0.697 | 15 | 182.3 |  | 40
LV25 | 25 | 11250 | 70 | 57 | 95 | 263.3 | 0.877 | 19 | 230.8 |  | 40
LV25 | 25 | 11250 | 75 | 57 | 95 | 275 | 0.943 | 21.33 | 259.2 |  | 40
LV25 | 25 | 11250 | 80 | 57 | 95 | 292.3 | 0.943 | 22.67 | 275.5 |  | 40
LV25 | 25 | 11250 | 85 | 57 | 95 | 309.6 | 0.943 | 24.02 | 291.8 |  | 40
LV25 | 25 | 11250 | 90 | 57 | 95 | 326.9 | 0.943 | 25.37 | 308.2 |  | 40
LV25 | 25 | 11250 | 65 | 62 | 95 | 284.8 | 0.481 | 11.27 | 136.9 |  | 40
LV25 | 25 | 11250 | 70 | 62 | 95 | 287.3 | 0.641 | 15.15 | 184.1 |  | 40
LV25 | 25 | 11250 | 75 | 62 | 95 | 289 | 0.801 | 19.05 | 231.5 |  | 40
LV25 | 25 | 11250 | 80 | 62 | 95 | 292.4 | 0.943 | 22.68 | 275.6 |  | 40
LV25 | 25 | 11250 | 85 | 62 | 95 | 309.7 | 0.943 | 24.02 | 291.9 |  | 40
LV25 | 25 | 11250 | 90 | 62 | 95 | 327.1 | 0.943 | 25.37 | 308.3 |  | 40
LV25 | 25 | 11250 | 70 | 67 | 95 | 311.2 | 0.433 | 11.1 | 134.9 |  | 40
LV25 | 25 | 11250 | 75 | 67 | 95 | 313.2 | 0.584 | 15.06 | 183 |  | 40
LV25 | 25 | 11250 | 80 | 67 | 95 | 314.4 | 0.735 | 19.02 | 231.1 |  | 40
LV25 | 25 | 11250 | 85 | 67 | 95 | 315.9 | 0.886 | 23.04 | 279.9 |  | 40
LV25 | 25 | 11250 | 90 | 67 | 95 | 327.1 | 0.943 | 25.37 | 308.3 |  | 40
LV25 | 25 | 11250 | 75 | 72 | 95 | 338.6 | 0.396 | 11.04 | 134.1 |  | 40
LV25 | 25 | 11250 | 80 | 72 | 95 | 340.5 | 0.537 | 15.06 | 183 |  | 40
LV25 | 25 | 11250 | 85 | 72 | 95 | 341.7 | 0.679 | 19.09 | 231.9 |  | 40
LV25 | 25 | 11250 | 90 | 72 | 95 | 342.6 | 0.82 | 23.12 | 280.9 |  | 40
LV25 | 25 | 11250 | 80 | 77 | 95 | 367.2 | 0.368 | 11.11 | 135 |  | 40
LV25 | 25 | 11250 | 85 | 77 | 95 | 368.4 | 0.499 | 15.14 | 184 |  | 40
LV25 | 25 | 11250 | 90 | 77 | 95 | 369.3 | 0.631 | 19.19 | 233.2 |  | 40
LV25 | 25 | 11250 | 65 | 57 | 105 | 244.4 | 0.707 | 14.22 | 172.8 |  | 40
LV25 | 25 | 11250 | 70 | 57 | 105 | 246.3 | 0.896 | 18.16 | 220.6 |  | 40
LV25 | 25 | 11250 | 75 | 57 | 105 | 259.7 | 0.943 | 20.15 | 244.8 |  | 40
LV25 | 25 | 11250 | 80 | 57 | 105 | 276.5 | 0.943 | 21.46 | 260.7 |  | 40
LV25 | 25 | 11250 | 85 | 57 | 105 | 293.5 | 0.943 | 22.77 | 276.7 |  | 40
LV25 | 25 | 11250 | 90 | 57 | 105 | 310.3 | 0.943 | 24.07 | 292.5 |  | 40
LV25 | 25 | 11250 | 65 | 62 | 105 | 266.8 | 0.481 | 10.55 | 128.2 |  | 40
LV25 | 25 | 11250 | 70 | 62 | 105 | 269.1 | 0.65 | 14.4 | 175 |  | 40
LV25 | 25 | 11250 | 75 | 62 | 105 | 270.6 | 0.829 | 18.47 | 224.4 |  | 40
LV25 | 25 | 11250 | 80 | 62 | 105 | 276.6 | 0.943 | 21.46 | 260.7 |  | 40
LV25 | 25 | 11250 | 85 | 62 | 105 | 293.5 | 0.943 | 22.77 | 276.7 |  | 40
LV25 | 25 | 11250 | 90 | 62 | 105 | 310.3 | 0.943 | 24.07 | 292.5 |  | 40
LV25 | 25 | 11250 | 70 | 67 | 105 | 291.7 | 0.443 | 10.63 | 129.2 |  | 40
LV25 | 25 | 11250 | 75 | 67 | 105 | 293.8 | 0.594 | 14.36 | 174.5 |  | 40
LV25 | 25 | 11250 | 80 | 67 | 105 | 295.2 | 0.754 | 18.32 | 222.6 |  | 40
LV25 | 25 | 11250 | 85 | 67 | 105 | 296.4 | 0.914 | 22.3 | 271 |  | 40
LV25 | 25 | 11250 | 90 | 67 | 105 | 310.5 | 0.942 | 24.08 | 292.6 |  | 40
LV25 | 25 | 11250 | 75 | 72 | 105 | 317.9 | 0.405 | 10.6 | 128.8 |  | 40
LV25 | 25 | 11250 | 80 | 72 | 105 | 320 | 0.547 | 14.4 | 174.9 |  | 40
LV25 | 25 | 11250 | 85 | 72 | 105 | 320.6 | 0.697 | 18.4 | 223.6 |  | 40
LV25 | 25 | 11250 | 90 | 72 | 105 | 321.1 | 0.848 | 22.42 | 272.4 |  | 40
LV25 | 25 | 11250 | 80 | 77 | 105 | 345.4 | 0.368 | 10.45 | 127 |  | 40
LV25 | 25 | 11250 | 85 | 77 | 105 | 346.3 | 0.509 | 14.51 | 176.3 |  | 40
LV25 | 25 | 11250 | 90 | 77 | 105 | 347.1 | 0.641 | 18.31 | 222.5 |  | 40
LV25 | 25 | 11250 | 65 | 57 | 115 | 226.8 | 0.726 | 13.55 | 164.6 |  | 41
LV25 | 25 | 11250 | 70 | 57 | 115 | 228.9 | 0.924 | 17.4 | 211.4 |  | 41
LV25 | 25 | 11250 | 75 | 57 | 115 | 243.7 | 0.943 | 18.91 | 229.7 |  | 41
LV25 | 25 | 11250 | 80 | 57 | 115 | 260 | 0.942 | 20.16 | 245 |  | 41
LV25 | 25 | 11250 | 85 | 57 | 115 | 276.2 | 0.943 | 21.43 | 260.4 |  | 41
LV25 | 25 | 11250 | 90 | 57 | 115 | 292.4 | 0.943 | 22.68 | 275.6 |  | 41
LV25 | 25 | 11250 | 65 | 62 | 115 | 247.8 | 0.481 | 9.8 | 119.1 |  | 41
LV25 | 25 | 11250 | 70 | 62 | 115 | 250.1 | 0.669 | 13.78 | 167.4 |  | 41
LV25 | 25 | 11250 | 75 | 62 | 115 | 251.1 | 0.848 | 17.53 | 213 |  | 41
LV25 | 25 | 11250 | 80 | 62 | 115 | 260 | 0.943 | 20.17 | 245.1 |  | 41
LV25 | 25 | 11250 | 85 | 62 | 115 | 276.2 | 0.943 | 21.43 | 260.4 |  | 41
LV25 | 25 | 11250 | 90 | 62 | 115 | 292.3 | 0.943 | 22.67 | 275.5 |  | 41
LV25 | 25 | 11250 | 70 | 67 | 115 | 271.5 | 0.443 | 9.9 | 120.3 |  | 41
LV25 | 25 | 11250 | 75 | 67 | 115 | 273.6 | 0.613 | 13.79 | 167.6 |  | 41
LV25 | 25 | 11250 | 80 | 67 | 115 | 274.8 | 0.782 | 17.7 | 215 |  | 41
LV25 | 25 | 11250 | 85 | 67 | 115 | 276.9 | 0.933 | 21.27 | 258.4 |  | 41
LV25 | 25 | 11250 | 90 | 67 | 115 | 292.2 | 0.943 | 22.67 | 275.4 |  | 41
LV25 | 25 | 11250 | 75 | 72 | 115 | 297.1 | 0.405 | 9.91 | 120.4 |  | 41
LV25 | 25 | 11250 | 80 | 72 | 115 | 297.8 | 0.565 | 13.86 | 168.4 |  | 41
LV25 | 25 | 11250 | 85 | 72 | 115 | 298.8 | 0.717 | 17.62 | 214.1 |  | 41
LV25 | 25 | 11250 | 90 | 72 | 115 | 299.1 | 0.877 | 21.58 | 262.2 |  | 41
LV25 | 25 | 11250 | 80 | 77 | 115 | 322.1 | 0.368 | 9.74 | 118.4 |  | 41
LV25 | 25 | 11250 | 85 | 77 | 115 | 323 | 0.519 | 13.79 | 167.5 |  | 41
LV25 | 25 | 11250 | 90 | 77 | 115 | 323.6 | 0.66 | 17.57 | 213.5 |  | 41
LV25 | 25 | 11250 | 65 | 57 | 125 | 208.4 | 0.744 | 12.77 | 155.1 |  | 41
LV25 | 25 | 11250 | 70 | 57 | 125 | 211.1 | 0.943 | 16.38 | 199 |  | 41
LV25 | 25 | 11250 | 75 | 57 | 125 | 226.6 | 0.943 | 17.58 | 213.6 |  | 41
LV25 | 25 | 11250 | 80 | 57 | 125 | 242.4 | 0.943 | 18.81 | 228.5 |  | 41
LV25 | 25 | 11250 | 85 | 57 | 125 | 257.9 | 0.943 | 20.01 | 243.1 |  | 41
LV25 | 25 | 11250 | 90 | 57 | 125 | 273.3 | 0.943 | 21.2 | 257.6 |  | 41
LV25 | 25 | 11250 | 65 | 62 | 125 | 228 | 0.49 | 9.2 | 111.8 |  | 41
LV25 | 25 | 11250 | 70 | 62 | 125 | 230.3 | 0.679 | 12.86 | 156.3 |  | 41
LV25 | 25 | 11250 | 75 | 62 | 125 | 231.5 | 0.876 | 16.7 | 202.9 |  | 41
LV25 | 25 | 11250 | 80 | 62 | 125 | 242.2 | 0.943 | 18.79 | 228.3 |  | 41
LV25 | 25 | 11250 | 85 | 62 | 125 | 257.9 | 0.943 | 20.01 | 243.1 |  | 41
LV25 | 25 | 11250 | 90 | 62 | 125 | 273.3 | 0.943 | 21.2 | 257.6 |  | 41
LV25 | 25 | 11250 | 70 | 67 | 125 | 250.3 | 0.453 | 9.33 | 113.3 |  | 41
LV25 | 25 | 11250 | 75 | 67 | 125 | 252.4 | 0.632 | 13.12 | 159.4 |  | 41
LV25 | 25 | 11250 | 80 | 67 | 125 | 253.3 | 0.811 | 16.9 | 205.3 |  | 41
LV25 | 25 | 11250 | 85 | 67 | 125 | 257.9 | 0.943 | 20.01 | 243.1 |  | 41
LV25 | 25 | 11250 | 90 | 67 | 125 | 273.5 | 0.943 | 21.22 | 257.8 |  | 41
LV25 | 25 | 11250 | 75 | 72 | 125 | 273.8 | 0.415 | 9.34 | 113.5 |  | 41
LV25 | 25 | 11250 | 80 | 72 | 125 | 275.2 | 0.575 | 13.02 | 158.2 |  | 41
LV25 | 25 | 11250 | 85 | 72 | 125 | 276 | 0.745 | 16.91 | 205.5 |  | 41
LV25 | 25 | 11250 | 90 | 72 | 125 | 276.2 | 0.914 | 20.78 | 252.5 |  | 41
LV25 | 25 | 11250 | 80 | 77 | 125 | 297.4 | 0.377 | 9.23 | 112.1 |  | 41
LV25 | 25 | 11250 | 85 | 77 | 125 | 298.7 | 0.528 | 12.98 | 157.7 |  | 41
LV25 | 25 | 11250 | 90 | 77 | 125 | 298.9 | 0.688 | 16.93 | 205.7 |  | 41
LV25 | 25 | 12500 | 65 | 57 | 75 | 297.6 | 0.698 | 15.38 | 207.6 |  | 39
LV25 | 25 | 12500 | 70 | 57 | 75 | 299.3 | 0.876 | 19.43 | 262.3 |  | 39
LV25 | 25 | 12500 | 75 | 57 | 75 | 311.5 | 0.943 | 21.75 | 293.6 |  | 39
LV25 | 25 | 12500 | 80 | 57 | 75 | 330.2 | 0.943 | 23.06 | 311.3 |  | 39
LV25 | 25 | 12500 | 85 | 57 | 75 | 348.9 | 0.943 | 24.36 | 328.9 |  | 39
LV25 | 25 | 12500 | 90 | 57 | 75 | 367.7 | 0.943 | 25.67 | 346.6 |  | 39
LV25 | 25 | 12500 | 65 | 62 | 75 | 323.2 | 0.471 | 11.28 | 152.3 |  | 39
LV25 | 25 | 12500 | 70 | 62 | 75 | 325.4 | 0.641 | 15.45 | 208.6 |  | 39
LV25 | 25 | 12500 | 75 | 62 | 75 | 327.3 | 0.801 | 19.42 | 262.2 |  | 39
LV25 | 25 | 12500 | 80 | 62 | 75 | 330.3 | 0.943 | 23.07 | 311.4 |  | 39
LV25 | 25 | 12500 | 85 | 62 | 75 | 348.8 | 0.943 | 24.36 | 328.8 |  | 39
LV25 | 25 | 12500 | 90 | 62 | 75 | 367.9 | 0.943 | 25.69 | 346.8 |  | 39
LV25 | 25 | 12500 | 70 | 67 | 75 | 352 | 0.434 | 11.3 | 152.6 |  | 39
LV25 | 25 | 12500 | 75 | 67 | 75 | 354 | 0.584 | 15.33 | 206.9 |  | 39
LV25 | 25 | 12500 | 80 | 67 | 75 | 355.3 | 0.735 | 19.35 | 261.2 |  | 39
LV25 | 25 | 12500 | 85 | 67 | 75 | 356.1 | 0.886 | 23.37 | 315.5 |  | 39
LV25 | 25 | 12500 | 90 | 67 | 75 | 368 | 0.942 | 25.69 | 346.8 |  | 39
LV25 | 25 | 12500 | 75 | 72 | 75 | 381.8 | 0.396 | 11.19 | 151.1 |  | 39
LV25 | 25 | 12500 | 80 | 72 | 75 | 383.2 | 0.537 | 15.25 | 205.9 |  | 39
LV25 | 25 | 12500 | 85 | 72 | 75 | 384.5 | 0.679 | 19.33 | 260.9 |  | 39
LV25 | 25 | 12500 | 90 | 72 | 75 | 385.4 | 0.82 | 23.41 | 316 |  | 39
LV25 | 25 | 12500 | 80 | 77 | 75 | 413 | 0.368 | 11.24 | 151.8 |  | 39
LV25 | 25 | 12500 | 85 | 77 | 75 | 413.4 | 0.5 | 15.3 | 206.5 |  | 39
LV25 | 25 | 12500 | 90 | 77 | 75 | 413.9 | 0.622 | 19.07 | 257.5 |  | 39
LV25 | 25 | 12500 | 65 | 57 | 85 | 282 | 0.707 | 14.77 | 199.4 |  | 39
LV25 | 25 | 12500 | 70 | 57 | 85 | 283.8 | 0.895 | 18.82 | 254.1 |  | 39
LV25 | 25 | 12500 | 75 | 57 | 85 | 297.4 | 0.943 | 20.77 | 280.4 |  | 39
LV25 | 25 | 12500 | 80 | 57 | 85 | 315.9 | 0.943 | 22.06 | 297.8 |  | 39
LV25 | 25 | 12500 | 85 | 57 | 85 | 334.4 | 0.943 | 23.35 | 315.2 |  | 39
LV25 | 25 | 12500 | 90 | 57 | 85 | 352.6 | 0.943 | 24.62 | 332.4 |  | 39
LV25 | 25 | 12500 | 65 | 62 | 85 | 306.2 | 0.481 | 10.9 | 147.2 |  | 39
LV25 | 25 | 12500 | 70 | 62 | 85 | 308.8 | 0.65 | 14.87 | 200.8 |  | 39
LV25 | 25 | 12500 | 75 | 62 | 85 | 310.6 | 0.82 | 18.87 | 254.7 |  | 39
LV25 | 25 | 12500 | 80 | 62 | 85 | 315.9 | 0.943 | 22.06 | 297.8 |  | 39
LV25 | 25 | 12500 | 85 | 62 | 85 | 334.5 | 0.943 | 23.36 | 315.3 |  | 39
LV25 | 25 | 12500 | 90 | 62 | 85 | 352.6 | 0.943 | 24.62 | 332.4 |  | 39
LV25 | 25 | 12500 | 70 | 67 | 85 | 334.3 | 0.434 | 10.74 | 145 |  | 39
LV25 | 25 | 12500 | 75 | 67 | 85 | 336.1 | 0.594 | 14.79 | 199.6 |  | 39
LV25 | 25 | 12500 | 80 | 67 | 85 | 337.8 | 0.754 | 18.87 | 254.7 |  | 39
LV25 | 25 | 12500 | 85 | 67 | 85 | 338.7 | 0.905 | 22.7 | 306.4 |  | 39
LV25 | 25 | 12500 | 90 | 67 | 85 | 352.7 | 0.943 | 24.63 | 332.5 |  | 39
LV25 | 25 | 12500 | 75 | 72 | 85 | 363.1 | 0.405 | 10.9 | 147.2 |  | 39
LV25 | 25 | 12500 | 80 | 72 | 85 | 364.8 | 0.547 | 14.78 | 199.5 |  | 39
LV25 | 25 | 12500 | 85 | 72 | 85 | 366 | 0.688 | 18.65 | 251.8 |  | 39
LV25 | 25 | 12500 | 90 | 72 | 85 | 366.5 | 0.839 | 22.77 | 307.4 |  | 39
LV25 | 25 | 12500 | 80 | 77 | 85 | 392.4 | 0.367 | 10.68 | 144.2 |  | 39
LV25 | 25 | 12500 | 85 | 77 | 85 | 393.7 | 0.5 | 14.57 | 196.7 |  | 39
LV25 | 25 | 12500 | 90 | 77 | 85 | 394.2 | 0.641 | 18.71 | 252.6 |  | 39
LV25 | 25 | 12500 | 65 | 57 | 95 | 265.4 | 0.716 | 14.08 | 190.1 |  | 40
LV25 | 25 | 12500 | 70 | 57 | 95 | 267.2 | 0.914 | 18.1 | 244.3 |  | 40
LV25 | 25 | 12500 | 75 | 57 | 95 | 282.6 | 0.943 | 19.73 | 266.4 |  | 40
LV25 | 25 | 12500 | 80 | 57 | 95 | 300.5 | 0.942 | 20.98 | 283.2 |  | 40
LV25 | 25 | 12500 | 85 | 57 | 95 | 318.4 | 0.943 | 22.23 | 300.1 |  | 40
LV25 | 25 | 12500 | 90 | 57 | 95 | 336.4 | 0.943 | 23.49 | 317.1 |  | 40
LV25 | 25 | 12500 | 65 | 62 | 95 | 288.6 | 0.481 | 10.28 | 138.8 |  | 40
LV25 | 25 | 12500 | 70 | 62 | 95 | 291 | 0.66 | 14.22 | 192 |  | 40
LV25 | 25 | 12500 | 75 | 62 | 95 | 293 | 0.839 | 18.21 | 245.8 |  | 40
LV25 | 25 | 12500 | 80 | 62 | 95 | 300.5 | 0.942 | 20.98 | 283.2 |  | 40
LV25 | 25 | 12500 | 85 | 62 | 95 | 318.5 | 0.943 | 22.24 | 300.2 |  | 40
LV25 | 25 | 12500 | 90 | 62 | 95 | 336.7 | 0.943 | 23.51 | 317.4 |  | 40
LV25 | 25 | 12500 | 70 | 67 | 95 | 315.3 | 0.443 | 10.35 | 139.7 |  | 40
LV25 | 25 | 12500 | 75 | 67 | 95 | 317.7 | 0.603 | 14.19 | 191.6 |  | 40
LV25 | 25 | 12500 | 80 | 67 | 95 | 319.1 | 0.773 | 18.27 | 246.7 |  | 40
LV25 | 25 | 12500 | 85 | 67 | 95 | 320.6 | 0.924 | 21.93 | 296.1 |  | 40
LV25 | 25 | 12500 | 90 | 67 | 95 | 336.5 | 0.942 | 23.49 | 317.1 |  | 40
LV25 | 25 | 12500 | 75 | 72 | 95 | 342.9 | 0.405 | 10.3 | 139 |  | 40
LV25 | 25 | 12500 | 80 | 72 | 95 | 345.1 | 0.556 | 14.21 | 191.9 |  | 40
LV25 | 25 | 12500 | 85 | 72 | 95 | 345.9 | 0.707 | 18.11 | 244.5 |  | 40
LV25 | 25 | 12500 | 90 | 72 | 95 | 346.3 | 0.858 | 22 | 297 |  | 40
LV25 | 25 | 12500 | 80 | 77 | 95 | 371.5 | 0.368 | 10.12 | 136.6 |  | 40
LV25 | 25 | 12500 | 85 | 77 | 95 | 372.3 | 0.509 | 14.04 | 189.5 |  | 40
LV25 | 25 | 12500 | 90 | 77 | 95 | 373 | 0.65 | 17.97 | 242.6 |  | 40
LV25 | 25 | 12500 | 65 | 57 | 105 | 248.2 | 0.735 | 13.52 | 182.5 |  | 40
LV25 | 25 | 12500 | 70 | 57 | 105 | 250.1 | 0.933 | 17.29 | 233.4 |  | 40
LV25 | 25 | 12500 | 75 | 57 | 105 | 266.8 | 0.943 | 18.63 | 251.5 |  | 40
LV25 | 25 | 12500 | 80 | 57 | 105 | 284.1 | 0.943 | 19.84 | 267.8 |  | 40
LV25 | 25 | 12500 | 85 | 57 | 105 | 301.6 | 0.943 | 21.06 | 284.3 |  | 40
LV25 | 25 | 12500 | 90 | 57 | 105 | 318.7 | 0.943 | 22.25 | 300.4 |  | 40
LV25 | 25 | 12500 | 65 | 62 | 105 | 269.9 | 0.49 | 9.8 | 132.3 |  | 40
LV25 | 25 | 12500 | 70 | 62 | 105 | 272.4 | 0.669 | 13.5 | 182.3 |  | 40
LV25 | 25 | 12500 | 75 | 62 | 105 | 274.2 | 0.858 | 17.42 | 235.2 |  | 40
LV25 | 25 | 12500 | 80 | 62 | 105 | 284.1 | 0.943 | 19.84 | 267.8 |  | 40
LV25 | 25 | 12500 | 85 | 62 | 105 | 301.6 | 0.943 | 21.06 | 284.3 |  | 40
LV25 | 25 | 12500 | 90 | 62 | 105 | 318.8 | 0.943 | 22.26 | 300.5 |  | 40
LV25 | 25 | 12500 | 70 | 67 | 105 | 295.7 | 0.443 | 9.7 | 131 |  | 40
LV25 | 25 | 12500 | 75 | 67 | 105 | 297.8 | 0.613 | 13.52 | 182.5 |  | 40
LV25 | 25 | 12500 | 80 | 67 | 105 | 299 | 0.792 | 17.54 | 236.8 |  | 40
LV25 | 25 | 12500 | 85 | 67 | 105 | 301.7 | 0.943 | 21.07 | 284.4 |  | 40
LV25 | 25 | 12500 | 90 | 67 | 105 | 318.9 | 0.943 | 22.27 | 300.6 |  | 40
LV25 | 25 | 12500 | 75 | 72 | 105 | 322.2 | 0.405 | 9.67 | 130.6 |  | 40
LV25 | 25 | 12500 | 80 | 72 | 105 | 323.7 | 0.566 | 13.56 | 183.1 |  | 40
LV25 | 25 | 12500 | 85 | 72 | 105 | 324.8 | 0.726 | 17.47 | 235.8 |  | 40
LV25 | 25 | 12500 | 90 | 72 | 105 | 324.6 | 0.886 | 21.3 | 287.6 |  | 40
LV25 | 25 | 12500 | 80 | 77 | 105 | 349 | 0.377 | 9.75 | 131.6 |  | 40
LV25 | 25 | 12500 | 85 | 77 | 105 | 349.8 | 0.518 | 13.43 | 181.3 |  | 40
LV25 | 25 | 12500 | 90 | 77 | 105 | 350.2 | 0.669 | 17.36 | 234.4 |  | 40
LV25 | 25 | 12500 | 65 | 57 | 115 | 229.9 | 0.754 | 12.84 | 173.4 |  | 41
LV25 | 25 | 12500 | 70 | 57 | 115 | 233.3 | 0.943 | 16.29 | 219.9 |  | 41
LV25 | 25 | 12500 | 75 | 57 | 115 | 249.9 | 0.943 | 17.45 | 235.6 |  | 41
LV25 | 25 | 12500 | 80 | 57 | 115 | 266.8 | 0.943 | 18.63 | 251.5 |  | 41
LV25 | 25 | 12500 | 85 | 57 | 115 | 283.6 | 0.943 | 19.8 | 267.3 |  | 41
LV25 | 25 | 12500 | 90 | 57 | 115 | 300.2 | 0.943 | 20.96 | 283 |  | 41
LV25 | 25 | 12500 | 65 | 62 | 115 | 250.6 | 0.49 | 9.1 | 122.8 |  | 41
LV25 | 25 | 12500 | 70 | 62 | 115 | 252.9 | 0.688 | 12.89 | 174 |  | 41
LV25 | 25 | 12500 | 75 | 62 | 115 | 254.5 | 0.886 | 16.7 | 225.5 |  | 41
LV25 | 25 | 12500 | 80 | 62 | 115 | 266.8 | 0.943 | 18.63 | 251.5 |  | 41
LV25 | 25 | 12500 | 85 | 62 | 115 | 283.5 | 0.943 | 19.8 | 267.3 |  | 41
LV25 | 25 | 12500 | 90 | 62 | 115 | 300.2 | 0.943 | 20.96 | 283 |  | 41
LV25 | 25 | 12500 | 70 | 67 | 115 | 274.9 | 0.453 | 9.21 | 124.4 |  | 41
LV25 | 25 | 12500 | 75 | 67 | 115 | 277 | 0.631 | 12.96 | 174.9 |  | 41
LV25 | 25 | 12500 | 80 | 67 | 115 | 278.1 | 0.82 | 16.89 | 228 |  | 41
LV25 | 25 | 12500 | 85 | 67 | 115 | 283.5 | 0.943 | 19.79 | 267.2 |  | 41
LV25 | 25 | 12500 | 90 | 67 | 115 | 300.1 | 0.943 | 20.96 | 282.9 |  | 41
LV25 | 25 | 12500 | 75 | 72 | 115 | 300.2 | 0.415 | 9.22 | 124.5 |  | 41
LV25 | 25 | 12500 | 80 | 72 | 115 | 301.3 | 0.584 | 13.04 | 176.1 |  | 41
LV25 | 25 | 12500 | 85 | 72 | 115 | 302.3 | 0.754 | 16.89 | 228 |  | 41
LV25 | 25 | 12500 | 90 | 72 | 115 | 302.8 | 0.914 | 20.51 | 276.9 |  | 41
LV25 | 25 | 12500 | 80 | 77 | 115 | 325.2 | 0.377 | 9.08 | 122.6 |  | 41
LV25 | 25 | 12500 | 85 | 77 | 115 | 326 | 0.537 | 12.97 | 175.1 |  | 41
LV25 | 25 | 12500 | 90 | 77 | 115 | 326.5 | 0.698 | 16.87 | 227.8 |  | 41
LV25 | 25 | 12500 | 65 | 57 | 125 | 211.1 | 0.773 | 12.08 | 163.1 |  | 41
LV25 | 25 | 12500 | 70 | 57 | 125 | 216.2 | 0.943 | 15.1 | 203.8 |  | 41
LV25 | 25 | 12500 | 75 | 57 | 125 | 232.3 | 0.943 | 16.22 | 219 |  | 41
LV25 | 25 | 12500 | 80 | 57 | 125 | 248.4 | 0.943 | 17.35 | 234.2 |  | 41
LV25 | 25 | 12500 | 85 | 57 | 125 | 264.4 | 0.943 | 18.46 | 249.2 |  | 41
LV25 | 25 | 12500 | 90 | 57 | 125 | 280.3 | 0.943 | 19.57 | 264.2 |  | 41
LV25 | 25 | 12500 | 65 | 62 | 125 | 230.3 | 0.5 | 8.53 | 115.1 |  | 41
LV25 | 25 | 12500 | 70 | 62 | 125 | 232.6 | 0.707 | 12.18 | 164.4 |  | 41
LV25 | 25 | 12500 | 75 | 62 | 125 | 234.3 | 0.915 | 15.87 | 214.3 |  | 41
LV25 | 25 | 12500 | 80 | 62 | 125 | 248.4 | 0.943 | 17.35 | 234.2 |  | 41
LV25 | 25 | 12500 | 85 | 62 | 125 | 264.9 | 0.943 | 18.5 | 249.7 |  | 41
LV25 | 25 | 12500 | 90 | 62 | 125 | 280.3 | 0.943 | 19.57 | 264.2 |  | 41
LV25 | 25 | 12500 | 70 | 67 | 125 | 253.2 | 0.452 | 8.48 | 114.5 |  | 41
LV25 | 25 | 12500 | 75 | 67 | 125 | 255.2 | 0.65 | 12.3 | 166 |  | 41
LV25 | 25 | 12500 | 80 | 67 | 125 | 256 | 0.848 | 16.09 | 217.2 |  | 41
LV25 | 25 | 12500 | 85 | 67 | 125 | 264.5 | 0.943 | 18.47 | 249.3 |  | 41
LV25 | 25 | 12500 | 90 | 67 | 125 | 280.2 | 0.943 | 19.56 | 264.1 |  | 41
LV25 | 25 | 12500 | 75 | 72 | 125 | 276.9 | 0.415 | 8.5 | 114.8 |  | 41
LV25 | 25 | 12500 | 80 | 72 | 125 | 278.2 | 0.594 | 12.24 | 165.2 |  | 41
LV25 | 25 | 12500 | 85 | 72 | 125 | 278.7 | 0.783 | 16.16 | 218.1 |  | 41
LV25 | 25 | 12500 | 90 | 72 | 125 | 280.2 | 0.943 | 19.56 | 264.1 |  | 41
LV25 | 25 | 12500 | 80 | 77 | 125 | 300.6 | 0.387 | 8.61 | 116.2 |  | 41
LV25 | 25 | 12500 | 85 | 77 | 125 | 301.7 | 0.547 | 12.21 | 164.9 |  | 41
LV25 | 25 | 12500 | 90 | 77 | 125 | 301.2 | 0.726 | 16.19 | 218.6 |  | 41
LV28 | 27.5 | 6875 | 65 | 57 | 75 | 286.3 | 0.629 | 24.26 | 180.1 |  | 42
LV28 | 27.5 | 6875 | 70 | 57 | 75 | 287.5 | 0.735 | 28.47 | 211.4 |  | 42
LV28 | 27.5 | 6875 | 75 | 57 | 75 | 288.8 | 0.851 | 33.12 | 245.9 |  | 42
LV28 | 27.5 | 6875 | 80 | 57 | 75 | 290.1 | 0.958 | 37.41 | 277.8 |  | 42
LV28 | 27.5 | 6875 | 85 | 57 | 75 | 304 | 0.967 | 39.61 | 294.1 |  | 42
LV28 | 27.5 | 6875 | 90 | 57 | 75 | 319.6 | 0.967 | 41.63 | 309.1 |  | 42
LV28 | 27.5 | 6875 | 65 | 62 | 75 | 313.3 | 0.474 | 20 | 148.5 |  | 42
LV28 | 27.5 | 6875 | 70 | 62 | 75 | 314.7 | 0.581 | 24.61 | 182.7 |  | 42
LV28 | 27.5 | 6875 | 75 | 62 | 75 | 316 | 0.677 | 28.82 | 214 |  | 42
LV28 | 27.5 | 6875 | 80 | 62 | 75 | 317.2 | 0.774 | 33.06 | 245.5 |  | 42
LV28 | 27.5 | 6875 | 85 | 62 | 75 | 318.3 | 0.88 | 37.74 | 280.2 |  | 42
LV28 | 27.5 | 6875 | 90 | 62 | 75 | 320.2 | 0.968 | 41.72 | 309.8 |  | 42
LV28 | 27.5 | 6875 | 70 | 67 | 75 | 343 | 0.435 | 20.11 | 149.3 |  | 42
LV28 | 27.5 | 6875 | 75 | 67 | 75 | 344.1 | 0.532 | 24.66 | 183.1 |  | 42
LV28 | 27.5 | 6875 | 80 | 67 | 75 | 345.5 | 0.619 | 28.81 | 213.9 |  | 42
LV28 | 27.5 | 6875 | 85 | 67 | 75 | 346.4 | 0.716 | 33.4 | 248 |  | 42
LV28 | 27.5 | 6875 | 90 | 67 | 75 | 347.3 | 0.803 | 37.56 | 278.9 |  | 42
LV28 | 27.5 | 6875 | 75 | 72 | 75 | 374.4 | 0.397 | 20 | 148.5 |  | 42
LV28 | 27.5 | 6875 | 80 | 72 | 75 | 375.4 | 0.484 | 24.46 | 181.6 |  | 42
LV28 | 27.5 | 6875 | 85 | 72 | 75 | 376.5 | 0.571 | 28.94 | 214.9 |  | 42
LV28 | 27.5 | 6875 | 90 | 72 | 75 | 377.3 | 0.648 | 32.93 | 244.5 |  | 42
LV28 | 27.5 | 6875 | 80 | 77 | 75 | 407.5 | 0.358 | 19.64 | 145.8 |  | 42
LV28 | 27.5 | 6875 | 85 | 77 | 75 | 407.9 | 0.435 | 23.92 | 177.6 |  | 42
LV28 | 27.5 | 6875 | 90 | 77 | 75 | 408.7 | 0.522 | 28.75 | 213.5 |  | 42
LV28 | 27.5 | 6875 | 65 | 57 | 85 | 274.1 | 0.629 | 23.22 | 172.4 |  | 42
LV28 | 27.5 | 6875 | 70 | 57 | 85 | 275.4 | 0.745 | 27.62 | 205.1 |  | 42
LV28 | 27.5 | 6875 | 75 | 57 | 85 | 276.5 | 0.861 | 32.05 | 238 |  | 42
LV28 | 27.5 | 6875 | 80 | 57 | 85 | 278.5 | 0.967 | 36.28 | 269.4 |  | 42
LV28 | 27.5 | 6875 | 85 | 57 | 85 | 293.2 | 0.967 | 38.2 | 283.6 |  | 42
LV28 | 27.5 | 6875 | 90 | 57 | 85 | 308.5 | 0.967 | 40.19 | 298.4 |  | 42
LV28 | 27.5 | 6875 | 65 | 62 | 85 | 299.8 | 0.474 | 19.14 | 142.1 |  | 42
LV28 | 27.5 | 6875 | 70 | 62 | 85 | 301 | 0.58 | 23.53 | 174.7 |  | 42
LV28 | 27.5 | 6875 | 75 | 62 | 85 | 302.2 | 0.687 | 27.96 | 207.6 |  | 42
LV28 | 27.5 | 6875 | 80 | 62 | 85 | 303.7 | 0.784 | 32.05 | 238 |  | 42
LV28 | 27.5 | 6875 | 85 | 62 | 85 | 304.6 | 0.89 | 36.5 | 271 |  | 42
LV28 | 27.5 | 6875 | 90 | 62 | 85 | 308.8 | 0.967 | 40.23 | 298.7 |  | 42
LV28 | 27.5 | 6875 | 70 | 67 | 85 | 328.5 | 0.435 | 19.26 | 143 |  | 42
LV28 | 27.5 | 6875 | 75 | 67 | 85 | 329.7 | 0.532 | 23.62 | 175.4 |  | 42
LV28 | 27.5 | 6875 | 80 | 67 | 85 | 330.8 | 0.629 | 28.01 | 208 |  | 42
LV28 | 27.5 | 6875 | 85 | 67 | 85 | 331.9 | 0.726 | 32.43 | 240.8 |  | 42
LV28 | 27.5 | 6875 | 90 | 67 | 85 | 332.6 | 0.822 | 36.84 | 273.5 |  | 42
LV28 | 27.5 | 6875 | 75 | 72 | 85 | 358.7 | 0.397 | 19.16 | 142.3 |  | 42
LV28 | 27.5 | 6875 | 80 | 72 | 85 | 359.9 | 0.484 | 23.45 | 174.1 |  | 42
LV28 | 27.5 | 6875 | 85 | 72 | 85 | 361 | 0.571 | 27.74 | 206 |  | 42
LV28 | 27.5 | 6875 | 90 | 72 | 85 | 361.6 | 0.658 | 32.04 | 237.9 |  | 42
LV28 | 27.5 | 6875 | 80 | 77 | 85 | 390.2 | 0.358 | 18.81 | 139.7 |  | 42
LV28 | 27.5 | 6875 | 85 | 77 | 85 | 391.3 | 0.445 | 23.45 | 174.1 |  | 42
LV28 | 27.5 | 6875 | 90 | 77 | 85 | 392.5 | 0.522 | 27.61 | 205 |  | 42
LV28 | 27.5 | 6875 | 65 | 57 | 95 | 260.7 | 0.639 | 22.42 | 166.5 |  | 43
LV28 | 27.5 | 6875 | 70 | 57 | 95 | 262.1 | 0.755 | 26.64 | 197.8 |  | 43
LV28 | 27.5 | 6875 | 75 | 57 | 95 | 263.3 | 0.871 | 30.88 | 229.3 |  | 43
LV28 | 27.5 | 6875 | 80 | 57 | 95 | 266.5 | 0.967 | 34.72 | 257.8 |  | 43
LV28 | 27.5 | 6875 | 85 | 57 | 95 | 281.7 | 0.967 | 36.7 | 272.5 |  | 43
LV28 | 27.5 | 6875 | 90 | 57 | 95 | 296.8 | 0.967 | 38.67 | 287.1 |  | 43
LV28 | 27.5 | 6875 | 65 | 62 | 95 | 285.2 | 0.474 | 18.21 | 135.2 |  | 43
LV28 | 27.5 | 6875 | 70 | 62 | 95 | 286.8 | 0.58 | 22.41 | 166.4 |  | 43
LV28 | 27.5 | 6875 | 75 | 62 | 95 | 288.1 | 0.696 | 27.02 | 200.6 |  | 43
LV28 | 27.5 | 6875 | 80 | 62 | 95 | 289.3 | 0.803 | 31.29 | 232.3 |  | 43
LV28 | 27.5 | 6875 | 85 | 62 | 95 | 289.9 | 0.909 | 35.5 | 263.6 |  | 43
LV28 | 27.5 | 6875 | 90 | 62 | 95 | 296.9 | 0.967 | 38.68 | 287.2 |  | 43
LV28 | 27.5 | 6875 | 70 | 67 | 95 | 312.8 | 0.435 | 18.34 | 136.2 |  | 43
LV28 | 27.5 | 6875 | 75 | 67 | 95 | 314.2 | 0.532 | 22.52 | 167.2 |  | 43
LV28 | 27.5 | 6875 | 80 | 67 | 95 | 315.5 | 0.629 | 26.72 | 198.4 |  | 43
LV28 | 27.5 | 6875 | 85 | 67 | 95 | 316.3 | 0.735 | 31.31 | 232.5 |  | 43
LV28 | 27.5 | 6875 | 90 | 67 | 95 | 317.2 | 0.832 | 35.54 | 263.9 |  | 43
LV28 | 27.5 | 6875 | 75 | 72 | 95 | 341.8 | 0.397 | 18.26 | 135.6 |  | 43
LV28 | 27.5 | 6875 | 80 | 72 | 95 | 343.1 | 0.484 | 22.34 | 165.9 |  | 43
LV28 | 27.5 | 6875 | 85 | 72 | 95 | 344.2 | 0.58 | 26.91 | 199.8 |  | 43
LV28 | 27.5 | 6875 | 90 | 72 | 95 | 345 | 0.668 | 31.02 | 230.3 |  | 43
LV28 | 27.5 | 6875 | 80 | 77 | 95 | 372.3 | 0.358 | 17.95 | 133.3 |  | 43
LV28 | 27.5 | 6875 | 85 | 77 | 95 | 373.5 | 0.445 | 22.38 | 166.2 |  | 43
LV28 | 27.5 | 6875 | 90 | 77 | 95 | 374.3 | 0.532 | 26.83 | 199.2 |  | 43
LV28 | 27.5 | 6875 | 65 | 57 | 105 | 246.8 | 0.639 | 21.23 | 157.6 |  | 43
LV28 | 27.5 | 6875 | 70 | 57 | 105 | 248.1 | 0.764 | 25.54 | 189.6 |  | 43
LV28 | 27.5 | 6875 | 75 | 57 | 105 | 249.2 | 0.89 | 29.87 | 221.8 |  | 43
LV28 | 27.5 | 6875 | 80 | 57 | 105 | 254.9 | 0.967 | 33.2 | 246.5 |  | 43
LV28 | 27.5 | 6875 | 85 | 57 | 105 | 269.4 | 0.967 | 35.1 | 260.6 |  | 43
LV28 | 27.5 | 6875 | 90 | 57 | 105 | 284.1 | 0.967 | 37.01 | 274.8 |  | 43
LV28 | 27.5 | 6875 | 65 | 62 | 105 | 270.1 | 0.474 | 17.24 | 128 |  | 43
LV28 | 27.5 | 6875 | 70 | 62 | 105 | 271.6 | 0.59 | 21.59 | 160.3 |  | 43
LV28 | 27.5 | 6875 | 75 | 62 | 105 | 272.9 | 0.706 | 25.95 | 192.7 |  | 43
LV28 | 27.5 | 6875 | 80 | 62 | 105 | 273.5 | 0.813 | 29.94 | 222.3 |  | 43
LV28 | 27.5 | 6875 | 85 | 62 | 105 | 274.6 | 0.929 | 34.34 | 255 |  | 43
LV28 | 27.5 | 6875 | 90 | 62 | 105 | 284.3 | 0.967 | 37.04 | 275 |  | 43
LV28 | 27.5 | 6875 | 70 | 67 | 105 | 296.5 | 0.435 | 17.39 | 129.1 |  | 43
LV28 | 27.5 | 6875 | 75 | 67 | 105 | 297.8 | 0.542 | 21.72 | 161.3 |  | 43
LV28 | 27.5 | 6875 | 80 | 67 | 105 | 299 | 0.638 | 25.71 | 190.9 |  | 43
LV28 | 27.5 | 6875 | 85 | 67 | 105 | 299.8 | 0.745 | 30.07 | 223.3 |  | 43
LV28 | 27.5 | 6875 | 90 | 67 | 105 | 300.6 | 0.851 | 34.46 | 255.9 |  | 43
LV28 | 27.5 | 6875 | 75 | 72 | 105 | 324 | 0.397 | 17.31 | 128.5 |  | 43
LV28 | 27.5 | 6875 | 80 | 72 | 105 | 325.3 | 0.493 | 21.62 | 160.5 |  | 43
LV28 | 27.5 | 6875 | 85 | 72 | 105 | 326.3 | 0.59 | 25.93 | 192.5 |  | 43
LV28 | 27.5 | 6875 | 90 | 72 | 105 | 327.2 | 0.687 | 30.26 | 224.7 |  | 43
LV28 | 27.5 | 6875 | 80 | 77 | 105 | 353.1 | 0.358 | 17.02 | 126.4 |  | 43
LV28 | 27.5 | 6875 | 85 | 77 | 105 | 354.2 | 0.455 | 21.68 | 161 |  | 43
LV28 | 27.5 | 6875 | 90 | 77 | 105 | 355.3 | 0.542 | 25.93 | 192.5 |  | 43
LV28 | 27.5 | 6875 | 65 | 57 | 115 | 232.1 | 0.648 | 20.26 | 150.4 |  | 44
LV28 | 27.5 | 6875 | 70 | 57 | 115 | 233.4 | 0.784 | 24.63 | 182.9 |  | 44
LV28 | 27.5 | 6875 | 75 | 57 | 115 | 234.1 | 0.909 | 28.67 | 212.9 |  | 44
LV28 | 27.5 | 6875 | 80 | 57 | 115 | 242.3 | 0.967 | 31.57 | 234.4 |  | 44
LV28 | 27.5 | 6875 | 85 | 57 | 115 | 256.5 | 0.967 | 33.41 | 248.1 |  | 44
LV28 | 27.5 | 6875 | 90 | 57 | 115 | 270.7 | 0.967 | 35.27 | 261.9 |  | 44
LV28 | 27.5 | 6875 | 65 | 62 | 115 | 254.1 | 0.474 | 16.22 | 120.4 |  | 44
LV28 | 27.5 | 6875 | 70 | 62 | 115 | 255.7 | 0.6 | 20.66 | 153.4 |  | 44
LV28 | 27.5 | 6875 | 75 | 62 | 115 | 256.9 | 0.716 | 24.77 | 183.9 |  | 44
LV28 | 27.5 | 6875 | 80 | 62 | 115 | 258 | 0.832 | 28.9 | 214.6 |  | 44
LV28 | 27.5 | 6875 | 85 | 62 | 115 | 258.7 | 0.948 | 33.04 | 245.3 |  | 44
LV28 | 27.5 | 6875 | 90 | 62 | 115 | 270.8 | 0.968 | 35.29 | 262 |  | 44
LV28 | 27.5 | 6875 | 70 | 67 | 115 | 279.1 | 0.435 | 16.36 | 121.5 |  | 44
LV28 | 27.5 | 6875 | 75 | 67 | 115 | 280.5 | 0.542 | 20.46 | 151.9 |  | 44
LV28 | 27.5 | 6875 | 80 | 67 | 115 | 281.2 | 0.658 | 24.92 | 185 |  | 44
LV28 | 27.5 | 6875 | 85 | 67 | 115 | 282.3 | 0.764 | 29.06 | 215.8 |  | 44
LV28 | 27.5 | 6875 | 90 | 67 | 115 | 282.9 | 0.871 | 33.17 | 246.3 |  | 44
LV28 | 27.5 | 6875 | 75 | 72 | 115 | 305.1 | 0.397 | 16.3 | 121 |  | 44
LV28 | 27.5 | 6875 | 80 | 72 | 115 | 306.3 | 0.493 | 20.35 | 151.1 |  | 44
LV28 | 27.5 | 6875 | 85 | 72 | 115 | 307.2 | 0.6 | 24.82 | 184.3 |  | 44
LV28 | 27.5 | 6875 | 90 | 72 | 115 | 307.9 | 0.697 | 28.89 | 214.5 |  | 44
LV28 | 27.5 | 6875 | 80 | 77 | 115 | 332.6 | 0.358 | 16.04 | 119.1 |  | 44
LV28 | 27.5 | 6875 | 85 | 77 | 115 | 333.7 | 0.455 | 20.43 | 151.7 |  | 44
LV28 | 27.5 | 6875 | 90 | 77 | 115 | 334.5 | 0.551 | 24.84 | 184.4 |  | 44
LV28 | 27.5 | 6875 | 65 | 57 | 125 | 216.6 | 0.658 | 19.19 | 142.5 |  | 44
LV28 | 27.5 | 6875 | 70 | 57 | 125 | 217.8 | 0.793 | 23.27 | 172.8 |  | 44
LV28 | 27.5 | 6875 | 75 | 57 | 125 | 218.5 | 0.938 | 27.61 | 205 |  | 44
LV28 | 27.5 | 6875 | 80 | 57 | 125 | 228.8 | 0.968 | 29.82 | 221.4 |  | 44
LV28 | 27.5 | 6875 | 85 | 57 | 125 | 242.5 | 0.967 | 31.6 | 234.6 |  | 44
LV28 | 27.5 | 6875 | 90 | 57 | 125 | 256.3 | 0.968 | 33.4 | 248 |  | 44
LV28 | 27.5 | 6875 | 65 | 62 | 125 | 237.4 | 0.474 | 15.15 | 112.5 |  | 44
LV28 | 27.5 | 6875 | 70 | 62 | 125 | 238.8 | 0.6 | 19.29 | 143.2 |  | 44
LV28 | 27.5 | 6875 | 75 | 62 | 125 | 240 | 0.726 | 23.46 | 174.2 |  | 44
LV28 | 27.5 | 6875 | 80 | 62 | 125 | 241 | 0.851 | 27.62 | 205.1 |  | 44
LV28 | 27.5 | 6875 | 85 | 62 | 125 | 242.8 | 0.967 | 31.64 | 234.9 |  | 44
LV28 | 27.5 | 6875 | 90 | 62 | 125 | 256.3 | 0.968 | 33.4 | 248 |  | 44
LV28 | 27.5 | 6875 | 70 | 67 | 125 | 260.8 | 0.435 | 15.29 | 113.5 |  | 44
LV28 | 27.5 | 6875 | 75 | 67 | 125 | 262.1 | 0.551 | 19.46 | 144.5 |  | 44
LV28 | 27.5 | 6875 | 80 | 67 | 125 | 263.1 | 0.667 | 23.65 | 175.6 |  | 44
LV28 | 27.5 | 6875 | 85 | 67 | 125 | 263.6 | 0.784 | 27.82 | 206.6 |  | 44
LV28 | 27.5 | 6875 | 90 | 67 | 125 | 264 | 0.9 | 31.99 | 237.5 |  | 44
LV28 | 27.5 | 6875 | 75 | 72 | 125 | 285.1 | 0.397 | 15.23 | 113.1 |  | 44
LV28 | 27.5 | 6875 | 80 | 72 | 125 | 286.2 | 0.503 | 19.39 | 144 |  | 44
LV28 | 27.5 | 6875 | 85 | 72 | 125 | 287.3 | 0.609 | 23.58 | 175.1 |  | 44
LV28 | 27.5 | 6875 | 90 | 72 | 125 | 287.9 | 0.716 | 27.76 | 206.1 |  | 44
LV28 | 27.5 | 6875 | 80 | 77 | 125 | 310.9 | 0.368 | 15.39 | 114.3 |  | 44
LV28 | 27.5 | 6875 | 85 | 77 | 125 | 312 | 0.464 | 19.52 | 144.9 |  | 44
LV28 | 27.5 | 6875 | 90 | 77 | 125 | 312.7 | 0.561 | 23.62 | 175.4 |  | 44
LV28 | 27.5 | 8250 | 65 | 57 | 75 | 300.5 | 0.639 | 21.54 | 191.9 |  | 42
LV28 | 27.5 | 8250 | 70 | 57 | 75 | 302.4 | 0.764 | 25.94 | 231.1 |  | 42
LV28 | 27.5 | 8250 | 75 | 57 | 75 | 303.8 | 0.89 | 30.35 | 270.4 |  | 42
LV28 | 27.5 | 8250 | 80 | 57 | 75 | 310.1 | 0.967 | 33.67 | 300 |  | 42
LV28 | 27.5 | 8250 | 85 | 57 | 75 | 327.1 | 0.967 | 35.51 | 316.4 |  | 42
LV28 | 27.5 | 8250 | 90 | 57 | 75 | 344 | 0.967 | 37.35 | 332.8 |  | 42
LV28 | 27.5 | 8250 | 65 | 62 | 75 | 327.8 | 0.474 | 17.44 | 155.4 |  | 42
LV28 | 27.5 | 8250 | 70 | 62 | 75 | 329.6 | 0.59 | 21.83 | 194.5 |  | 42
LV28 | 27.5 | 8250 | 75 | 62 | 75 | 331 | 0.706 | 26.23 | 233.7 |  | 42
LV28 | 27.5 | 8250 | 80 | 62 | 75 | 332.1 | 0.812 | 30.28 | 269.8 |  | 42
LV28 | 27.5 | 8250 | 85 | 62 | 75 | 333 | 0.929 | 34.7 | 309.2 |  | 42
LV28 | 27.5 | 8250 | 90 | 62 | 75 | 344.2 | 0.967 | 37.37 | 333 |  | 42
LV28 | 27.5 | 8250 | 70 | 67 | 75 | 358.5 | 0.435 | 17.52 | 156.1 |  | 42
LV28 | 27.5 | 8250 | 75 | 67 | 75 | 360 | 0.542 | 21.89 | 195 |  | 42
LV28 | 27.5 | 8250 | 80 | 67 | 75 | 361.3 | 0.648 | 26.29 | 234.2 |  | 42
LV28 | 27.5 | 8250 | 85 | 67 | 75 | 362.2 | 0.745 | 30.28 | 269.8 |  | 42
LV28 | 27.5 | 8250 | 90 | 67 | 75 | 363.2 | 0.851 | 34.7 | 309.2 |  | 42
LV28 | 27.5 | 8250 | 75 | 72 | 75 | 390.7 | 0.396 | 17.38 | 154.9 |  | 42
LV28 | 27.5 | 8250 | 80 | 72 | 75 | 392.1 | 0.493 | 21.71 | 193.4 |  | 42
LV28 | 27.5 | 8250 | 85 | 72 | 75 | 393.2 | 0.59 | 26.04 | 232 |  | 42
LV28 | 27.5 | 8250 | 90 | 72 | 75 | 394.1 | 0.687 | 30.38 | 270.7 |  | 42
LV28 | 27.5 | 8250 | 80 | 77 | 75 | 424 | 0.358 | 17.04 | 151.8 |  | 42
LV28 | 27.5 | 8250 | 85 | 77 | 75 | 425 | 0.455 | 21.68 | 193.2 |  | 42
LV28 | 27.5 | 8250 | 90 | 77 | 75 | 426.3 | 0.542 | 25.93 | 231 |  | 42
LV28 | 27.5 | 8250 | 65 | 57 | 85 | 287 | 0.648 | 20.88 | 186 |  | 42
LV28 | 27.5 | 8250 | 70 | 57 | 85 | 288.7 | 0.774 | 25.07 | 223.4 |  | 42
LV28 | 27.5 | 8250 | 75 | 57 | 85 | 289.8 | 0.9 | 29.26 | 260.7 |  | 42
LV28 | 27.5 | 8250 | 80 | 57 | 85 | 298.2 | 0.967 | 32.38 | 288.5 |  | 42
LV28 | 27.5 | 8250 | 85 | 57 | 85 | 315 | 0.967 | 34.2 | 304.7 |  | 42
LV28 | 27.5 | 8250 | 90 | 57 | 85 | 331.7 | 0.967 | 36.02 | 320.9 |  | 42
LV28 | 27.5 | 8250 | 65 | 62 | 85 | 313.2 | 0.474 | 16.66 | 148.4 |  | 42
LV28 | 27.5 | 8250 | 70 | 62 | 85 | 314.9 | 0.59 | 20.85 | 185.8 |  | 42
LV28 | 27.5 | 8250 | 75 | 62 | 85 | 316.1 | 0.716 | 25.4 | 226.3 |  | 42
LV28 | 27.5 | 8250 | 80 | 62 | 85 | 317.2 | 0.832 | 29.62 | 263.9 |  | 42
LV28 | 27.5 | 8250 | 85 | 62 | 85 | 318.3 | 0.948 | 33.87 | 301.8 |  | 42
LV28 | 27.5 | 8250 | 90 | 62 | 85 | 331.9 | 0.967 | 36.03 | 321 |  | 42
LV28 | 27.5 | 8250 | 70 | 67 | 85 | 342.6 | 0.435 | 16.75 | 149.2 |  | 42
LV28 | 27.5 | 8250 | 75 | 67 | 85 | 344.2 | 0.542 | 20.92 | 186.4 |  | 42
LV28 | 27.5 | 8250 | 80 | 67 | 85 | 345.3 | 0.648 | 25.12 | 223.8 |  | 42
LV28 | 27.5 | 8250 | 85 | 67 | 85 | 346.4 | 0.764 | 29.71 | 264.7 |  | 42
LV28 | 27.5 | 8250 | 90 | 67 | 85 | 347.4 | 0.87 | 33.94 | 302.4 |  | 42
LV28 | 27.5 | 8250 | 75 | 72 | 85 | 373.7 | 0.397 | 16.63 | 148.2 |  | 42
LV28 | 27.5 | 8250 | 80 | 72 | 85 | 375.2 | 0.493 | 20.77 | 185.1 |  | 42
LV28 | 27.5 | 8250 | 85 | 72 | 85 | 376.4 | 0.6 | 25.34 | 225.8 |  | 42
LV28 | 27.5 | 8250 | 90 | 72 | 85 | 377.3 | 0.697 | 29.49 | 262.8 |  | 42
LV28 | 27.5 | 8250 | 80 | 77 | 85 | 405.7 | 0.358 | 16.3 | 145.2 |  | 42
LV28 | 27.5 | 8250 | 85 | 77 | 85 | 406.7 | 0.455 | 20.75 | 184.9 |  | 42
LV28 | 27.5 | 8250 | 90 | 77 | 85 | 407.8 | 0.551 | 25.24 | 224.9 |  | 42
LV28 | 27.5 | 8250 | 65 | 57 | 95 | 272.4 | 0.658 | 20.11 | 179.2 |  | 43
LV28 | 27.5 | 8250 | 70 | 57 | 95 | 274.1 | 0.784 | 24.11 | 214.8 |  | 43
LV28 | 27.5 | 8250 | 75 | 57 | 95 | 275 | 0.919 | 28.36 | 252.7 |  | 43
LV28 | 27.5 | 8250 | 80 | 57 | 95 | 285.9 | 0.967 | 31.04 | 276.6 |  | 43
LV28 | 27.5 | 8250 | 85 | 57 | 95 | 302.2 | 0.967 | 32.81 | 292.3 |  | 43
LV28 | 27.5 | 8250 | 90 | 57 | 95 | 318.4 | 0.967 | 34.57 | 308 |  | 43
LV28 | 27.5 | 8250 | 65 | 62 | 95 | 297.4 | 0.474 | 15.82 | 141 |  | 43
LV28 | 27.5 | 8250 | 70 | 62 | 95 | 299.2 | 0.6 | 20.13 | 179.4 |  | 43
LV28 | 27.5 | 8250 | 75 | 62 | 95 | 300.5 | 0.725 | 24.47 | 218 |  | 43
LV28 | 27.5 | 8250 | 80 | 62 | 95 | 301.5 | 0.842 | 28.48 | 253.8 |  | 43
LV28 | 27.5 | 8250 | 85 | 62 | 95 | 303.6 | 0.958 | 32.64 | 290.8 |  | 43
LV28 | 27.5 | 8250 | 90 | 62 | 95 | 318.5 | 0.967 | 34.58 | 308.1 |  | 43
LV28 | 27.5 | 8250 | 70 | 67 | 95 | 325.6 | 0.435 | 15.9 | 141.7 |  | 43
LV28 | 27.5 | 8250 | 75 | 67 | 95 | 327.3 | 0.551 | 20.25 | 180.4 |  | 43
LV28 | 27.5 | 8250 | 80 | 67 | 95 | 328.4 | 0.658 | 24.24 | 216 |  | 43
LV28 | 27.5 | 8250 | 85 | 67 | 95 | 329.3 | 0.774 | 28.6 | 254.8 |  | 43
LV28 | 27.5 | 8250 | 90 | 67 | 95 | 330.4 | 0.89 | 33.01 | 294.1 |  | 43
LV28 | 27.5 | 8250 | 75 | 72 | 95 | 355.6 | 0.397 | 15.82 | 141 |  | 43
LV28 | 27.5 | 8250 | 80 | 72 | 95 | 357 | 0.503 | 20.16 | 179.6 |  | 43
LV28 | 27.5 | 8250 | 85 | 72 | 95 | 358.4 | 0.61 | 24.52 | 218.5 |  | 43
LV28 | 27.5 | 8250 | 90 | 72 | 95 | 359.1 | 0.706 | 28.46 | 253.6 |  | 43
LV28 | 27.5 | 8250 | 80 | 77 | 95 | 386.1 | 0.358 | 15.51 | 138.2 |  | 43
LV28 | 27.5 | 8250 | 85 | 77 | 95 | 387.4 | 0.455 | 19.76 | 176.1 |  | 43
LV28 | 27.5 | 8250 | 90 | 77 | 95 | 388.4 | 0.551 | 24.04 | 214.2 |  | 43
LV28 | 27.5 | 8250 | 65 | 57 | 105 | 257.3 | 0.658 | 19 | 169.3 |  | 43
LV28 | 27.5 | 8250 | 70 | 57 | 105 | 258.8 | 0.803 | 23.32 | 207.8 |  | 43
LV28 | 27.5 | 8250 | 75 | 57 | 105 | 259.6 | 0.938 | 27.34 | 243.6 |  | 43
LV28 | 27.5 | 8250 | 80 | 57 | 105 | 272.5 | 0.967 | 29.58 | 263.6 |  | 43
LV28 | 27.5 | 8250 | 85 | 57 | 105 | 288.4 | 0.967 | 31.31 | 279 |  | 43
LV28 | 27.5 | 8250 | 90 | 57 | 105 | 304.5 | 0.967 | 33.05 | 294.5 |  | 43
LV28 | 27.5 | 8250 | 65 | 62 | 105 | 280.9 | 0.474 | 14.95 | 133.2 |  | 43
LV28 | 27.5 | 8250 | 70 | 62 | 105 | 282.7 | 0.609 | 19.34 | 172.3 |  | 43
LV28 | 27.5 | 8250 | 75 | 62 | 105 | 284 | 0.735 | 23.43 | 208.8 |  | 43
LV28 | 27.5 | 8250 | 80 | 62 | 105 | 285.3 | 0.861 | 27.56 | 245.6 |  | 43
LV28 | 27.5 | 8250 | 85 | 62 | 105 | 288.5 | 0.967 | 31.32 | 279.1 |  | 43
LV28 | 27.5 | 8250 | 90 | 62 | 105 | 304.6 | 0.967 | 33.06 | 294.6 |  | 43
LV28 | 27.5 | 8250 | 70 | 67 | 105 | 307.9 | 0.435 | 15.04 | 134 |  | 43
LV28 | 27.5 | 8250 | 75 | 67 | 105 | 309.5 | 0.551 | 19.15 | 170.6 |  | 43
LV28 | 27.5 | 8250 | 80 | 67 | 105 | 310.5 | 0.677 | 23.59 | 210.2 |  | 43
LV28 | 27.5 | 8250 | 85 | 67 | 105 | 311.4 | 0.793 | 27.72 | 247 |  | 43
LV28 | 27.5 | 8250 | 90 | 67 | 105 | 312.3 | 0.909 | 31.87 | 284 |  | 43
LV28 | 27.5 | 8250 | 75 | 72 | 105 | 336.4 | 0.397 | 14.97 | 133.4 |  | 43
LV28 | 27.5 | 8250 | 80 | 72 | 105 | 338 | 0.503 | 19.08 | 170 |  | 43
LV28 | 27.5 | 8250 | 85 | 72 | 105 | 338.9 | 0.619 | 23.55 | 209.8 |  | 43
LV28 | 27.5 | 8250 | 90 | 72 | 105 | 339.8 | 0.725 | 27.67 | 246.5 |  | 43
LV28 | 27.5 | 8250 | 80 | 77 | 105 | 365.4 | 0.368 | 15.07 | 134.3 |  | 43
LV28 | 27.5 | 8250 | 85 | 77 | 105 | 366.4 | 0.464 | 19.09 | 170.1 |  | 43
LV28 | 27.5 | 8250 | 90 | 77 | 105 | 367.6 | 0.571 | 23.55 | 209.8 |  | 43
LV28 | 27.5 | 8250 | 65 | 57 | 115 | 241.5 | 0.667 | 18.09 | 161.2 |  | 44
LV28 | 27.5 | 8250 | 70 | 57 | 115 | 242.8 | 0.822 | 22.4 | 199.6 |  | 44
LV28 | 27.5 | 8250 | 75 | 57 | 115 | 244.1 | 0.957 | 26.23 | 233.7 |  | 44
LV28 | 27.5 | 8250 | 80 | 57 | 115 | 258.6 | 0.968 | 28.08 | 250.2 |  | 44
LV28 | 27.5 | 8250 | 85 | 57 | 115 | 273.8 | 0.967 | 29.72 | 264.8 |  | 44
LV28 | 27.5 | 8250 | 90 | 57 | 115 | 289.3 | 0.967 | 31.4 | 279.8 |  | 44
LV28 | 27.5 | 8250 | 65 | 62 | 115 | 263.7 | 0.474 | 14.03 | 125 |  | 44
LV28 | 27.5 | 8250 | 70 | 62 | 115 | 265.3 | 0.619 | 18.44 | 164.3 |  | 44
LV28 | 27.5 | 8250 | 75 | 62 | 115 | 266.5 | 0.755 | 22.57 | 201.1 |  | 44
LV28 | 27.5 | 8250 | 80 | 62 | 115 | 267.4 | 0.89 | 26.7 | 237.9 |  | 44
LV28 | 27.5 | 8250 | 85 | 62 | 115 | 274 | 0.968 | 29.75 | 265.1 |  | 44
LV28 | 27.5 | 8250 | 90 | 62 | 115 | 289.3 | 0.968 | 31.41 | 279.9 |  | 44
LV28 | 27.5 | 8250 | 70 | 67 | 115 | 289.1 | 0.435 | 14.13 | 125.9 |  | 44
LV28 | 27.5 | 8250 | 75 | 67 | 115 | 290.6 | 0.561 | 18.29 | 163 |  | 44
LV28 | 27.5 | 8250 | 80 | 67 | 115 | 291.6 | 0.687 | 22.48 | 200.3 |  | 44
LV28 | 27.5 | 8250 | 85 | 67 | 115 | 292.8 | 0.812 | 26.7 | 237.9 |  | 44
LV28 | 27.5 | 8250 | 90 | 67 | 115 | 293.2 | 0.939 | 30.89 | 275.2 |  | 44
LV28 | 27.5 | 8250 | 75 | 72 | 115 | 316.1 | 0.397 | 14.07 | 125.4 |  | 44
LV28 | 27.5 | 8250 | 80 | 72 | 115 | 317.6 | 0.513 | 18.27 | 162.8 |  | 44
LV28 | 27.5 | 8250 | 85 | 72 | 115 | 318.6 | 0.629 | 22.48 | 200.3 |  | 44
LV28 | 27.5 | 8250 | 90 | 72 | 115 | 319.4 | 0.745 | 26.7 | 237.9 |  | 44
LV28 | 27.5 | 8250 | 80 | 77 | 115 | 343.5 | 0.368 | 14.18 | 126.3 |  | 44
LV28 | 27.5 | 8250 | 85 | 77 | 115 | 344.6 | 0.474 | 18.33 | 163.3 |  | 44
LV28 | 27.5 | 8250 | 90 | 77 | 115 | 345.3 | 0.58 | 22.49 | 200.4 |  | 44
LV28 | 27.5 | 8250 | 65 | 57 | 125 | 224.4 | 0.677 | 17.05 | 151.9 |  | 44
LV28 | 27.5 | 8250 | 70 | 57 | 125 | 226 | 0.842 | 21.35 | 190.2 |  | 44
LV28 | 27.5 | 8250 | 75 | 57 | 125 | 229 | 0.967 | 24.86 | 221.5 |  | 44
LV28 | 27.5 | 8250 | 80 | 57 | 125 | 243.6 | 0.968 | 26.45 | 235.7 |  | 44
LV28 | 27.5 | 8250 | 85 | 57 | 125 | 258.4 | 0.967 | 28.06 | 250 |  | 44
LV28 | 27.5 | 8250 | 90 | 57 | 125 | 273.2 | 0.967 | 29.66 | 264.3 |  | 44
LV28 | 27.5 | 8250 | 65 | 62 | 125 | 245.4 | 0.484 | 13.32 | 118.7 |  | 44
LV28 | 27.5 | 8250 | 70 | 62 | 125 | 247 | 0.629 | 17.43 | 155.3 |  | 44
LV28 | 27.5 | 8250 | 75 | 62 | 125 | 248.1 | 0.774 | 21.55 | 192 |  | 44
LV28 | 27.5 | 8250 | 80 | 62 | 125 | 248.7 | 0.919 | 25.66 | 228.6 |  | 44
LV28 | 27.5 | 8250 | 85 | 62 | 125 | 258.5 | 0.968 | 28.07 | 250.1 |  | 44
LV28 | 27.5 | 8250 | 90 | 62 | 125 | 273.2 | 0.967 | 29.66 | 264.3 |  | 44
LV28 | 27.5 | 8250 | 70 | 67 | 125 | 269.4 | 0.435 | 13.16 | 117.3 |  | 44
LV28 | 27.5 | 8250 | 75 | 67 | 125 | 271 | 0.57 | 17.35 | 154.6 |  | 44
LV28 | 27.5 | 8250 | 80 | 67 | 125 | 271.9 | 0.706 | 21.55 | 192 |  | 44
LV28 | 27.5 | 8250 | 85 | 67 | 125 | 272.8 | 0.842 | 25.77 | 229.6 |  | 44
LV28 | 27.5 | 8250 | 90 | 67 | 125 | 274 | 0.958 | 29.45 | 262.4 |  | 44
LV28 | 27.5 | 8250 | 75 | 72 | 125 | 294.9 | 0.406 | 13.45 | 119.8 |  | 44
LV28 | 27.5 | 8250 | 80 | 72 | 125 | 296.2 | 0.522 | 17.36 | 154.7 |  | 44
LV28 | 27.5 | 8250 | 85 | 72 | 125 | 297 | 0.648 | 21.6 | 192.5 |  | 44
LV28 | 27.5 | 8250 | 90 | 72 | 125 | 297.5 | 0.774 | 25.84 | 230.2 |  | 44
LV28 | 27.5 | 8250 | 80 | 77 | 125 | 320.2 | 0.368 | 13.21 | 117.7 |  | 44
LV28 | 27.5 | 8250 | 85 | 77 | 125 | 321.4 | 0.484 | 17.45 | 155.5 |  | 44
LV28 | 27.5 | 8250 | 90 | 77 | 125 | 321.9 | 0.59 | 21.31 | 189.9 |  | 44
LV28 | 27.5 | 9625 | 65 | 57 | 75 | 311.3 | 0.658 | 19.7 | 204.8 |  | 42
LV28 | 27.5 | 9625 | 70 | 57 | 75 | 313 | 0.793 | 23.89 | 248.3 |  | 42
LV28 | 27.5 | 9625 | 75 | 57 | 75 | 314.3 | 0.929 | 28.08 | 291.9 |  | 42
LV28 | 27.5 | 9625 | 80 | 57 | 75 | 328 | 0.967 | 30.52 | 317.3 |  | 42
LV28 | 27.5 | 9625 | 85 | 57 | 75 | 346 | 0.968 | 32.21 | 334.8 |  | 42
LV28 | 27.5 | 9625 | 90 | 57 | 75 | 364 | 0.967 | 33.87 | 352.1 |  | 42
LV28 | 27.5 | 9625 | 65 | 62 | 75 | 339.2 | 0.474 | 15.47 | 160.8 |  | 42
LV28 | 27.5 | 9625 | 70 | 62 | 75 | 341 | 0.6 | 19.67 | 204.5 |  | 42
LV28 | 27.5 | 9625 | 75 | 62 | 75 | 342.2 | 0.726 | 23.89 | 248.3 |  | 42
LV28 | 27.5 | 9625 | 80 | 62 | 75 | 343.6 | 0.851 | 28.14 | 292.5 |  | 42
LV28 | 27.5 | 9625 | 85 | 62 | 75 | 346.2 | 0.967 | 32.22 | 334.9 |  | 42
LV28 | 27.5 | 9625 | 90 | 62 | 75 | 364.2 | 0.967 | 33.89 | 352.3 |  | 42
LV28 | 27.5 | 9625 | 70 | 67 | 75 | 370.3 | 0.435 | 15.51 | 161.2 |  | 42
LV28 | 27.5 | 9625 | 75 | 67 | 75 | 372.2 | 0.551 | 19.74 | 205.2 |  | 42
LV28 | 27.5 | 9625 | 80 | 67 | 75 | 373.6 | 0.668 | 23.99 | 249.4 |  | 42
LV28 | 27.5 | 9625 | 85 | 67 | 75 | 374.5 | 0.783 | 28.23 | 293.4 |  | 42
LV28 | 27.5 | 9625 | 90 | 67 | 75 | 375.7 | 0.9 | 32.52 | 338 |  | 42
LV28 | 27.5 | 9625 | 75 | 72 | 75 | 402.8 | 0.396 | 15.36 | 159.7 |  | 42
LV28 | 27.5 | 9625 | 80 | 72 | 75 | 404.4 | 0.503 | 19.57 | 203.4 |  | 42
LV28 | 27.5 | 9625 | 85 | 72 | 75 | 405.3 | 0.609 | 23.76 | 247 |  | 42
LV28 | 27.5 | 9625 | 90 | 72 | 75 | 406.3 | 0.726 | 28.36 | 294.8 |  | 42
LV28 | 27.5 | 9625 | 80 | 77 | 75 | 437.8 | 0.368 | 15.48 | 160.9 |  | 42
LV28 | 27.5 | 9625 | 85 | 77 | 75 | 437.8 | 0.464 | 19.56 | 203.3 |  | 42
LV28 | 27.5 | 9625 | 90 | 77 | 75 | 438.8 | 0.561 | 23.68 | 246.2 |  | 42
LV28 | 27.5 | 9625 | 65 | 57 | 85 | 296.7 | 0.668 | 19.06 | 198.1 |  | 42
LV28 | 27.5 | 9625 | 70 | 57 | 85 | 298.1 | 0.812 | 23.3 | 242.2 |  | 42
LV28 | 27.5 | 9625 | 75 | 57 | 85 | 299.5 | 0.948 | 27.31 | 283.9 |  | 42
LV28 | 27.5 | 9625 | 80 | 57 | 85 | 315.1 | 0.967 | 29.32 | 304.8 |  | 42
LV28 | 27.5 | 9625 | 85 | 57 | 85 | 332.9 | 0.968 | 30.99 | 322.1 |  | 42
LV28 | 27.5 | 9625 | 90 | 57 | 85 | 350.8 | 0.968 | 32.65 | 339.4 |  | 42
LV28 | 27.5 | 9625 | 65 | 62 | 85 | 323.2 | 0.474 | 14.74 | 153.2 |  | 42
LV28 | 27.5 | 9625 | 70 | 62 | 85 | 325.1 | 0.609 | 19.06 | 198.1 |  | 42
LV28 | 27.5 | 9625 | 75 | 62 | 85 | 326.5 | 0.745 | 23.4 | 243.2 |  | 42
LV28 | 27.5 | 9625 | 80 | 62 | 85 | 327.5 | 0.871 | 27.43 | 285.1 |  | 42
LV28 | 27.5 | 9625 | 85 | 62 | 85 | 333.1 | 0.967 | 31 | 322.2 |  | 42
LV28 | 27.5 | 9625 | 90 | 62 | 85 | 351 | 0.967 | 32.66 | 339.5 |  | 42
LV28 | 27.5 | 9625 | 70 | 67 | 85 | 353.4 | 0.435 | 14.8 | 153.8 |  | 42
LV28 | 27.5 | 9625 | 75 | 67 | 85 | 354.9 | 0.561 | 19.15 | 199.1 |  | 42
LV28 | 27.5 | 9625 | 80 | 67 | 85 | 356.7 | 0.677 | 23.24 | 241.6 |  | 42
LV28 | 27.5 | 9625 | 85 | 67 | 85 | 357.7 | 0.803 | 27.63 | 287.2 |  | 42
LV28 | 27.5 | 9625 | 90 | 67 | 85 | 358.4 | 0.919 | 31.69 | 329.4 |  | 42
LV28 | 27.5 | 9625 | 75 | 72 | 85 | 384.3 | 0.397 | 14.66 | 152.4 |  | 42
LV28 | 27.5 | 9625 | 80 | 72 | 85 | 386.4 | 0.513 | 19.06 | 198.1 |  | 42
LV28 | 27.5 | 9625 | 85 | 72 | 85 | 387.3 | 0.619 | 23.07 | 239.8 |  | 42
LV28 | 27.5 | 9625 | 90 | 72 | 85 | 388.2 | 0.735 | 27.46 | 285.4 |  | 42
LV28 | 27.5 | 9625 | 80 | 77 | 85 | 417.4 | 0.368 | 14.77 | 153.5 |  | 42
LV28 | 27.5 | 9625 | 85 | 77 | 85 | 419 | 0.464 | 18.72 | 194.6 |  | 42
LV28 | 27.5 | 9625 | 90 | 77 | 85 | 419.8 | 0.571 | 23.05 | 239.6 |  | 42
LV28 | 27.5 | 9625 | 65 | 57 | 95 | 281.1 | 0.677 | 18.32 | 190.4 |  | 43
LV28 | 27.5 | 9625 | 70 | 57 | 95 | 282.5 | 0.822 | 22.35 | 232.3 |  | 43
LV28 | 27.5 | 9625 | 75 | 57 | 95 | 284.7 | 0.957 | 26.22 | 272.6 |  | 43
LV28 | 27.5 | 9625 | 80 | 57 | 95 | 301.4 | 0.967 | 28.04 | 291.5 |  | 43
LV28 | 27.5 | 9625 | 85 | 57 | 95 | 318.7 | 0.967 | 29.66 | 308.3 |  | 43
LV28 | 27.5 | 9625 | 90 | 57 | 95 | 336.3 | 0.967 | 31.29 | 325.3 |  | 43
LV28 | 27.5 | 9625 | 65 | 62 | 95 | 306.5 | 0.484 | 14.26 | 148.2 |  | 43
LV28 | 27.5 | 9625 | 70 | 62 | 95 | 308.3 | 0.619 | 18.36 | 190.9 |  | 43
LV28 | 27.5 | 9625 | 75 | 62 | 95 | 309.6 | 0.755 | 22.47 | 233.6 |  | 43
LV28 | 27.5 | 9625 | 80 | 62 | 95 | 310.8 | 0.89 | 26.61 | 276.6 |  | 43
LV28 | 27.5 | 9625 | 85 | 62 | 95 | 319 | 0.967 | 29.68 | 308.5 |  | 43
LV28 | 27.5 | 9625 | 90 | 62 | 95 | 336.5 | 0.967 | 31.31 | 325.5 |  | 43
LV28 | 27.5 | 9625 | 70 | 67 | 95 | 335.5 | 0.435 | 14.05 | 146.1 |  | 43
LV28 | 27.5 | 9625 | 75 | 67 | 95 | 337.4 | 0.561 | 18.21 | 189.3 |  | 43
LV28 | 27.5 | 9625 | 80 | 67 | 95 | 338.7 | 0.687 | 22.38 | 232.6 |  | 43
LV28 | 27.5 | 9625 | 85 | 67 | 95 | 339.9 | 0.813 | 26.57 | 276.2 |  | 43
LV28 | 27.5 | 9625 | 90 | 67 | 95 | 340.7 | 0.938 | 30.76 | 319.7 |  | 43
LV28 | 27.5 | 9625 | 75 | 72 | 95 | 365.4 | 0.397 | 13.94 | 144.9 |  | 43
LV28 | 27.5 | 9625 | 80 | 72 | 95 | 367.1 | 0.513 | 18.1 | 188.2 |  | 43
LV28 | 27.5 | 9625 | 85 | 72 | 95 | 368 | 0.639 | 22.61 | 235 |  | 43
LV28 | 27.5 | 9625 | 90 | 72 | 95 | 368.8 | 0.755 | 26.77 | 278.3 |  | 43
LV28 | 27.5 | 9625 | 80 | 77 | 95 | 396.8 | 0.368 | 14.04 | 145.9 |  | 43
LV28 | 27.5 | 9625 | 85 | 77 | 95 | 398.3 | 0.474 | 18.16 | 188.8 |  | 43
LV28 | 27.5 | 9625 | 90 | 77 | 95 | 399.2 | 0.58 | 22.29 | 231.7 |  | 43
LV28 | 27.5 | 9625 | 65 | 57 | 105 | 264.8 | 0.677 | 17.25 | 179.3 |  | 43
LV28 | 27.5 | 9625 | 70 | 57 | 105 | 266.4 | 0.842 | 21.57 | 224.2 |  | 43
LV28 | 27.5 | 9625 | 75 | 57 | 105 | 270.1 | 0.967 | 25.14 | 261.3 |  | 43
LV28 | 27.5 | 9625 | 80 | 57 | 105 | 287 | 0.967 | 26.71 | 277.6 |  | 43
LV28 | 27.5 | 9625 | 85 | 57 | 105 | 304 | 0.967 | 28.29 | 294.1 |  | 43
LV28 | 27.5 | 9625 | 90 | 57 | 105 | 320.9 | 0.967 | 29.86 | 310.4 |  | 43
LV28 | 27.5 | 9625 | 65 | 62 | 105 | 288.9 | 0.484 | 13.45 | 139.8 |  | 43
LV28 | 27.5 | 9625 | 70 | 62 | 105 | 290.8 | 0.629 | 17.59 | 182.9 |  | 43
LV28 | 27.5 | 9625 | 75 | 62 | 105 | 292 | 0.774 | 21.74 | 226 |  | 43
LV28 | 27.5 | 9625 | 80 | 62 | 105 | 293.1 | 0.909 | 25.64 | 266.5 |  | 43
LV28 | 27.5 | 9625 | 85 | 62 | 105 | 304 | 0.967 | 28.29 | 294.1 |  | 43
LV28 | 27.5 | 9625 | 90 | 62 | 105 | 320.9 | 0.968 | 29.87 | 310.5 |  | 43
LV28 | 27.5 | 9625 | 70 | 67 | 105 | 316.7 | 0.435 | 13.27 | 137.9 |  | 43
LV28 | 27.5 | 9625 | 75 | 67 | 105 | 318.5 | 0.571 | 17.49 | 181.8 |  | 43
LV28 | 27.5 | 9625 | 80 | 67 | 105 | 319.7 | 0.706 | 21.72 | 225.8 |  | 43
LV28 | 27.5 | 9625 | 85 | 67 | 105 | 320.8 | 0.842 | 25.97 | 270 |  | 43
LV28 | 27.5 | 9625 | 90 | 67 | 105 | 322.4 | 0.958 | 29.71 | 308.8 |  | 43
LV28 | 27.5 | 9625 | 75 | 72 | 105 | 345.1 | 0.406 | 13.49 | 140.2 |  | 43
LV28 | 27.5 | 9625 | 80 | 72 | 105 | 346.7 | 0.522 | 17.42 | 181.1 |  | 43
LV28 | 27.5 | 9625 | 85 | 72 | 105 | 347.6 | 0.648 | 21.67 | 225.3 |  | 43
LV28 | 27.5 | 9625 | 90 | 72 | 105 | 348 | 0.774 | 25.91 | 269.3 |  | 43
LV28 | 27.5 | 9625 | 80 | 77 | 105 | 375.1 | 0.368 | 13.27 | 137.9 |  | 43
LV28 | 27.5 | 9625 | 85 | 77 | 105 | 376.5 | 0.484 | 17.52 | 182.1 |  | 43
LV28 | 27.5 | 9625 | 90 | 77 | 105 | 377 | 0.59 | 21.4 | 222.5 |  | 43
LV28 | 27.5 | 9625 | 65 | 57 | 115 | 247.9 | 0.697 | 16.61 | 172.7 |  | 44
LV28 | 27.5 | 9625 | 70 | 57 | 115 | 249.2 | 0.861 | 20.63 | 214.5 |  | 44
LV28 | 27.5 | 9625 | 75 | 57 | 115 | 255.4 | 0.968 | 23.77 | 247.1 |  | 44
LV28 | 27.5 | 9625 | 80 | 57 | 115 | 271.7 | 0.967 | 25.28 | 262.8 |  | 44
LV28 | 27.5 | 9625 | 85 | 57 | 115 | 287.7 | 0.967 | 26.77 | 278.3 |  | 44
LV28 | 27.5 | 9625 | 90 | 57 | 115 | 304.5 | 0.967 | 28.33 | 294.5 |  | 44
LV28 | 27.5 | 9625 | 65 | 62 | 115 | 270.5 | 0.484 | 12.58 | 130.8 |  | 44
LV28 | 27.5 | 9625 | 70 | 62 | 115 | 272.2 | 0.639 | 16.72 | 173.8 |  | 44
LV28 | 27.5 | 9625 | 75 | 62 | 115 | 273.6 | 0.784 | 20.63 | 214.4 |  | 44
LV28 | 27.5 | 9625 | 80 | 62 | 115 | 274.7 | 0.938 | 24.8 | 257.8 |  | 44
LV28 | 27.5 | 9625 | 85 | 62 | 115 | 288.2 | 0.967 | 26.82 | 278.8 |  | 44
LV28 | 27.5 | 9625 | 90 | 62 | 115 | 304.6 | 0.967 | 28.34 | 294.6 |  | 44
LV28 | 27.5 | 9625 | 70 | 67 | 115 | 296.9 | 0.445 | 12.71 | 132.1 |  | 44
LV28 | 27.5 | 9625 | 75 | 67 | 115 | 298.7 | 0.581 | 16.68 | 173.4 |  | 44
LV28 | 27.5 | 9625 | 80 | 67 | 115 | 299.8 | 0.725 | 20.92 | 217.5 |  | 44
LV28 | 27.5 | 9625 | 85 | 67 | 115 | 300.5 | 0.861 | 24.89 | 258.7 |  | 44
LV28 | 27.5 | 9625 | 90 | 67 | 115 | 304.6 | 0.967 | 28.35 | 294.7 |  | 44
LV28 | 27.5 | 9625 | 75 | 72 | 115 | 323.7 | 0.406 | 12.65 | 131.5 |  | 44
LV28 | 27.5 | 9625 | 80 | 72 | 115 | 325.2 | 0.532 | 16.64 | 173 |  | 44
LV28 | 27.5 | 9625 | 85 | 72 | 115 | 326.1 | 0.668 | 20.94 | 217.7 |  | 44
LV28 | 27.5 | 9625 | 90 | 72 | 115 | 326.7 | 0.793 | 24.93 | 259.1 |  | 44
LV28 | 27.5 | 9625 | 80 | 77 | 115 | 351.9 | 0.367 | 12.44 | 129.3 |  | 44
LV28 | 27.5 | 9625 | 85 | 77 | 115 | 353.2 | 0.493 | 16.76 | 174.2 |  | 44
LV28 | 27.5 | 9625 | 90 | 77 | 115 | 353.7 | 0.61 | 20.74 | 215.6 |  | 44
LV28 | 27.5 | 9625 | 65 | 57 | 125 | 230.1 | 0.706 | 15.63 | 162.5 |  | 44
LV28 | 27.5 | 9625 | 70 | 57 | 125 | 231.3 | 0.88 | 19.59 | 203.6 |  | 44
LV28 | 27.5 | 9625 | 75 | 57 | 125 | 239.9 | 0.967 | 22.33 | 232.1 |  | 44
LV28 | 27.5 | 9625 | 80 | 57 | 125 | 255.5 | 0.967 | 23.77 | 247.1 |  | 44
LV28 | 27.5 | 9625 | 85 | 57 | 125 | 271.1 | 0.968 | 25.23 | 262.3 |  | 44
LV28 | 27.5 | 9625 | 90 | 57 | 125 | 286.7 | 0.968 | 26.69 | 277.4 |  | 44
LV28 | 27.5 | 9625 | 65 | 62 | 125 | 251.3 | 0.484 | 11.7 | 121.6 |  | 44
LV28 | 27.5 | 9625 | 70 | 62 | 125 | 253.1 | 0.648 | 15.79 | 164.1 |  | 44
LV28 | 27.5 | 9625 | 75 | 62 | 125 | 254.5 | 0.813 | 19.89 | 206.8 |  | 44
LV28 | 27.5 | 9625 | 80 | 62 | 125 | 256.1 | 0.958 | 23.6 | 245.3 |  | 44
LV28 | 27.5 | 9625 | 85 | 62 | 125 | 271.1 | 0.968 | 25.23 | 262.3 |  | 44
LV28 | 27.5 | 9625 | 90 | 62 | 125 | 286.8 | 0.967 | 26.69 | 277.4 |  | 44
LV28 | 27.5 | 9625 | 70 | 67 | 125 | 276.2 | 0.445 | 11.82 | 122.9 |  | 44
LV28 | 27.5 | 9625 | 75 | 67 | 125 | 278 | 0.59 | 15.78 | 164 |  | 44
LV28 | 27.5 | 9625 | 80 | 67 | 125 | 278.8 | 0.745 | 19.97 | 207.6 |  | 44
LV28 | 27.5 | 9625 | 85 | 67 | 125 | 279.4 | 0.89 | 23.92 | 248.7 |  | 44
LV28 | 27.5 | 9625 | 90 | 67 | 125 | 286.8 | 0.968 | 26.7 | 277.5 |  | 44
LV28 | 27.5 | 9625 | 75 | 72 | 125 | 301.3 | 0.406 | 11.77 | 122.4 |  | 44
LV28 | 27.5 | 9625 | 80 | 72 | 125 | 302.5 | 0.542 | 15.77 | 163.9 |  | 44
LV28 | 27.5 | 9625 | 85 | 72 | 125 | 303.3 | 0.687 | 20.04 | 208.3 |  | 44
LV28 | 27.5 | 9625 | 90 | 72 | 125 | 303.8 | 0.822 | 24.03 | 249.8 |  | 44
LV28 | 27.5 | 9625 | 80 | 77 | 125 | 327.7 | 0.377 | 11.89 | 123.6 |  | 44
LV28 | 27.5 | 9625 | 85 | 77 | 125 | 328.8 | 0.503 | 15.91 | 165.4 |  | 44
LV28 | 27.5 | 9625 | 90 | 77 | 125 | 329.1 | 0.629 | 19.9 | 206.9 |  | 44
LV28 | 27.5 | 11000 | 65 | 57 | 75 | 319.9 | 0.677 | 18.23 | 216.6 |  | 42
LV28 | 27.5 | 11000 | 70 | 57 | 75 | 321.1 | 0.822 | 22.22 | 264 |  | 42
LV28 | 27.5 | 11000 | 75 | 57 | 75 | 324 | 0.967 | 26.38 | 313.4 |  | 42
LV28 | 27.5 | 11000 | 80 | 57 | 75 | 342.8 | 0.968 | 27.92 | 331.7 |  | 42
LV28 | 27.5 | 11000 | 85 | 57 | 75 | 362 | 0.967 | 29.48 | 350.2 |  | 42
LV28 | 27.5 | 11000 | 90 | 57 | 75 | 381.2 | 0.967 | 31.04 | 368.8 |  | 42
LV28 | 27.5 | 11000 | 65 | 62 | 75 | 347.8 | 0.484 | 14.16 | 168.2 |  | 42
LV28 | 27.5 | 11000 | 70 | 62 | 75 | 349.8 | 0.619 | 18.22 | 216.5 |  | 42
LV28 | 27.5 | 11000 | 75 | 62 | 75 | 351.3 | 0.755 | 22.31 | 265.1 |  | 42
LV28 | 27.5 | 11000 | 80 | 62 | 75 | 352.8 | 0.89 | 26.43 | 314 |  | 42
LV28 | 27.5 | 11000 | 85 | 62 | 75 | 362.1 | 0.967 | 29.49 | 350.3 |  | 42
LV28 | 27.5 | 11000 | 90 | 62 | 75 | 381.3 | 0.967 | 31.05 | 368.9 |  | 42
LV28 | 27.5 | 11000 | 70 | 67 | 75 | 379.3 | 0.435 | 13.9 | 165.1 |  | 42
LV28 | 27.5 | 11000 | 75 | 67 | 75 | 381.4 | 0.571 | 18.32 | 217.7 |  | 42
LV28 | 27.5 | 11000 | 80 | 67 | 75 | 382.8 | 0.696 | 22.44 | 266.6 |  | 42
LV28 | 27.5 | 11000 | 85 | 67 | 75 | 383.9 | 0.822 | 26.57 | 315.7 |  | 42
LV28 | 27.5 | 11000 | 90 | 67 | 75 | 384.7 | 0.948 | 30.7 | 364.7 |  | 42
LV28 | 27.5 | 11000 | 75 | 72 | 75 | 412.4 | 0.397 | 13.77 | 163.6 |  | 42
LV28 | 27.5 | 11000 | 80 | 72 | 75 | 414.1 | 0.522 | 18.21 | 216.3 |  | 42
LV28 | 27.5 | 11000 | 85 | 72 | 75 | 415.1 | 0.639 | 22.31 | 265.1 |  | 42
LV28 | 27.5 | 11000 | 90 | 72 | 75 | 416.1 | 0.755 | 26.43 | 314 |  | 42
LV28 | 27.5 | 11000 | 80 | 77 | 75 | 446.9 | 0.368 | 13.83 | 164.3 |  | 42
LV28 | 27.5 | 11000 | 85 | 77 | 75 | 447.9 | 0.474 | 17.87 | 212.3 |  | 42
LV28 | 27.5 | 11000 | 90 | 77 | 75 | 448.9 | 0.59 | 22.3 | 264.9 |  | 42
LV28 | 27.5 | 11000 | 65 | 57 | 85 | 304.3 | 0.687 | 17.59 | 209 |  | 42
LV28 | 27.5 | 11000 | 70 | 57 | 85 | 305.7 | 0.842 | 21.66 | 257.3 |  | 42
LV28 | 27.5 | 11000 | 75 | 57 | 85 | 310.3 | 0.967 | 25.27 | 300.2 |  | 42
LV28 | 27.5 | 11000 | 80 | 57 | 85 | 329 | 0.967 | 26.79 | 318.3 |  | 42
LV28 | 27.5 | 11000 | 85 | 57 | 85 | 347.9 | 0.967 | 28.32 | 336.5 |  | 42
LV28 | 27.5 | 11000 | 90 | 57 | 85 | 366.7 | 0.968 | 29.87 | 354.8 |  | 42
LV28 | 27.5 | 11000 | 65 | 62 | 85 | 330.9 | 0.484 | 13.48 | 160.1 |  | 42
LV28 | 27.5 | 11000 | 70 | 62 | 85 | 333.1 | 0.629 | 17.63 | 209.4 |  | 42
LV28 | 27.5 | 11000 | 75 | 62 | 85 | 334.8 | 0.774 | 21.81 | 259.1 |  | 42
LV28 | 27.5 | 11000 | 80 | 62 | 85 | 335.4 | 0.909 | 25.66 | 304.9 |  | 42
LV28 | 27.5 | 11000 | 85 | 62 | 85 | 348 | 0.967 | 28.33 | 336.6 |  | 42
LV28 | 27.5 | 11000 | 90 | 62 | 85 | 366.8 | 0.967 | 29.87 | 354.8 |  | 42
LV28 | 27.5 | 11000 | 70 | 67 | 85 | 361.6 | 0.435 | 13.25 | 157.4 |  | 42
LV28 | 27.5 | 11000 | 75 | 67 | 85 | 363.6 | 0.571 | 17.47 | 207.5 |  | 42
LV28 | 27.5 | 11000 | 80 | 67 | 85 | 365 | 0.706 | 21.7 | 257.8 |  | 42
LV28 | 27.5 | 11000 | 85 | 67 | 85 | 366.4 | 0.842 | 25.96 | 308.4 |  | 42
LV28 | 27.5 | 11000 | 90 | 67 | 85 | 368.2 | 0.958 | 29.68 | 352.6 |  | 42
LV28 | 27.5 | 11000 | 75 | 72 | 85 | 393.5 | 0.406 | 13.46 | 159.9 |  | 42
LV28 | 27.5 | 11000 | 80 | 72 | 85 | 395.4 | 0.523 | 17.39 | 206.6 |  | 42
LV28 | 27.5 | 11000 | 85 | 72 | 85 | 396.4 | 0.648 | 21.62 | 256.9 |  | 42
LV28 | 27.5 | 11000 | 90 | 72 | 85 | 397.1 | 0.774 | 25.87 | 307.3 |  | 42
LV28 | 27.5 | 11000 | 80 | 77 | 85 | 426.3 | 0.368 | 13.19 | 156.7 |  | 42
LV28 | 27.5 | 11000 | 85 | 77 | 85 | 428 | 0.484 | 17.42 | 207 |  | 42
LV28 | 27.5 | 11000 | 90 | 77 | 85 | 428.9 | 0.6 | 21.65 | 257.2 |  | 42
LV28 | 27.5 | 11000 | 65 | 57 | 95 | 287.9 | 0.696 | 16.88 | 200.5 |  | 43
LV28 | 27.5 | 11000 | 70 | 57 | 95 | 289.4 | 0.851 | 20.73 | 246.3 |  | 43
LV28 | 27.5 | 11000 | 75 | 57 | 95 | 296.2 | 0.967 | 24.12 | 286.5 |  | 43
LV28 | 27.5 | 11000 | 80 | 57 | 95 | 314.4 | 0.967 | 25.6 | 304.1 |  | 43
LV28 | 27.5 | 11000 | 85 | 57 | 95 | 332.9 | 0.968 | 27.11 | 322.1 |  | 43
LV28 | 27.5 | 11000 | 90 | 57 | 95 | 351.2 | 0.967 | 28.59 | 339.7 |  | 43
LV28 | 27.5 | 11000 | 65 | 62 | 95 | 313.4 | 0.484 | 12.76 | 151.6 |  | 43
LV28 | 27.5 | 11000 | 70 | 62 | 95 | 315.7 | 0.638 | 16.96 | 201.5 |  | 43
LV28 | 27.5 | 11000 | 75 | 62 | 95 | 317.1 | 0.784 | 20.92 | 248.5 |  | 43
LV28 | 27.5 | 11000 | 80 | 62 | 95 | 318.5 | 0.929 | 24.9 | 295.8 |  | 43
LV28 | 27.5 | 11000 | 85 | 62 | 95 | 332.8 | 0.967 | 27.1 | 321.9 |  | 43
LV28 | 27.5 | 11000 | 90 | 62 | 95 | 351.3 | 0.967 | 28.6 | 339.8 |  | 43
LV28 | 27.5 | 11000 | 70 | 67 | 95 | 342.8 | 0.445 | 12.84 | 152.5 |  | 43
LV28 | 27.5 | 11000 | 75 | 67 | 95 | 344.8 | 0.58 | 16.84 | 200.1 |  | 43
LV28 | 27.5 | 11000 | 80 | 67 | 95 | 346.4 | 0.716 | 20.88 | 248 |  | 43
LV28 | 27.5 | 11000 | 85 | 67 | 95 | 347.5 | 0.861 | 25.19 | 299.2 |  | 43
LV28 | 27.5 | 11000 | 90 | 67 | 95 | 351.3 | 0.968 | 28.61 | 339.9 |  | 43
LV28 | 27.5 | 11000 | 75 | 72 | 95 | 373.6 | 0.406 | 12.78 | 151.8 |  | 43
LV28 | 27.5 | 11000 | 80 | 72 | 95 | 375.4 | 0.532 | 16.81 | 199.7 |  | 43
LV28 | 27.5 | 11000 | 85 | 72 | 95 | 376.4 | 0.658 | 20.84 | 247.6 |  | 43
LV28 | 27.5 | 11000 | 90 | 72 | 95 | 376.9 | 0.793 | 25.16 | 298.9 |  | 43
LV28 | 27.5 | 11000 | 80 | 77 | 95 | 405 | 0.368 | 12.53 | 148.9 |  | 43
LV28 | 27.5 | 11000 | 85 | 77 | 95 | 406.9 | 0.484 | 16.57 | 196.8 |  | 43
LV28 | 27.5 | 11000 | 90 | 77 | 95 | 407.5 | 0.609 | 20.9 | 248.3 |  | 43
LV28 | 27.5 | 11000 | 65 | 57 | 105 | 270.8 | 0.706 | 16.09 | 191.2 |  | 43
LV28 | 27.5 | 11000 | 70 | 57 | 105 | 272.1 | 0.88 | 20.16 | 239.5 |  | 43
LV28 | 27.5 | 11000 | 75 | 57 | 105 | 281.1 | 0.968 | 22.9 | 272 |  | 43
LV28 | 27.5 | 11000 | 80 | 57 | 105 | 298.9 | 0.968 | 24.34 | 289.2 |  | 43
LV28 | 27.5 | 11000 | 85 | 57 | 105 | 316.8 | 0.967 | 25.79 | 306.4 |  | 43
LV28 | 27.5 | 11000 | 90 | 57 | 105 | 334.7 | 0.967 | 27.26 | 323.8 |  | 43
LV28 | 27.5 | 11000 | 65 | 62 | 105 | 295.5 | 0.484 | 12.03 | 142.9 |  | 43
LV28 | 27.5 | 11000 | 70 | 62 | 105 | 297.3 | 0.648 | 16.22 | 192.7 |  | 43
LV28 | 27.5 | 11000 | 75 | 62 | 105 | 298.8 | 0.803 | 20.19 | 239.9 |  | 43
LV28 | 27.5 | 11000 | 80 | 62 | 105 | 300.4 | 0.958 | 24.22 | 287.7 |  | 43
LV28 | 27.5 | 11000 | 85 | 62 | 105 | 316.9 | 0.967 | 25.8 | 306.5 |  | 43
LV28 | 27.5 | 11000 | 90 | 62 | 105 | 334.8 | 0.967 | 27.26 | 323.9 |  | 43
LV28 | 27.5 | 11000 | 70 | 67 | 105 | 323.2 | 0.445 | 12.1 | 143.8 |  | 43
LV28 | 27.5 | 11000 | 75 | 67 | 105 | 325.1 | 0.59 | 16.15 | 191.9 |  | 43
LV28 | 27.5 | 11000 | 80 | 67 | 105 | 326.2 | 0.735 | 20.19 | 239.8 |  | 43
LV28 | 27.5 | 11000 | 85 | 67 | 105 | 327.5 | 0.88 | 24.27 | 288.3 |  | 43
LV28 | 27.5 | 11000 | 90 | 67 | 105 | 335.1 | 0.967 | 27.29 | 324.2 |  | 43
LV28 | 27.5 | 11000 | 75 | 72 | 105 | 352.2 | 0.406 | 12.05 | 143.1 |  | 43
LV28 | 27.5 | 11000 | 80 | 72 | 105 | 354.2 | 0.542 | 16.15 | 191.9 |  | 43
LV28 | 27.5 | 11000 | 85 | 72 | 105 | 355 | 0.677 | 20.24 | 240.4 |  | 43
LV28 | 27.5 | 11000 | 90 | 72 | 105 | 355.8 | 0.813 | 24.34 | 289.1 |  | 43
LV28 | 27.5 | 11000 | 80 | 77 | 105 | 382.2 | 0.368 | 11.83 | 140.5 |  | 43
LV28 | 27.5 | 11000 | 85 | 77 | 105 | 383.7 | 0.493 | 15.93 | 189.3 |  | 43
LV28 | 27.5 | 11000 | 90 | 77 | 105 | 384.3 | 0.619 | 20.03 | 237.9 |  | 43
LV28 | 27.5 | 11000 | 65 | 57 | 115 | 252.9 | 0.716 | 15.24 | 181 |  | 44
LV28 | 27.5 | 11000 | 70 | 57 | 115 | 254.4 | 0.899 | 19.26 | 228.8 |  | 44
LV28 | 27.5 | 11000 | 75 | 57 | 115 | 265.5 | 0.967 | 21.62 | 256.8 |  | 44
LV28 | 27.5 | 11000 | 80 | 57 | 115 | 282.6 | 0.967 | 23.01 | 273.3 |  | 44
LV28 | 27.5 | 11000 | 85 | 57 | 115 | 299.6 | 0.968 | 24.4 | 289.9 |  | 44
LV28 | 27.5 | 11000 | 90 | 57 | 115 | 316.9 | 0.967 | 25.81 | 306.6 |  | 44
LV28 | 27.5 | 11000 | 65 | 62 | 115 | 276.1 | 0.493 | 11.46 | 136.2 |  | 44
LV28 | 27.5 | 11000 | 70 | 62 | 115 | 278.1 | 0.658 | 15.4 | 183 |  | 44
LV28 | 27.5 | 11000 | 75 | 62 | 115 | 279.6 | 0.822 | 19.35 | 229.9 |  | 44
LV28 | 27.5 | 11000 | 80 | 62 | 115 | 282.6 | 0.967 | 23.01 | 273.4 |  | 44
LV28 | 27.5 | 11000 | 85 | 62 | 115 | 299.8 | 0.967 | 24.41 | 290 |  | 44
LV28 | 27.5 | 11000 | 90 | 62 | 115 | 317.1 | 0.967 | 25.82 | 306.7 |  | 44
LV28 | 27.5 | 11000 | 70 | 67 | 115 | 302.4 | 0.445 | 11.33 | 134.6 |  | 44
LV28 | 27.5 | 11000 | 75 | 67 | 115 | 304.2 | 0.6 | 15.36 | 182.5 |  | 44
LV28 | 27.5 | 11000 | 80 | 67 | 115 | 305.3 | 0.754 | 19.39 | 230.3 |  | 44
LV28 | 27.5 | 11000 | 85 | 67 | 115 | 306.2 | 0.909 | 23.43 | 278.4 |  | 44
LV28 | 27.5 | 11000 | 90 | 67 | 115 | 317.1 | 0.968 | 25.82 | 306.8 |  | 44
LV28 | 27.5 | 11000 | 75 | 72 | 115 | 330.2 | 0.406 | 11.3 | 134.2 |  | 44
LV28 | 27.5 | 11000 | 80 | 72 | 115 | 331.7 | 0.551 | 15.4 | 182.9 |  | 44
LV28 | 27.5 | 11000 | 85 | 72 | 115 | 332.6 | 0.697 | 19.5 | 231.7 |  | 44
LV28 | 27.5 | 11000 | 90 | 72 | 115 | 332.9 | 0.842 | 23.59 | 280.2 |  | 44
LV28 | 27.5 | 11000 | 80 | 77 | 115 | 358.4 | 0.377 | 11.38 | 135.2 |  | 44
LV28 | 27.5 | 11000 | 85 | 77 | 115 | 359.6 | 0.503 | 15.23 | 180.9 |  | 44
LV28 | 27.5 | 11000 | 90 | 77 | 115 | 360.1 | 0.638 | 19.35 | 229.9 |  | 44
LV28 | 27.5 | 11000 | 65 | 57 | 125 | 234.2 | 0.735 | 14.49 | 172.2 |  | 44
LV28 | 27.5 | 11000 | 70 | 57 | 125 | 235.6 | 0.929 | 18.42 | 218.8 |  | 44
LV28 | 27.5 | 11000 | 75 | 57 | 125 | 248.8 | 0.967 | 20.26 | 240.7 |  | 44
LV28 | 27.5 | 11000 | 80 | 57 | 125 | 265.2 | 0.968 | 21.6 | 256.6 |  | 44
LV28 | 27.5 | 11000 | 85 | 57 | 125 | 281.6 | 0.967 | 22.93 | 272.4 |  | 44
LV28 | 27.5 | 11000 | 90 | 57 | 125 | 298 | 0.967 | 24.27 | 288.3 |  | 44
LV28 | 27.5 | 11000 | 65 | 62 | 125 | 256.2 | 0.493 | 10.64 | 126.4 |  | 44
LV28 | 27.5 | 11000 | 70 | 62 | 125 | 258.1 | 0.668 | 14.5 | 172.3 |  | 44
LV28 | 27.5 | 11000 | 75 | 62 | 125 | 259.1 | 0.851 | 18.57 | 220.6 |  | 44
LV28 | 27.5 | 11000 | 80 | 62 | 125 | 265.3 | 0.967 | 21.6 | 256.6 |  | 44
LV28 | 27.5 | 11000 | 85 | 62 | 125 | 281.5 | 0.967 | 22.92 | 272.3 |  | 44
LV28 | 27.5 | 11000 | 90 | 62 | 125 | 298.1 | 0.967 | 24.27 | 288.3 |  | 44
LV28 | 27.5 | 11000 | 70 | 67 | 125 | 280.9 | 0.455 | 10.75 | 127.7 |  | 44
LV28 | 27.5 | 11000 | 75 | 67 | 125 | 282.2 | 0.619 | 14.71 | 174.7 |  | 44
LV28 | 27.5 | 11000 | 80 | 67 | 125 | 283.7 | 0.784 | 18.71 | 222.3 |  | 44
LV28 | 27.5 | 11000 | 85 | 67 | 125 | 284.3 | 0.938 | 22.46 | 266.8 |  | 44
LV28 | 27.5 | 11000 | 90 | 67 | 125 | 298.2 | 0.967 | 24.28 | 288.5 |  | 44
LV28 | 27.5 | 11000 | 75 | 72 | 125 | 306.8 | 0.416 | 10.74 | 127.6 |  | 44
LV28 | 27.5 | 11000 | 80 | 72 | 125 | 308.3 | 0.561 | 14.56 | 173 |  | 44
LV28 | 27.5 | 11000 | 85 | 72 | 125 | 308.8 | 0.716 | 18.61 | 221.1 |  | 44
LV28 | 27.5 | 11000 | 90 | 72 | 125 | 308.8 | 0.871 | 22.63 | 268.9 |  | 44
LV28 | 27.5 | 11000 | 80 | 77 | 125 | 333.2 | 0.377 | 10.58 | 125.7 |  | 44
LV28 | 27.5 | 11000 | 85 | 77 | 125 | 334.4 | 0.522 | 14.71 | 174.7 |  | 44
LV28 | 27.5 | 11000 | 90 | 77 | 125 | 334.3 | 0.658 | 18.51 | 219.9 |  | 44
LV28 | 27.5 | 12375 | 65 | 57 | 75 | 326.5 | 0.687 | 16.78 | 224.2 |  | 42
LV28 | 27.5 | 12375 | 70 | 57 | 75 | 328.2 | 0.851 | 20.91 | 279.4 |  | 42
LV28 | 27.5 | 12375 | 75 | 57 | 75 | 335.5 | 0.968 | 24.29 | 324.6 |  | 42
LV28 | 27.5 | 12375 | 80 | 57 | 75 | 355.5 | 0.967 | 25.73 | 343.9 |  | 42
LV28 | 27.5 | 12375 | 85 | 57 | 75 | 375.7 | 0.967 | 27.19 | 363.4 |  | 42
LV28 | 27.5 | 12375 | 90 | 57 | 75 | 395.7 | 0.967 | 28.64 | 382.8 |  | 42
LV28 | 27.5 | 12375 | 65 | 62 | 75 | 354.9 | 0.484 | 12.85 | 171.7 |  | 42
LV28 | 27.5 | 12375 | 70 | 62 | 75 | 357.1 | 0.638 | 17.06 | 228 |  | 42
LV28 | 27.5 | 12375 | 75 | 62 | 75 | 358.8 | 0.784 | 21.04 | 281.2 |  | 42
LV28 | 27.5 | 12375 | 80 | 62 | 75 | 360.4 | 0.929 | 25.04 | 334.7 |  | 42
LV28 | 27.5 | 12375 | 85 | 62 | 75 | 375.6 | 0.967 | 27.18 | 363.3 |  | 42
LV28 | 27.5 | 12375 | 90 | 62 | 75 | 395.8 | 0.967 | 28.64 | 382.8 |  | 42
LV28 | 27.5 | 12375 | 70 | 67 | 75 | 386.7 | 0.445 | 12.88 | 172.1 |  | 42
LV28 | 27.5 | 12375 | 75 | 67 | 75 | 388.8 | 0.581 | 16.89 | 225.7 |  | 42
LV28 | 27.5 | 12375 | 80 | 67 | 75 | 390.2 | 0.726 | 21.18 | 283.1 |  | 42
LV28 | 27.5 | 12375 | 85 | 67 | 75 | 391 | 0.861 | 25.19 | 336.6 |  | 42
LV28 | 27.5 | 12375 | 90 | 67 | 75 | 395.9 | 0.967 | 28.66 | 383 |  | 42
LV28 | 27.5 | 12375 | 75 | 72 | 75 | 420.1 | 0.406 | 12.77 | 170.7 |  | 42
LV28 | 27.5 | 12375 | 80 | 72 | 75 | 421.9 | 0.532 | 16.8 | 224.5 |  | 42
LV28 | 27.5 | 12375 | 85 | 72 | 75 | 423.1 | 0.658 | 20.82 | 278.3 |  | 42
LV28 | 27.5 | 12375 | 90 | 72 | 75 | 424 | 0.793 | 25.16 | 336.3 |  | 42
LV28 | 27.5 | 12375 | 80 | 77 | 75 | 455 | 0.367 | 12.51 | 167.2 |  | 42
LV28 | 27.5 | 12375 | 85 | 77 | 75 | 456.1 | 0.493 | 16.84 | 225 |  | 42
LV28 | 27.5 | 12375 | 90 | 77 | 75 | 457.1 | 0.609 | 20.85 | 278.6 |  | 42
LV28 | 27.5 | 12375 | 65 | 57 | 85 | 310.2 | 0.697 | 16.17 | 216.1 |  | 42
LV28 | 27.5 | 12375 | 70 | 57 | 85 | 311.8 | 0.871 | 20.31 | 271.5 |  | 42
LV28 | 27.5 | 12375 | 75 | 57 | 85 | 321.3 | 0.967 | 23.25 | 310.8 |  | 42
LV28 | 27.5 | 12375 | 80 | 57 | 85 | 341 | 0.967 | 24.68 | 329.9 |  | 42
LV28 | 27.5 | 12375 | 85 | 57 | 85 | 360.8 | 0.967 | 26.11 | 349 |  | 42
LV28 | 27.5 | 12375 | 90 | 57 | 85 | 380.3 | 0.967 | 27.53 | 367.9 |  | 42
LV28 | 27.5 | 12375 | 65 | 62 | 85 | 337.5 | 0.484 | 12.21 | 163.2 |  | 42
LV28 | 27.5 | 12375 | 70 | 62 | 85 | 339.9 | 0.638 | 16.24 | 217 |  | 42
LV28 | 27.5 | 12375 | 75 | 62 | 85 | 341.7 | 0.803 | 20.52 | 274.3 |  | 42
LV28 | 27.5 | 12375 | 80 | 62 | 85 | 343.2 | 0.948 | 24.34 | 325.3 |  | 42
LV28 | 27.5 | 12375 | 85 | 62 | 85 | 360.9 | 0.967 | 26.12 | 349.1 |  | 42
LV28 | 27.5 | 12375 | 90 | 62 | 85 | 380.3 | 0.967 | 27.53 | 367.9 |  | 42
LV28 | 27.5 | 12375 | 70 | 67 | 85 | 368.1 | 0.445 | 12.26 | 163.8 |  | 42
LV28 | 27.5 | 12375 | 75 | 67 | 85 | 370.2 | 0.59 | 16.34 | 218.4 |  | 42
LV28 | 27.5 | 12375 | 80 | 67 | 85 | 371.6 | 0.735 | 20.44 | 273.2 |  | 42
LV28 | 27.5 | 12375 | 85 | 67 | 85 | 373.1 | 0.88 | 24.57 | 328.4 |  | 42
LV28 | 27.5 | 12375 | 90 | 67 | 85 | 380.5 | 0.967 | 27.54 | 368.1 |  | 42
LV28 | 27.5 | 12375 | 75 | 72 | 85 | 400.5 | 0.406 | 12.17 | 162.7 |  | 42
LV28 | 27.5 | 12375 | 80 | 72 | 85 | 402.5 | 0.542 | 16.31 | 218 |  | 42
LV28 | 27.5 | 12375 | 85 | 72 | 85 | 403.4 | 0.677 | 20.44 | 273.2 |  | 42
LV28 | 27.5 | 12375 | 90 | 72 | 85 | 404.3 | 0.813 | 24.59 | 328.6 |  | 42
LV28 | 27.5 | 12375 | 80 | 77 | 85 | 433.8 | 0.368 | 11.93 | 159.5 |  | 42
LV28 | 27.5 | 12375 | 85 | 77 | 85 | 435.6 | 0.493 | 16.08 | 214.9 |  | 42
LV28 | 27.5 | 12375 | 90 | 77 | 85 | 436 | 0.619 | 20.19 | 269.9 |  | 42
LV28 | 27.5 | 12375 | 65 | 57 | 95 | 293.1 | 0.716 | 15.7 | 209.8 |  | 43
LV28 | 27.5 | 12375 | 70 | 57 | 95 | 295 | 0.89 | 19.64 | 262.5 |  | 43
LV28 | 27.5 | 12375 | 75 | 57 | 95 | 306.3 | 0.967 | 22.17 | 296.3 |  | 43
LV28 | 27.5 | 12375 | 80 | 57 | 95 | 325.4 | 0.967 | 23.55 | 314.8 |  | 43
LV28 | 27.5 | 12375 | 85 | 57 | 95 | 344.7 | 0.968 | 24.95 | 333.5 |  | 43
LV28 | 27.5 | 12375 | 90 | 57 | 95 | 363.9 | 0.967 | 26.34 | 352 |  | 43
LV28 | 27.5 | 12375 | 65 | 62 | 95 | 319.3 | 0.484 | 11.55 | 154.4 |  | 43
LV28 | 27.5 | 12375 | 70 | 62 | 95 | 321.6 | 0.648 | 15.59 | 208.4 |  | 43
LV28 | 27.5 | 12375 | 75 | 62 | 95 | 323.6 | 0.812 | 19.67 | 262.9 |  | 43
LV28 | 27.5 | 12375 | 80 | 62 | 95 | 325.6 | 0.967 | 23.57 | 315 |  | 43
LV28 | 27.5 | 12375 | 85 | 62 | 95 | 344.8 | 0.967 | 24.95 | 333.5 |  | 43
LV28 | 27.5 | 12375 | 90 | 62 | 95 | 364 | 0.967 | 26.34 | 352.1 |  | 43
LV28 | 27.5 | 12375 | 70 | 67 | 95 | 348.7 | 0.445 | 11.61 | 155.2 |  | 43
LV28 | 27.5 | 12375 | 75 | 67 | 95 | 350.7 | 0.6 | 15.74 | 210.4 |  | 43
LV28 | 27.5 | 12375 | 80 | 67 | 95 | 351.9 | 0.755 | 19.87 | 265.6 |  | 43
LV28 | 27.5 | 12375 | 85 | 67 | 95 | 353.5 | 0.9 | 23.79 | 318 |  | 43
LV28 | 27.5 | 12375 | 90 | 67 | 95 | 364 | 0.968 | 26.35 | 352.2 |  | 43
LV28 | 27.5 | 12375 | 75 | 72 | 95 | 379.5 | 0.406 | 11.54 | 154.2 |  | 43
LV28 | 27.5 | 12375 | 80 | 72 | 95 | 381.5 | 0.552 | 15.74 | 210.4 |  | 43
LV28 | 27.5 | 12375 | 85 | 72 | 95 | 382.8 | 0.687 | 19.67 | 262.9 |  | 43
LV28 | 27.5 | 12375 | 90 | 72 | 95 | 383.4 | 0.832 | 23.87 | 319 |  | 43
LV28 | 27.5 | 12375 | 80 | 77 | 95 | 411.6 | 0.377 | 11.62 | 155.3 |  | 43
LV28 | 27.5 | 12375 | 85 | 77 | 95 | 413.3 | 0.503 | 15.56 | 207.9 |  | 43
LV28 | 27.5 | 12375 | 90 | 77 | 95 | 414 | 0.638 | 19.78 | 264.3 |  | 43
LV28 | 27.5 | 12375 | 65 | 57 | 105 | 275.3 | 0.725 | 14.94 | 199.7 |  | 43
LV28 | 27.5 | 12375 | 70 | 57 | 105 | 277 | 0.909 | 18.85 | 251.9 |  | 43
LV28 | 27.5 | 12375 | 75 | 57 | 105 | 290.5 | 0.967 | 21.03 | 281 |  | 43
LV28 | 27.5 | 12375 | 80 | 57 | 105 | 309.1 | 0.967 | 22.37 | 299 |  | 43
LV28 | 27.5 | 12375 | 85 | 57 | 105 | 327.7 | 0.967 | 23.72 | 317 |  | 43
LV28 | 27.5 | 12375 | 90 | 57 | 105 | 346.3 | 0.967 | 25.07 | 335 |  | 43
LV28 | 27.5 | 12375 | 65 | 62 | 105 | 300.3 | 0.493 | 11.08 | 148.1 |  | 43
LV28 | 27.5 | 12375 | 70 | 62 | 105 | 302.7 | 0.668 | 15.12 | 202.1 |  | 43
LV28 | 27.5 | 12375 | 75 | 62 | 105 | 304.2 | 0.832 | 18.94 | 253.1 |  | 43
LV28 | 27.5 | 12375 | 80 | 62 | 105 | 309.2 | 0.967 | 22.38 | 299.1 |  | 43
LV28 | 27.5 | 12375 | 85 | 62 | 105 | 327.7 | 0.968 | 23.73 | 317.1 |  | 43
LV28 | 27.5 | 12375 | 90 | 62 | 105 | 346.3 | 0.967 | 25.07 | 335 |  | 43
LV28 | 27.5 | 12375 | 70 | 67 | 105 | 328.2 | 0.445 | 10.92 | 146 |  | 43
LV28 | 27.5 | 12375 | 75 | 67 | 105 | 330.1 | 0.61 | 15.05 | 201.2 |  | 43
LV28 | 27.5 | 12375 | 80 | 67 | 105 | 331.5 | 0.764 | 18.96 | 253.4 |  | 43
LV28 | 27.5 | 12375 | 85 | 67 | 105 | 332.6 | 0.929 | 23.11 | 308.9 |  | 43
LV28 | 27.5 | 12375 | 90 | 67 | 105 | 346.5 | 0.967 | 25.08 | 335.2 |  | 43
LV28 | 27.5 | 12375 | 75 | 72 | 105 | 357.6 | 0.416 | 11.13 | 148.7 |  | 43
LV28 | 27.5 | 12375 | 80 | 72 | 105 | 359.4 | 0.561 | 15.08 | 201.6 |  | 43
LV28 | 27.5 | 12375 | 85 | 72 | 105 | 360.3 | 0.706 | 19.04 | 254.5 |  | 43
LV28 | 27.5 | 12375 | 90 | 72 | 105 | 361.3 | 0.851 | 23.02 | 307.6 |  | 43
LV28 | 27.5 | 12375 | 80 | 77 | 105 | 388.1 | 0.377 | 10.95 | 146.4 |  | 43
LV28 | 27.5 | 12375 | 85 | 77 | 105 | 389.7 | 0.513 | 14.95 | 199.8 |  | 43
LV28 | 27.5 | 12375 | 90 | 77 | 105 | 390.3 | 0.648 | 18.93 | 253 |  | 43
LV28 | 27.5 | 12375 | 65 | 57 | 115 | 256.9 | 0.735 | 14.13 | 188.9 |  | 44
LV28 | 27.5 | 12375 | 70 | 57 | 115 | 258.6 | 0.938 | 18.15 | 242.6 |  | 44
LV28 | 27.5 | 12375 | 75 | 57 | 115 | 273.9 | 0.967 | 19.82 | 264.9 |  | 44
LV28 | 27.5 | 12375 | 80 | 57 | 115 | 291.6 | 0.967 | 21.11 | 282.1 |  | 44
LV28 | 27.5 | 12375 | 85 | 57 | 115 | 309.6 | 0.967 | 22.41 | 299.5 |  | 44
LV28 | 27.5 | 12375 | 90 | 57 | 115 | 327.5 | 0.967 | 23.7 | 316.8 |  | 44
LV28 | 27.5 | 12375 | 65 | 62 | 115 | 280.4 | 0.493 | 10.35 | 138.3 |  | 44
LV28 | 27.5 | 12375 | 70 | 62 | 115 | 282.7 | 0.677 | 14.33 | 191.5 |  | 44
LV28 | 27.5 | 12375 | 75 | 62 | 115 | 284.1 | 0.861 | 18.3 | 244.6 |  | 44
LV28 | 27.5 | 12375 | 80 | 62 | 115 | 291.8 | 0.967 | 21.12 | 282.3 |  | 44
LV28 | 27.5 | 12375 | 85 | 62 | 115 | 309.7 | 0.967 | 22.42 | 299.6 |  | 44
LV28 | 27.5 | 12375 | 90 | 62 | 115 | 327.6 | 0.967 | 23.71 | 316.9 |  | 44
LV28 | 27.5 | 12375 | 70 | 67 | 115 | 306.8 | 0.455 | 10.44 | 139.5 |  | 44
LV28 | 27.5 | 12375 | 75 | 67 | 115 | 308.8 | 0.619 | 14.31 | 191.2 |  | 44
LV28 | 27.5 | 12375 | 80 | 67 | 115 | 310.2 | 0.793 | 18.41 | 246 |  | 44
LV28 | 27.5 | 12375 | 85 | 67 | 115 | 311.3 | 0.948 | 22.08 | 295.1 |  | 44
LV28 | 27.5 | 12375 | 90 | 67 | 115 | 327.6 | 0.967 | 23.71 | 316.9 |  | 44
LV28 | 27.5 | 12375 | 75 | 72 | 115 | 334.6 | 0.416 | 10.42 | 139.2 |  | 44
LV28 | 27.5 | 12375 | 80 | 72 | 115 | 336.2 | 0.571 | 14.36 | 191.9 |  | 44
LV28 | 27.5 | 12375 | 85 | 72 | 115 | 336.9 | 0.726 | 18.29 | 244.5 |  | 44
LV28 | 27.5 | 12375 | 90 | 72 | 115 | 337.6 | 0.88 | 22.24 | 297.2 |  | 44
LV28 | 27.5 | 12375 | 80 | 77 | 115 | 363.5 | 0.377 | 10.26 | 137.1 |  | 44
LV28 | 27.5 | 12375 | 85 | 77 | 115 | 364.9 | 0.522 | 14.26 | 190.6 |  | 44
LV28 | 27.5 | 12375 | 90 | 77 | 115 | 365 | 0.668 | 18.23 | 243.7 |  | 44
LV28 | 27.5 | 12375 | 65 | 57 | 125 | 237.7 | 0.755 | 13.42 | 179.4 |  | 44
LV28 | 27.5 | 12375 | 70 | 57 | 125 | 239.6 | 0.957 | 17.16 | 229.4 |  | 44
LV28 | 27.5 | 12375 | 75 | 57 | 125 | 256.4 | 0.967 | 18.56 | 248 |  | 44
LV28 | 27.5 | 12375 | 80 | 57 | 125 | 273.3 | 0.967 | 19.78 | 264.4 |  | 44
LV28 | 27.5 | 12375 | 85 | 57 | 125 | 290.4 | 0.967 | 21.02 | 280.9 |  | 44
LV28 | 27.5 | 12375 | 90 | 57 | 125 | 307.6 | 0.967 | 22.26 | 297.5 |  | 44
LV28 | 27.5 | 12375 | 65 | 62 | 125 | 259.9 | 0.503 | 9.78 | 130.7 |  | 44
LV28 | 27.5 | 12375 | 70 | 62 | 125 | 262 | 0.697 | 13.66 | 182.5 |  | 44
LV28 | 27.5 | 12375 | 75 | 62 | 125 | 263.1 | 0.89 | 17.52 | 234.2 |  | 44
LV28 | 27.5 | 12375 | 80 | 62 | 125 | 273.2 | 0.967 | 19.78 | 264.3 |  | 44
LV28 | 27.5 | 12375 | 85 | 62 | 125 | 290.4 | 0.967 | 21.02 | 280.9 |  | 44
LV28 | 27.5 | 12375 | 90 | 62 | 125 | 307.7 | 0.968 | 22.27 | 297.7 |  | 44
LV28 | 27.5 | 12375 | 70 | 67 | 125 | 284.6 | 0.455 | 9.68 | 129.4 |  | 44
LV28 | 27.5 | 12375 | 75 | 67 | 125 | 286.4 | 0.639 | 13.68 | 182.9 |  | 44
LV28 | 27.5 | 12375 | 80 | 67 | 125 | 287.4 | 0.813 | 17.48 | 233.6 |  | 44
LV28 | 27.5 | 12375 | 85 | 67 | 125 | 290.5 | 0.967 | 21.03 | 281 |  | 44
LV28 | 27.5 | 12375 | 90 | 67 | 125 | 307.5 | 0.967 | 22.26 | 297.5 |  | 44
LV28 | 27.5 | 12375 | 75 | 72 | 125 | 310.5 | 0.416 | 9.67 | 129.2 |  | 44
LV28 | 27.5 | 12375 | 80 | 72 | 125 | 311.8 | 0.581 | 13.54 | 181 |  | 44
LV28 | 27.5 | 12375 | 85 | 72 | 125 | 312.6 | 0.755 | 17.65 | 235.9 |  | 44
LV28 | 27.5 | 12375 | 90 | 72 | 125 | 312.2 | 0.919 | 21.47 | 286.9 |  | 44
LV28 | 27.5 | 12375 | 80 | 77 | 125 | 337.3 | 0.387 | 9.76 | 130.5 |  | 44
LV28 | 27.5 | 12375 | 85 | 77 | 125 | 338.5 | 0.542 | 13.72 | 183.4 |  | 44
LV28 | 27.5 | 12375 | 90 | 77 | 125 | 338.6 | 0.696 | 17.64 | 235.8 |  | 44
LV28 | 27.5 | 13750 | 65 | 57 | 75 | 332.1 | 0.706 | 15.79 | 234.5 |  | 42
LV28 | 27.5 | 13750 | 70 | 57 | 75 | 334.1 | 0.88 | 19.8 | 294.1 |  | 42
LV28 | 27.5 | 13750 | 75 | 57 | 75 | 345.7 | 0.967 | 22.52 | 334.4 |  | 42
LV28 | 27.5 | 13750 | 80 | 57 | 75 | 366.6 | 0.967 | 23.88 | 354.6 |  | 42
LV28 | 27.5 | 13750 | 85 | 57 | 75 | 387.3 | 0.967 | 25.23 | 374.7 |  | 42
LV28 | 27.5 | 13750 | 90 | 57 | 75 | 408.2 | 0.967 | 26.59 | 394.9 |  | 42
LV28 | 27.5 | 13750 | 65 | 62 | 75 | 360.5 | 0.484 | 11.74 | 174.4 |  | 42
LV28 | 27.5 | 13750 | 70 | 62 | 75 | 362.9 | 0.648 | 15.84 | 235.2 |  | 42
LV28 | 27.5 | 13750 | 75 | 62 | 75 | 364.7 | 0.813 | 19.96 | 296.4 |  | 42
LV28 | 27.5 | 13750 | 80 | 62 | 75 | 367.6 | 0.958 | 23.71 | 352.1 |  | 42
LV28 | 27.5 | 13750 | 85 | 62 | 75 | 387.4 | 0.967 | 25.24 | 374.8 |  | 42
LV28 | 27.5 | 13750 | 90 | 62 | 75 | 408.3 | 0.967 | 26.6 | 395 |  | 42
LV28 | 27.5 | 13750 | 70 | 67 | 75 | 392.9 | 0.445 | 11.77 | 174.8 |  | 42
LV28 | 27.5 | 13750 | 75 | 67 | 75 | 395 | 0.6 | 15.95 | 236.9 |  | 42
LV28 | 27.5 | 13750 | 80 | 67 | 75 | 396.5 | 0.745 | 19.89 | 295.4 |  | 42
LV28 | 27.5 | 13750 | 85 | 67 | 75 | 397.9 | 0.89 | 23.85 | 354.1 |  | 42
LV28 | 27.5 | 13750 | 90 | 67 | 75 | 408.5 | 0.967 | 26.61 | 395.1 |  | 42
LV28 | 27.5 | 13750 | 75 | 72 | 75 | 426.5 | 0.406 | 11.67 | 173.3 |  | 42
LV28 | 27.5 | 13750 | 80 | 72 | 75 | 428.5 | 0.551 | 15.91 | 236.3 |  | 42
LV28 | 27.5 | 13750 | 85 | 72 | 75 | 429.4 | 0.687 | 19.87 | 295 |  | 42
LV28 | 27.5 | 13750 | 90 | 72 | 75 | 431 | 0.822 | 23.87 | 354.4 |  | 42
LV28 | 27.5 | 13750 | 80 | 77 | 75 | 461.6 | 0.377 | 11.73 | 174.2 |  | 42
LV28 | 27.5 | 13750 | 85 | 77 | 75 | 462.2 | 0.503 | 15.66 | 232.5 |  | 42
LV28 | 27.5 | 13750 | 90 | 77 | 75 | 463.4 | 0.629 | 19.62 | 291.4 |  | 42
LV28 | 27.5 | 13750 | 65 | 57 | 85 | 315.3 | 0.716 | 15.2 | 225.7 |  | 42
LV28 | 27.5 | 13750 | 70 | 57 | 85 | 317.2 | 0.9 | 19.22 | 285.4 |  | 42
LV28 | 27.5 | 13750 | 75 | 57 | 85 | 330.9 | 0.967 | 21.56 | 320.1 |  | 42
LV28 | 27.5 | 13750 | 80 | 57 | 85 | 351.2 | 0.968 | 22.88 | 339.8 |  | 42
LV28 | 27.5 | 13750 | 85 | 57 | 85 | 371.7 | 0.967 | 24.22 | 359.6 |  | 42
LV28 | 27.5 | 13750 | 90 | 57 | 85 | 392.1 | 0.968 | 25.55 | 379.4 |  | 42
LV28 | 27.5 | 13750 | 65 | 62 | 85 | 342.6 | 0.493 | 11.38 | 169 |  | 42
LV28 | 27.5 | 13750 | 70 | 62 | 85 | 344.9 | 0.658 | 15.28 | 226.9 |  | 42
LV28 | 27.5 | 13750 | 75 | 62 | 85 | 346.9 | 0.832 | 19.43 | 288.6 |  | 42
LV28 | 27.5 | 13750 | 80 | 62 | 85 | 351.4 | 0.967 | 22.89 | 339.9 |  | 42
LV28 | 27.5 | 13750 | 85 | 62 | 85 | 371.8 | 0.967 | 24.22 | 359.6 |  | 42
LV28 | 27.5 | 13750 | 90 | 62 | 85 | 392.3 | 0.967 | 25.56 | 379.5 |  | 42
LV28 | 27.5 | 13750 | 70 | 67 | 85 | 373.8 | 0.445 | 11.2 | 166.3 |  | 42
LV28 | 27.5 | 13750 | 75 | 67 | 85 | 376.1 | 0.6 | 15.19 | 225.6 |  | 42
LV28 | 27.5 | 13750 | 80 | 67 | 85 | 377.4 | 0.764 | 19.42 | 288.4 |  | 42
LV28 | 27.5 | 13750 | 85 | 67 | 85 | 378.7 | 0.919 | 23.44 | 348.1 |  | 42
LV28 | 27.5 | 13750 | 90 | 67 | 85 | 392.3 | 0.967 | 25.56 | 379.5 |  | 42
LV28 | 27.5 | 13750 | 75 | 72 | 85 | 406.2 | 0.406 | 11.11 | 165 |  | 42
LV28 | 27.5 | 13750 | 80 | 72 | 85 | 408.2 | 0.551 | 15.16 | 225.1 |  | 42
LV28 | 27.5 | 13750 | 85 | 72 | 85 | 409.6 | 0.697 | 19.21 | 285.3 |  | 42
LV28 | 27.5 | 13750 | 90 | 72 | 85 | 410.2 | 0.842 | 23.25 | 345.3 |  | 42
LV28 | 27.5 | 13750 | 80 | 77 | 85 | 439.6 | 0.377 | 11.16 | 165.8 |  | 42
LV28 | 27.5 | 13750 | 85 | 77 | 85 | 441.2 | 0.513 | 15.23 | 226.2 |  | 42
LV28 | 27.5 | 13750 | 90 | 77 | 85 | 441.6 | 0.648 | 19.27 | 286.2 |  | 42
LV28 | 27.5 | 13750 | 65 | 57 | 95 | 297.7 | 0.735 | 14.74 | 218.9 |  | 43
LV28 | 27.5 | 13750 | 70 | 57 | 95 | 299.4 | 0.919 | 18.53 | 275.2 |  | 43
LV28 | 27.5 | 13750 | 75 | 57 | 95 | 315 | 0.968 | 20.53 | 304.8 |  | 43
LV28 | 27.5 | 13750 | 80 | 57 | 95 | 335.1 | 0.967 | 21.82 | 324.1 |  | 43
LV28 | 27.5 | 13750 | 85 | 57 | 95 | 354.8 | 0.968 | 23.12 | 343.3 |  | 43
LV28 | 27.5 | 13750 | 90 | 57 | 95 | 374.9 | 0.967 | 24.42 | 362.7 |  | 43
LV28 | 27.5 | 13750 | 65 | 62 | 95 | 323.7 | 0.493 | 10.75 | 159.7 |  | 43
LV28 | 27.5 | 13750 | 70 | 62 | 95 | 326 | 0.667 | 14.65 | 217.6 |  | 43
LV28 | 27.5 | 13750 | 75 | 62 | 95 | 327.9 | 0.851 | 18.79 | 279.1 |  | 43
LV28 | 27.5 | 13750 | 80 | 62 | 95 | 334.9 | 0.967 | 21.82 | 324 |  | 43
LV28 | 27.5 | 13750 | 85 | 62 | 95 | 355 | 0.967 | 23.12 | 343.4 |  | 43
LV28 | 27.5 | 13750 | 90 | 62 | 95 | 375 | 0.967 | 24.42 | 362.7 |  | 43
LV28 | 27.5 | 13750 | 70 | 67 | 95 | 353.8 | 0.455 | 10.84 | 160.9 |  | 43
LV28 | 27.5 | 13750 | 75 | 67 | 95 | 355.8 | 0.619 | 14.84 | 220.3 |  | 43
LV28 | 27.5 | 13750 | 80 | 67 | 95 | 357.6 | 0.774 | 18.63 | 276.7 |  | 43
LV28 | 27.5 | 13750 | 85 | 67 | 95 | 358.5 | 0.938 | 22.65 | 336.4 |  | 43
LV28 | 27.5 | 13750 | 90 | 67 | 95 | 375 | 0.967 | 24.42 | 362.7 |  | 43
LV28 | 27.5 | 13750 | 75 | 72 | 95 | 384.7 | 0.416 | 10.77 | 160 |  | 43
LV28 | 27.5 | 13750 | 80 | 72 | 95 | 386.8 | 0.561 | 14.61 | 217 |  | 43
LV28 | 27.5 | 13750 | 85 | 72 | 95 | 388 | 0.716 | 18.71 | 277.8 |  | 43
LV28 | 27.5 | 13750 | 90 | 72 | 95 | 388.7 | 0.871 | 22.79 | 338.4 |  | 43
LV28 | 27.5 | 13750 | 80 | 77 | 95 | 416.8 | 0.377 | 10.59 | 157.2 |  | 43
LV28 | 27.5 | 13750 | 85 | 77 | 95 | 418.2 | 0.522 | 14.71 | 218.5 |  | 43
LV28 | 27.5 | 13750 | 90 | 77 | 95 | 418.8 | 0.658 | 18.55 | 275.5 |  | 43
LV28 | 27.5 | 13750 | 65 | 57 | 105 | 279.4 | 0.745 | 14.01 | 208.1 |  | 43
LV28 | 27.5 | 13750 | 70 | 57 | 105 | 281.9 | 0.948 | 17.99 | 267.2 |  | 43
LV28 | 27.5 | 13750 | 75 | 57 | 105 | 298.6 | 0.967 | 19.45 | 288.8 |  | 43
LV28 | 27.5 | 13750 | 80 | 57 | 105 | 317.7 | 0.968 | 20.7 | 307.4 |  | 43
LV28 | 27.5 | 13750 | 85 | 57 | 105 | 337.1 | 0.967 | 21.96 | 326.1 |  | 43
LV28 | 27.5 | 13750 | 90 | 57 | 105 | 356.5 | 0.967 | 23.22 | 344.8 |  | 43
LV28 | 27.5 | 13750 | 65 | 62 | 105 | 304 | 0.493 | 10.1 | 150 |  | 43
LV28 | 27.5 | 13750 | 70 | 62 | 105 | 306.4 | 0.687 | 14.17 | 210.4 |  | 43
LV28 | 27.5 | 13750 | 75 | 62 | 105 | 308.5 | 0.871 | 18.09 | 268.6 |  | 43
LV28 | 27.5 | 13750 | 80 | 62 | 105 | 317.8 | 0.967 | 20.7 | 307.4 |  | 43
LV28 | 27.5 | 13750 | 85 | 62 | 105 | 336.9 | 0.967 | 21.95 | 325.9 |  | 43
LV28 | 27.5 | 13750 | 90 | 62 | 105 | 356.5 | 0.967 | 23.23 | 344.9 |  | 43
LV28 | 27.5 | 13750 | 70 | 67 | 105 | 332.9 | 0.455 | 10.2 | 151.4 |  | 43
LV28 | 27.5 | 13750 | 75 | 67 | 105 | 334.9 | 0.629 | 14.18 | 210.6 |  | 43
LV28 | 27.5 | 13750 | 80 | 67 | 105 | 336 | 0.803 | 18.17 | 269.8 |  | 43
LV28 | 27.5 | 13750 | 85 | 67 | 105 | 338 | 0.958 | 21.8 | 323.7 |  | 43
LV28 | 27.5 | 13750 | 90 | 67 | 105 | 356.6 | 0.967 | 23.23 | 345 |  | 43
LV28 | 27.5 | 13750 | 75 | 72 | 105 | 362.2 | 0.416 | 10.15 | 150.7 |  | 43
LV28 | 27.5 | 13750 | 80 | 72 | 105 | 364.2 | 0.571 | 13.99 | 207.8 |  | 43
LV28 | 27.5 | 13750 | 85 | 72 | 105 | 365.1 | 0.735 | 18.07 | 268.4 |  | 43
LV28 | 27.5 | 13750 | 90 | 72 | 105 | 365.6 | 0.9 | 22.15 | 328.9 |  | 43
LV28 | 27.5 | 13750 | 80 | 77 | 105 | 392.6 | 0.377 | 9.97 | 148.1 |  | 43
LV28 | 27.5 | 13750 | 85 | 77 | 105 | 393.8 | 0.532 | 14.11 | 209.5 |  | 43
LV28 | 27.5 | 13750 | 90 | 77 | 105 | 394.3 | 0.677 | 17.98 | 267 |  | 43
LV28 | 27.5 | 13750 | 65 | 57 | 115 | 260.4 | 0.764 | 13.4 | 199 |  | 44
LV28 | 27.5 | 13750 | 70 | 57 | 115 | 262.7 | 0.967 | 17.11 | 254.1 |  | 44
LV28 | 27.5 | 13750 | 75 | 57 | 115 | 281.1 | 0.967 | 18.31 | 271.9 |  | 44
LV28 | 27.5 | 13750 | 80 | 57 | 115 | 299.4 | 0.968 | 19.51 | 289.7 |  | 44
LV28 | 27.5 | 13750 | 85 | 57 | 115 | 318.1 | 0.967 | 20.72 | 307.7 |  | 44
LV28 | 27.5 | 13750 | 90 | 57 | 115 | 336.4 | 0.967 | 21.91 | 325.4 |  | 44
LV28 | 27.5 | 13750 | 65 | 62 | 115 | 283.6 | 0.503 | 9.61 | 142.7 |  | 44
LV28 | 27.5 | 13750 | 70 | 62 | 115 | 285.8 | 0.697 | 13.41 | 199.1 |  | 44
LV28 | 27.5 | 13750 | 75 | 62 | 115 | 287.7 | 0.9 | 17.43 | 258.9 |  | 44
LV28 | 27.5 | 13750 | 80 | 62 | 115 | 299.5 | 0.967 | 19.51 | 289.7 |  | 44
LV28 | 27.5 | 13750 | 85 | 62 | 115 | 318.1 | 0.968 | 20.73 | 307.8 |  | 44
LV28 | 27.5 | 13750 | 90 | 62 | 115 | 336.7 | 0.967 | 21.93 | 325.7 |  | 44
LV28 | 27.5 | 13750 | 70 | 67 | 115 | 310.9 | 0.454 | 9.52 | 141.3 |  | 44
LV28 | 27.5 | 13750 | 75 | 67 | 115 | 312.8 | 0.638 | 13.45 | 199.7 |  | 44
LV28 | 27.5 | 13750 | 80 | 67 | 115 | 313.7 | 0.822 | 17.37 | 258 |  | 44
LV28 | 27.5 | 13750 | 85 | 67 | 115 | 318.2 | 0.967 | 20.73 | 307.8 |  | 44
LV28 | 27.5 | 13750 | 90 | 67 | 115 | 336.9 | 0.967 | 21.95 | 325.9 |  | 44
LV28 | 27.5 | 13750 | 75 | 72 | 115 | 338.6 | 0.416 | 9.49 | 140.9 |  | 44
LV28 | 27.5 | 13750 | 80 | 72 | 115 | 340.4 | 0.59 | 13.53 | 200.9 |  | 44
LV28 | 27.5 | 13750 | 85 | 72 | 115 | 341.2 | 0.755 | 17.34 | 257.5 |  | 44
LV28 | 27.5 | 13750 | 90 | 72 | 115 | 341.2 | 0.929 | 21.34 | 316.9 |  | 44
LV28 | 27.5 | 13750 | 80 | 77 | 115 | 367.7 | 0.387 | 9.58 | 142.3 |  | 44
LV28 | 27.5 | 13750 | 85 | 77 | 115 | 368.4 | 0.542 | 13.44 | 199.6 |  | 44
LV28 | 27.5 | 13750 | 90 | 77 | 115 | 368.3 | 0.697 | 17.28 | 256.6 |  | 44
LV28 | 27.5 | 13750 | 65 | 57 | 125 | 240.6 | 0.784 | 12.7 | 188.6 |  | 44
LV28 | 27.5 | 13750 | 70 | 57 | 125 | 245.1 | 0.967 | 15.97 | 237.1 |  | 44
LV28 | 27.5 | 13750 | 75 | 57 | 125 | 262.7 | 0.967 | 17.11 | 254.1 |  | 44
LV28 | 27.5 | 13750 | 80 | 57 | 125 | 280.2 | 0.968 | 18.26 | 271.1 |  | 44
LV28 | 27.5 | 13750 | 85 | 57 | 125 | 297.9 | 0.967 | 19.41 | 288.2 |  | 44
LV28 | 27.5 | 13750 | 90 | 57 | 125 | 315.4 | 0.967 | 20.55 | 305.1 |  | 44
LV28 | 27.5 | 13750 | 65 | 62 | 125 | 262.4 | 0.503 | 8.89 | 132 |  | 44
LV28 | 27.5 | 13750 | 70 | 62 | 125 | 264.3 | 0.716 | 12.74 | 189.2 |  | 44
LV28 | 27.5 | 13750 | 75 | 62 | 125 | 265.8 | 0.929 | 16.62 | 246.8 |  | 44
LV28 | 27.5 | 13750 | 80 | 62 | 125 | 280.3 | 0.968 | 18.26 | 271.2 |  | 44
LV28 | 27.5 | 13750 | 85 | 62 | 125 | 298 | 0.967 | 19.41 | 288.2 |  | 44
LV28 | 27.5 | 13750 | 90 | 62 | 125 | 315.5 | 0.967 | 20.55 | 305.2 |  | 44
LV28 | 27.5 | 13750 | 70 | 67 | 125 | 288.3 | 0.464 | 9.02 | 133.9 |  | 44
LV28 | 27.5 | 13750 | 75 | 67 | 125 | 289.8 | 0.658 | 12.84 | 190.7 |  | 44
LV28 | 27.5 | 13750 | 80 | 67 | 125 | 290.6 | 0.851 | 16.66 | 247.4 |  | 44
LV28 | 27.5 | 13750 | 85 | 67 | 125 | 298 | 0.967 | 19.41 | 288.2 |  | 44
LV28 | 27.5 | 13750 | 90 | 67 | 125 | 315.4 | 0.967 | 20.55 | 305.1 |  | 44
LV28 | 27.5 | 13750 | 75 | 72 | 125 | 314.2 | 0.426 | 9.01 | 133.8 |  | 44
LV28 | 27.5 | 13750 | 80 | 72 | 125 | 315.7 | 0.609 | 12.96 | 192.4 |  | 44
LV28 | 27.5 | 13750 | 85 | 72 | 125 | 315.9 | 0.784 | 16.67 | 247.6 |  | 44
LV28 | 27.5 | 13750 | 90 | 72 | 125 | 316.1 | 0.958 | 20.38 | 302.7 |  | 44
LV28 | 27.5 | 13750 | 80 | 77 | 125 | 340.8 | 0.387 | 8.88 | 131.9 |  | 44
LV28 | 27.5 | 13750 | 85 | 77 | 125 | 341.4 | 0.561 | 12.9 | 191.5 |  | 44
LV28 | 27.5 | 13750 | 90 | 77 | 125 | 341.4 | 0.726 | 16.68 | 247.7 |  | 44
RV27 | 27.5 | 6875 | 65 | 57 | 75 | 268.7 | 0.635 | 22.98 | 170.6 | 20.5 | 33
RV27 | 27.5 | 6875 | 70 | 57 | 75 | 269.3 | 0.76 | 27.56 | 204.6 | 20.5 | 33
RV27 | 27.5 | 6875 | 75 | 57 | 75 | 269.4 | 0.875 | 31.76 | 235.8 | 20.5 | 33
RV27 | 27.5 | 6875 | 80 | 57 | 75 | 271.8 | 0.962 | 35.22 | 261.5 | 20.4 | 33
RV27 | 27.5 | 6875 | 85 | 57 | 75 | 286.4 | 0.962 | 37.1 | 275.5 | 20.3 | 33
RV27 | 27.5 | 6875 | 90 | 57 | 75 | 300.9 | 0.962 | 38.98 | 289.4 | 20.2 | 33
RV27 | 27.5 | 6875 | 65 | 62 | 75 | 294.4 | 0.471 | 18.68 | 138.7 | 20.5 | 33
RV27 | 27.5 | 6875 | 70 | 62 | 75 | 294.7 | 0.587 | 23.29 | 172.9 | 20.5 | 33
RV27 | 27.5 | 6875 | 75 | 62 | 75 | 295 | 0.693 | 27.52 | 204.3 | 20.4 | 33
RV27 | 27.5 | 6875 | 80 | 62 | 75 | 294.9 | 0.798 | 31.7 | 235.4 | 20.4 | 33
RV27 | 27.5 | 6875 | 85 | 62 | 75 | 295.2 | 0.914 | 36.32 | 269.7 | 20.3 | 33
RV27 | 27.5 | 6875 | 90 | 62 | 75 | 301.1 | 0.962 | 39 | 289.6 | 20.3 | 33
RV27 | 27.5 | 6875 | 70 | 67 | 75 | 322.5 | 0.433 | 18.8 | 139.6 | 20.5 | 33
RV27 | 27.5 | 6875 | 75 | 67 | 75 | 322.5 | 0.529 | 22.98 | 170.6 | 20.4 | 33
RV27 | 27.5 | 6875 | 80 | 67 | 75 | 322.6 | 0.635 | 27.58 | 204.8 | 20.3 | 33
RV27 | 27.5 | 6875 | 85 | 67 | 75 | 322.4 | 0.731 | 31.74 | 235.7 | 20.3 | 33
RV27 | 27.5 | 6875 | 90 | 67 | 75 | 322.1 | 0.837 | 36.31 | 269.6 | 20.3 | 33
RV27 | 27.5 | 6875 | 75 | 72 | 75 | 352.1 | 0.394 | 18.71 | 138.9 | 20.3 | 33
RV27 | 27.5 | 6875 | 80 | 72 | 75 | 352.3 | 0.49 | 23.27 | 172.8 | 20.3 | 33
RV27 | 27.5 | 6875 | 85 | 72 | 75 | 351.7 | 0.577 | 27.34 | 203 | 20.2 | 33
RV27 | 27.5 | 6875 | 90 | 72 | 75 | 351.5 | 0.673 | 31.88 | 236.7 | 20.2 | 33
RV27 | 27.5 | 6875 | 80 | 77 | 75 | 371.4 | 0.366 | 18.29 | 135.8 | 23.2 | 33
RV27 | 27.5 | 6875 | 85 | 77 | 75 | 382.9 | 0.442 | 22.81 | 169.4 | 20.1 | 33
RV27 | 27.5 | 6875 | 90 | 77 | 75 | 381.7 | 0.529 | 27.19 | 201.9 | 20.4 | 33
RV27 | 27.5 | 6875 | 65 | 57 | 85 | 258.5 | 0.644 | 22.44 | 166.6 | 22.8 | 33
RV27 | 27.5 | 6875 | 70 | 57 | 85 | 259.1 | 0.77 | 26.86 | 199.4 | 22.7 | 33
RV27 | 27.5 | 6875 | 75 | 57 | 85 | 259.3 | 0.885 | 30.91 | 229.5 | 22.7 | 33
RV27 | 27.5 | 6875 | 80 | 57 | 85 | 263.5 | 0.962 | 34.14 | 253.5 | 22.6 | 33
RV27 | 27.5 | 6875 | 85 | 57 | 85 | 278 | 0.962 | 36.01 | 267.4 | 22.6 | 33
RV27 | 27.5 | 6875 | 90 | 57 | 85 | 292.4 | 0.962 | 37.89 | 281.3 | 22.6 | 33
RV27 | 27.5 | 6875 | 65 | 62 | 85 | 283.2 | 0.471 | 17.98 | 133.5 | 22.8 | 33
RV27 | 27.5 | 6875 | 70 | 62 | 85 | 283.6 | 0.587 | 22.41 | 166.4 | 22.8 | 33
RV27 | 27.5 | 6875 | 75 | 62 | 85 | 284 | 0.702 | 26.86 | 199.4 | 22.7 | 33
RV27 | 27.5 | 6875 | 80 | 62 | 85 | 283.7 | 0.817 | 31.23 | 231.9 | 22.7 | 33
RV27 | 27.5 | 6875 | 85 | 62 | 85 | 284 | 0.924 | 35.33 | 262.3 | 22.6 | 33
RV27 | 27.5 | 6875 | 90 | 62 | 85 | 292.6 | 0.962 | 37.91 | 281.5 | 22.6 | 33
RV27 | 27.5 | 6875 | 70 | 67 | 85 | 310.5 | 0.433 | 18.1 | 134.4 | 22.8 | 33
RV27 | 27.5 | 6875 | 75 | 67 | 85 | 310.8 | 0.539 | 22.55 | 167.4 | 22.8 | 33
RV27 | 27.5 | 6875 | 80 | 67 | 85 | 310.9 | 0.645 | 26.99 | 200.4 | 22.7 | 33
RV27 | 27.5 | 6875 | 85 | 67 | 85 | 311 | 0.741 | 31.02 | 230.3 | 22.7 | 33
RV27 | 27.5 | 6875 | 90 | 67 | 85 | 310.9 | 0.847 | 35.45 | 263.2 | 22.6 | 33
RV27 | 27.5 | 6875 | 75 | 72 | 85 | 340 | 0.394 | 18.06 | 134.1 | 22.8 | 33
RV27 | 27.5 | 6875 | 80 | 72 | 85 | 339.9 | 0.491 | 22.46 | 166.8 | 22.7 | 33
RV27 | 27.5 | 6875 | 85 | 72 | 85 | 339.7 | 0.587 | 26.84 | 199.3 | 22.7 | 33
RV27 | 27.5 | 6875 | 90 | 72 | 85 | 339.4 | 0.683 | 31.22 | 231.8 | 22.6 | 33
RV27 | 27.5 | 6875 | 80 | 77 | 85 | 369.5 | 0.356 | 17.71 | 131.5 | 22.7 | 33
RV27 | 27.5 | 6875 | 85 | 77 | 85 | 369.4 | 0.452 | 22.49 | 167 | 22.6 | 33
RV27 | 27.5 | 6875 | 90 | 77 | 85 | 368.2 | 0.539 | 26.71 | 198.3 | 22.9 | 33
RV27 | 27.5 | 6875 | 65 | 57 | 95 | 247.4 | 0.644 | 21.47 | 159.4 | 25.1 | 34
RV27 | 27.5 | 6875 | 70 | 57 | 95 | 247.9 | 0.779 | 26.01 | 193.1 | 25.1 | 34
RV27 | 27.5 | 6875 | 75 | 57 | 95 | 248.3 | 0.904 | 30.24 | 224.5 | 25 | 34
RV27 | 27.5 | 6875 | 80 | 57 | 95 | 254.5 | 0.962 | 32.97 | 244.8 | 25 | 34
RV27 | 27.5 | 6875 | 85 | 57 | 95 | 268.7 | 0.962 | 34.81 | 258.5 | 25.1 | 34
RV27 | 27.5 | 6875 | 90 | 57 | 95 | 283.1 | 0.962 | 36.67 | 272.3 | 25.1 | 34
RV27 | 27.5 | 6875 | 65 | 62 | 95 | 271.1 | 0.471 | 17.21 | 127.8 | 25.3 | 34
RV27 | 27.5 | 6875 | 70 | 62 | 95 | 271.6 | 0.596 | 21.82 | 162 | 25.3 | 34
RV27 | 27.5 | 6875 | 75 | 62 | 95 | 272 | 0.712 | 26.07 | 193.6 | 25.2 | 34
RV27 | 27.5 | 6875 | 80 | 62 | 95 | 271.7 | 0.827 | 30.26 | 224.7 | 25.2 | 34
RV27 | 27.5 | 6875 | 85 | 62 | 95 | 272.3 | 0.943 | 34.57 | 256.7 | 25.1 | 34
RV27 | 27.5 | 6875 | 90 | 62 | 95 | 283.3 | 0.962 | 36.7 | 272.5 | 25.1 | 34
RV27 | 27.5 | 6875 | 70 | 67 | 95 | 297.5 | 0.433 | 17.35 | 128.8 | 25.4 | 34
RV27 | 27.5 | 6875 | 75 | 67 | 95 | 297.9 | 0.539 | 21.62 | 160.5 | 25.3 | 34
RV27 | 27.5 | 6875 | 80 | 67 | 95 | 298.2 | 0.654 | 26.26 | 195 | 25.3 | 34
RV27 | 27.5 | 6875 | 85 | 67 | 95 | 298.2 | 0.76 | 30.52 | 226.6 | 25.2 | 34
RV27 | 27.5 | 6875 | 90 | 67 | 95 | 298.6 | 0.866 | 34.81 | 258.5 | 25.1 | 34
RV27 | 27.5 | 6875 | 75 | 72 | 95 | 326.1 | 0.394 | 17.32 | 128.6 | 25.4 | 34
RV27 | 27.5 | 6875 | 80 | 72 | 95 | 326.1 | 0.491 | 21.55 | 160 | 25.3 | 34
RV27 | 27.5 | 6875 | 85 | 72 | 95 | 326.2 | 0.596 | 26.2 | 194.5 | 25.3 | 34
RV27 | 27.5 | 6875 | 90 | 72 | 95 | 326 | 0.692 | 30.4 | 225.7 | 25.2 | 34
RV27 | 27.5 | 6875 | 80 | 77 | 95 | 354.9 | 0.356 | 17.01 | 126.3 | 25.4 | 34
RV27 | 27.5 | 6875 | 85 | 77 | 95 | 355 | 0.452 | 21.62 | 160.5 | 25.3 | 34
RV27 | 27.5 | 6875 | 90 | 77 | 95 | 353.6 | 0.539 | 25.66 | 190.5 | 25.6 | 34
RV27 | 27.5 | 6875 | 65 | 57 | 105 | 235.7 | 0.654 | 20.77 | 154.2 | 27.7 | 34
RV27 | 27.5 | 6875 | 70 | 57 | 105 | 236.3 | 0.789 | 25.1 | 186.4 | 27.6 | 34
RV27 | 27.5 | 6875 | 75 | 57 | 105 | 236.4 | 0.923 | 29.4 | 218.3 | 27.5 | 34
RV27 | 27.5 | 6875 | 80 | 57 | 105 | 245.1 | 0.962 | 31.76 | 235.8 | 27.5 | 34
RV27 | 27.5 | 6875 | 85 | 57 | 105 | 259.1 | 0.962 | 33.56 | 249.2 | 27.6 | 34
RV27 | 27.5 | 6875 | 90 | 57 | 105 | 273.2 | 0.962 | 35.39 | 262.8 | 27.7 | 34
RV27 | 27.5 | 6875 | 65 | 62 | 105 | 258.4 | 0.471 | 16.4 | 121.8 | 27.9 | 34
RV27 | 27.5 | 6875 | 70 | 62 | 105 | 259 | 0.596 | 20.79 | 154.4 | 27.8 | 34
RV27 | 27.5 | 6875 | 75 | 62 | 105 | 259.6 | 0.721 | 25.23 | 187.3 | 27.7 | 34
RV27 | 27.5 | 6875 | 80 | 62 | 105 | 259.5 | 0.846 | 29.58 | 219.6 | 27.7 | 34
RV27 | 27.5 | 6875 | 85 | 62 | 105 | 259.5 | 0.962 | 33.62 | 249.6 | 27.6 | 34
RV27 | 27.5 | 6875 | 90 | 62 | 105 | 273.4 | 0.962 | 35.42 | 263 | 27.7 | 34
RV27 | 27.5 | 6875 | 70 | 67 | 105 | 283.8 | 0.433 | 16.55 | 122.9 | 28 | 34
RV27 | 27.5 | 6875 | 75 | 67 | 105 | 284.3 | 0.548 | 21 | 155.9 | 28 | 34
RV27 | 27.5 | 6875 | 80 | 67 | 105 | 284.7 | 0.664 | 25.45 | 189 | 27.9 | 34
RV27 | 27.5 | 6875 | 85 | 67 | 105 | 284.6 | 0.77 | 29.49 | 219 | 27.8 | 34
RV27 | 27.5 | 6875 | 90 | 67 | 105 | 285.6 | 0.885 | 34.03 | 252.7 | 27.7 | 34
RV27 | 27.5 | 6875 | 75 | 72 | 105 | 311.4 | 0.394 | 16.54 | 122.8 | 28.1 | 34
RV27 | 27.5 | 6875 | 80 | 72 | 105 | 311.7 | 0.5 | 21 | 155.9 | 28 | 34
RV27 | 27.5 | 6875 | 85 | 72 | 105 | 311.7 | 0.606 | 25.44 | 188.9 | 28 | 34
RV27 | 27.5 | 6875 | 90 | 72 | 105 | 311.6 | 0.702 | 29.47 | 218.8 | 27.9 | 34
RV27 | 27.5 | 6875 | 80 | 77 | 105 | 339.5 | 0.356 | 16.27 | 120.8 | 28.2 | 34
RV27 | 27.5 | 6875 | 85 | 77 | 105 | 339.5 | 0.452 | 20.67 | 153.5 | 28.1 | 34
RV27 | 27.5 | 6875 | 90 | 77 | 105 | 338.5 | 0.548 | 25 | 185.6 | 28.3 | 34
RV27 | 27.5 | 6875 | 65 | 57 | 115 | 222.5 | 0.664 | 19.89 | 147.7 | 30.7 | 35
RV27 | 27.5 | 6875 | 70 | 57 | 115 | 222.9 | 0.808 | 24.26 | 180.1 | 30.6 | 35
RV27 | 27.5 | 6875 | 75 | 57 | 115 | 223.2 | 0.943 | 28.34 | 210.4 | 30.3 | 35
RV27 | 27.5 | 6875 | 80 | 57 | 115 | 234.4 | 0.962 | 30.37 | 225.5 | 30.4 | 35
RV27 | 27.5 | 6875 | 85 | 57 | 115 | 248.2 | 0.962 | 32.15 | 238.7 | 30.5 | 35
RV27 | 27.5 | 6875 | 90 | 57 | 115 | 262 | 0.962 | 33.94 | 252 | 30.5 | 35
RV27 | 27.5 | 6875 | 65 | 62 | 115 | 244 | 0.471 | 15.49 | 115 | 31 | 35
RV27 | 27.5 | 6875 | 70 | 62 | 115 | 244.9 | 0.606 | 19.99 | 148.4 | 30.8 | 35
RV27 | 27.5 | 6875 | 75 | 62 | 115 | 245.4 | 0.74 | 24.47 | 181.7 | 30.7 | 35
RV27 | 27.5 | 6875 | 80 | 62 | 115 | 245.9 | 0.865 | 28.66 | 212.8 | 30.5 | 35
RV27 | 27.5 | 6875 | 85 | 62 | 115 | 248.3 | 0.962 | 32.18 | 238.9 | 30.5 | 35
RV27 | 27.5 | 6875 | 90 | 62 | 115 | 262.2 | 0.962 | 33.97 | 252.2 | 30.5 | 35
RV27 | 27.5 | 6875 | 70 | 67 | 115 | 268.6 | 0.433 | 15.66 | 116.3 | 31.1 | 35
RV27 | 27.5 | 6875 | 75 | 67 | 115 | 269.1 | 0.558 | 20.22 | 150.1 | 30.9 | 35
RV27 | 27.5 | 6875 | 80 | 67 | 115 | 269.8 | 0.673 | 24.47 | 181.7 | 30.8 | 35
RV27 | 27.5 | 6875 | 85 | 67 | 115 | 269.5 | 0.789 | 28.63 | 212.6 | 30.7 | 35
RV27 | 27.5 | 6875 | 90 | 67 | 115 | 270 | 0.904 | 32.88 | 244.1 | 30.6 | 35
RV27 | 27.5 | 6875 | 75 | 72 | 115 | 294.9 | 0.394 | 15.66 | 116.3 | 31.1 | 35
RV27 | 27.5 | 6875 | 80 | 72 | 115 | 295.2 | 0.51 | 20.27 | 150.5 | 31 | 35
RV27 | 27.5 | 6875 | 85 | 72 | 115 | 295.5 | 0.616 | 24.5 | 181.9 | 30.9 | 35
RV27 | 27.5 | 6875 | 90 | 72 | 115 | 295.4 | 0.721 | 28.7 | 213.1 | 30.9 | 35
RV27 | 27.5 | 6875 | 80 | 77 | 115 | 321.8 | 0.365 | 15.84 | 117.6 | 31.2 | 35
RV27 | 27.5 | 6875 | 85 | 77 | 115 | 322.1 | 0.462 | 20.03 | 148.7 | 31.1 | 35
RV27 | 27.5 | 6875 | 90 | 77 | 115 | 321.3 | 0.558 | 24.15 | 179.3 | 31.4 | 35
RV27 | 27.5 | 6875 | 65 | 57 | 125 | 208.6 | 0.674 | 18.92 | 140.5 | 34 | 35
RV27 | 27.5 | 6875 | 70 | 57 | 125 | 208.9 | 0.827 | 23.27 | 172.8 | 33.8 | 35
RV27 | 27.5 | 6875 | 75 | 57 | 125 | 209.7 | 0.962 | 27.16 | 201.7 | 33.5 | 35
RV27 | 27.5 | 6875 | 80 | 57 | 125 | 223.1 | 0.962 | 28.9 | 214.6 | 33.5 | 35
RV27 | 27.5 | 6875 | 85 | 57 | 125 | 236.5 | 0.962 | 30.64 | 227.5 | 33.5 | 35
RV27 | 27.5 | 6875 | 90 | 57 | 125 | 250.1 | 0.962 | 32.4 | 240.6 | 33.6 | 35
RV27 | 27.5 | 6875 | 65 | 62 | 125 | 228.9 | 0.481 | 14.83 | 110.1 | 34.3 | 35
RV27 | 27.5 | 6875 | 70 | 62 | 125 | 229.8 | 0.616 | 19.06 | 141.5 | 34 | 35
RV27 | 27.5 | 6875 | 75 | 62 | 125 | 230.5 | 0.75 | 23.29 | 172.9 | 33.8 | 35
RV27 | 27.5 | 6875 | 80 | 62 | 125 | 231.4 | 0.895 | 27.88 | 207 | 33.6 | 35
RV27 | 27.5 | 6875 | 85 | 62 | 125 | 236.7 | 0.962 | 30.67 | 227.7 | 33.5 | 35
RV27 | 27.5 | 6875 | 90 | 62 | 125 | 250.2 | 0.962 | 32.42 | 240.7 | 33.6 | 35
RV27 | 27.5 | 6875 | 70 | 67 | 125 | 252.2 | 0.433 | 14.71 | 109.2 | 34.4 | 35
RV27 | 27.5 | 6875 | 75 | 67 | 125 | 253.3 | 0.558 | 19.03 | 141.3 | 34.1 | 35
RV27 | 27.5 | 6875 | 80 | 67 | 125 | 253.8 | 0.693 | 23.68 | 175.8 | 33.9 | 35
RV27 | 27.5 | 6875 | 85 | 67 | 125 | 254 | 0.818 | 27.97 | 207.7 | 33.8 | 35
RV27 | 27.5 | 6875 | 90 | 67 | 125 | 254.4 | 0.933 | 31.97 | 237.4 | 33.6 | 35
RV27 | 27.5 | 6875 | 75 | 72 | 125 | 277.3 | 0.395 | 14.73 | 109.4 | 34.4 | 35
RV27 | 27.5 | 6875 | 80 | 72 | 125 | 278.1 | 0.51 | 19.1 | 141.8 | 34.2 | 35
RV27 | 27.5 | 6875 | 85 | 72 | 125 | 278.4 | 0.625 | 23.45 | 174.1 | 34 | 35
RV27 | 27.5 | 6875 | 90 | 72 | 125 | 278.1 | 0.741 | 27.74 | 206 | 34 | 35
RV27 | 27.5 | 6875 | 80 | 77 | 125 | 303.1 | 0.366 | 14.92 | 110.8 | 34.5 | 35
RV27 | 27.5 | 6875 | 85 | 77 | 125 | 303.6 | 0.471 | 19.27 | 143.1 | 34.3 | 35
RV27 | 27.5 | 6875 | 90 | 77 | 125 | 303.1 | 0.577 | 23.56 | 174.9 | 34.5 | 35
RV27 | 27.5 | 8250 | 65 | 57 | 75 | 280.2 | 0.654 | 20.57 | 183.3 | 20.8 | 33
RV27 | 27.5 | 8250 | 70 | 57 | 75 | 280.5 | 0.789 | 24.84 | 221.3 | 20.7 | 33
RV27 | 27.5 | 8250 | 75 | 57 | 75 | 280.8 | 0.923 | 29.1 | 259.3 | 20.6 | 33
RV27 | 27.5 | 8250 | 80 | 57 | 75 | 291.7 | 0.962 | 31.49 | 280.6 | 20.6 | 33
RV27 | 27.5 | 8250 | 85 | 57 | 75 | 307.5 | 0.962 | 33.2 | 295.8 | 20.5 | 33
RV27 | 27.5 | 8250 | 90 | 57 | 75 | 323.3 | 0.962 | 34.9 | 311 | 20.4 | 33
RV27 | 27.5 | 8250 | 65 | 62 | 75 | 306.6 | 0.471 | 16.22 | 144.5 | 20.8 | 33
RV27 | 27.5 | 8250 | 70 | 62 | 75 | 307.1 | 0.597 | 20.56 | 183.2 | 20.7 | 33
RV27 | 27.5 | 8250 | 75 | 62 | 75 | 307.4 | 0.722 | 24.89 | 221.8 | 20.6 | 33
RV27 | 27.5 | 8250 | 80 | 62 | 75 | 307.8 | 0.846 | 29.24 | 260.5 | 20.6 | 33
RV27 | 27.5 | 8250 | 85 | 62 | 75 | 307.7 | 0.962 | 33.21 | 295.9 | 20.5 | 33
RV27 | 27.5 | 8250 | 90 | 62 | 75 | 323.5 | 0.962 | 34.92 | 311.1 | 20.4 | 33
RV27 | 27.5 | 8250 | 70 | 67 | 75 | 335.7 | 0.433 | 16.31 | 145.3 | 20.7 | 33
RV27 | 27.5 | 8250 | 75 | 67 | 75 | 335.9 | 0.548 | 20.67 | 184.2 | 20.6 | 33
RV27 | 27.5 | 8250 | 80 | 67 | 75 | 336 | 0.664 | 25.03 | 223 | 20.5 | 33
RV27 | 27.5 | 8250 | 85 | 67 | 75 | 335.3 | 0.779 | 29.32 | 261.2 | 20.5 | 33
RV27 | 27.5 | 8250 | 90 | 67 | 75 | 336 | 0.895 | 33.74 | 300.6 | 20.4 | 33
RV27 | 27.5 | 8250 | 75 | 72 | 75 | 365.5 | 0.394 | 16.17 | 144.1 | 20.5 | 33
RV27 | 27.5 | 8250 | 80 | 72 | 75 | 365.5 | 0.5 | 20.52 | 182.8 | 20.4 | 33
RV27 | 27.5 | 8250 | 85 | 72 | 75 | 365.2 | 0.606 | 24.84 | 221.3 | 20.4 | 33
RV27 | 27.5 | 8250 | 90 | 72 | 75 | 365 | 0.712 | 29.16 | 259.8 | 20.3 | 33
RV27 | 27.5 | 8250 | 80 | 77 | 75 | 397.3 | 0.365 | 16.3 | 145.2 | 20.4 | 33
RV27 | 27.5 | 8250 | 85 | 77 | 75 | 397.1 | 0.462 | 20.58 | 183.4 | 20.3 | 33
RV27 | 27.5 | 8250 | 90 | 77 | 75 | 396.7 | 0.558 | 24.84 | 221.3 | 20.2 | 33
RV27 | 27.5 | 8250 | 65 | 57 | 85 | 269 | 0.664 | 20.04 | 178.6 | 23 | 33
RV27 | 27.5 | 8250 | 70 | 57 | 85 | 269.3 | 0.808 | 24.42 | 217.6 | 23 | 33
RV27 | 27.5 | 8250 | 75 | 57 | 85 | 270.1 | 0.943 | 28.57 | 254.6 | 22.9 | 33
RV27 | 27.5 | 8250 | 80 | 57 | 85 | 282.6 | 0.962 | 30.51 | 271.8 | 22.9 | 33
RV27 | 27.5 | 8250 | 85 | 57 | 85 | 298.3 | 0.962 | 32.2 | 286.9 | 22.8 | 33
RV27 | 27.5 | 8250 | 90 | 57 | 85 | 314.1 | 0.962 | 33.91 | 302.1 | 22.7 | 33
RV27 | 27.5 | 8250 | 65 | 62 | 85 | 294.2 | 0.471 | 15.57 | 138.7 | 23.1 | 33
RV27 | 27.5 | 8250 | 70 | 62 | 85 | 295.1 | 0.606 | 20.07 | 178.8 | 23.1 | 33
RV27 | 27.5 | 8250 | 75 | 62 | 85 | 295.7 | 0.741 | 24.58 | 219 | 23 | 33
RV27 | 27.5 | 8250 | 80 | 62 | 85 | 297.4 | 0.846 | 28.25 | 251.7 | 25.6 | 33
RV27 | 27.5 | 8250 | 85 | 62 | 85 | 298.5 | 0.962 | 32.22 | 287.1 | 22.8 | 33
RV27 | 27.5 | 8250 | 90 | 62 | 85 | 314.2 | 0.962 | 33.93 | 302.3 | 22.8 | 33
RV27 | 27.5 | 8250 | 70 | 67 | 85 | 322.8 | 0.433 | 15.68 | 139.7 | 23.1 | 33
RV27 | 27.5 | 8250 | 75 | 67 | 85 | 323.4 | 0.558 | 20.25 | 180.4 | 23 | 33
RV27 | 27.5 | 8250 | 80 | 67 | 85 | 323.6 | 0.673 | 24.46 | 217.9 | 22.9 | 33
RV27 | 27.5 | 8250 | 85 | 67 | 85 | 323 | 0.789 | 28.6 | 254.8 | 22.9 | 33
RV27 | 27.5 | 8250 | 90 | 67 | 85 | 323.4 | 0.904 | 32.82 | 292.4 | 22.8 | 33
RV27 | 27.5 | 8250 | 75 | 72 | 85 | 352.2 | 0.394 | 15.59 | 138.9 | 23 | 33
RV27 | 27.5 | 8250 | 80 | 72 | 85 | 352.4 | 0.51 | 20.17 | 179.7 | 23 | 33
RV27 | 27.5 | 8250 | 85 | 72 | 85 | 352.1 | 0.616 | 24.33 | 216.8 | 22.9 | 33
RV27 | 27.5 | 8250 | 90 | 72 | 85 | 351.7 | 0.721 | 28.47 | 253.7 | 22.8 | 33
RV27 | 27.5 | 8250 | 80 | 77 | 85 | 382.6 | 0.366 | 15.7 | 139.9 | 22.9 | 33
RV27 | 27.5 | 8250 | 85 | 77 | 85 | 382.5 | 0.462 | 19.82 | 176.6 | 22.8 | 33
RV27 | 27.5 | 8250 | 90 | 77 | 85 | 382.4 | 0.567 | 24.35 | 217 | 22.8 | 33
RV27 | 27.5 | 8250 | 65 | 57 | 95 | 257 | 0.674 | 19.43 | 173.1 | 25.4 | 34
RV27 | 27.5 | 8250 | 70 | 57 | 95 | 257.1 | 0.818 | 23.59 | 210.2 | 25.4 | 34
RV27 | 27.5 | 8250 | 75 | 57 | 95 | 257.9 | 0.952 | 27.56 | 245.6 | 25.3 | 34
RV27 | 27.5 | 8250 | 80 | 57 | 95 | 272.6 | 0.962 | 29.43 | 262.2 | 25.3 | 34
RV27 | 27.5 | 8250 | 85 | 57 | 95 | 288.1 | 0.962 | 31.1 | 277.1 | 25.3 | 34
RV27 | 27.5 | 8250 | 90 | 57 | 95 | 303.7 | 0.962 | 32.78 | 292.1 | 25.3 | 34
RV27 | 27.5 | 8250 | 65 | 62 | 95 | 281.4 | 0.481 | 15.19 | 135.3 | 25.6 | 34
RV27 | 27.5 | 8250 | 70 | 62 | 95 | 282.2 | 0.616 | 19.49 | 173.7 | 25.5 | 34
RV27 | 27.5 | 8250 | 75 | 62 | 95 | 282.7 | 0.75 | 23.8 | 212.1 | 25.5 | 34
RV27 | 27.5 | 8250 | 80 | 62 | 95 | 283.7 | 0.885 | 28.18 | 251.1 | 25.4 | 34
RV27 | 27.5 | 8250 | 85 | 62 | 95 | 288.3 | 0.962 | 31.12 | 277.3 | 25.3 | 34
RV27 | 27.5 | 8250 | 90 | 62 | 95 | 303.9 | 0.962 | 32.81 | 292.3 | 25.3 | 34
RV27 | 27.5 | 8250 | 70 | 67 | 95 | 308.8 | 0.433 | 15.01 | 133.7 | 25.7 | 34
RV27 | 27.5 | 8250 | 75 | 67 | 95 | 309.5 | 0.558 | 19.38 | 172.7 | 25.6 | 34
RV27 | 27.5 | 8250 | 80 | 67 | 95 | 309.8 | 0.683 | 23.75 | 211.6 | 25.5 | 34
RV27 | 27.5 | 8250 | 85 | 67 | 95 | 309.7 | 0.808 | 28.08 | 250.2 | 25.5 | 34
RV27 | 27.5 | 8250 | 90 | 67 | 95 | 310.4 | 0.923 | 32.17 | 286.6 | 25.3 | 34
RV27 | 27.5 | 8250 | 75 | 72 | 95 | 337.4 | 0.394 | 14.94 | 133.1 | 25.7 | 34
RV27 | 27.5 | 8250 | 80 | 72 | 95 | 337.7 | 0.51 | 19.32 | 172.1 | 25.6 | 34
RV27 | 27.5 | 8250 | 85 | 72 | 95 | 337.6 | 0.625 | 23.69 | 211.1 | 25.5 | 34
RV27 | 27.5 | 8250 | 90 | 72 | 95 | 337.2 | 0.741 | 28.04 | 249.8 | 25.5 | 34
RV27 | 27.5 | 8250 | 80 | 77 | 95 | 367 | 0.365 | 15.05 | 134.1 | 25.7 | 34
RV27 | 27.5 | 8250 | 85 | 77 | 95 | 367.7 | 0.471 | 19.45 | 173.3 | 25.6 | 34
RV27 | 27.5 | 8250 | 90 | 77 | 95 | 366.7 | 0.577 | 23.75 | 211.6 | 25.5 | 34
RV27 | 27.5 | 8250 | 65 | 57 | 105 | 244.4 | 0.683 | 18.73 | 166.9 | 28 | 34
RV27 | 27.5 | 8250 | 70 | 57 | 105 | 244.7 | 0.837 | 22.97 | 204.7 | 27.9 | 34
RV27 | 27.5 | 8250 | 75 | 57 | 105 | 246.9 | 0.962 | 26.66 | 237.5 | 27.8 | 34
RV27 | 27.5 | 8250 | 80 | 57 | 105 | 262.1 | 0.962 | 28.29 | 252.1 | 27.9 | 34
RV27 | 27.5 | 8250 | 85 | 57 | 105 | 277.4 | 0.962 | 29.94 | 266.8 | 27.9 | 34
RV27 | 27.5 | 8250 | 90 | 57 | 105 | 292.8 | 0.962 | 31.62 | 281.7 | 27.9 | 34
RV27 | 27.5 | 8250 | 65 | 62 | 105 | 267.7 | 0.481 | 14.46 | 128.8 | 28.3 | 34
RV27 | 27.5 | 8250 | 70 | 62 | 105 | 268.7 | 0.625 | 18.86 | 168 | 28.1 | 34
RV27 | 27.5 | 8250 | 75 | 62 | 105 | 269.2 | 0.76 | 22.96 | 204.6 | 28 | 34
RV27 | 27.5 | 8250 | 80 | 62 | 105 | 269.9 | 0.904 | 27.38 | 244 | 27.9 | 34
RV27 | 27.5 | 8250 | 85 | 62 | 105 | 277.5 | 0.962 | 29.96 | 266.9 | 27.9 | 34
RV27 | 27.5 | 8250 | 90 | 62 | 105 | 293 | 0.962 | 31.63 | 281.8 | 27.9 | 34
RV27 | 27.5 | 8250 | 70 | 67 | 105 | 294 | 0.433 | 14.29 | 127.3 | 28.3 | 34
RV27 | 27.5 | 8250 | 75 | 67 | 105 | 295 | 0.567 | 18.79 | 167.4 | 28.2 | 34
RV27 | 27.5 | 8250 | 80 | 67 | 105 | 295.4 | 0.693 | 22.96 | 204.6 | 28.2 | 34
RV27 | 27.5 | 8250 | 85 | 67 | 105 | 295.6 | 0.827 | 27.45 | 244.6 | 28.1 | 34
RV27 | 27.5 | 8250 | 90 | 67 | 105 | 295.6 | 0.952 | 31.59 | 281.5 | 27.9 | 34
RV27 | 27.5 | 8250 | 75 | 72 | 105 | 321.4 | 0.395 | 14.23 | 126.8 | 28.4 | 34
RV27 | 27.5 | 8250 | 80 | 72 | 105 | 322.1 | 0.519 | 18.78 | 167.3 | 28.3 | 34
RV27 | 27.5 | 8250 | 85 | 72 | 105 | 322.4 | 0.635 | 22.97 | 204.7 | 28.2 | 34
RV27 | 27.5 | 8250 | 90 | 72 | 105 | 321.9 | 0.76 | 27.45 | 244.6 | 28.2 | 34
RV27 | 27.5 | 8250 | 80 | 77 | 105 | 350.4 | 0.366 | 14.38 | 128.1 | 28.5 | 34
RV27 | 27.5 | 8250 | 85 | 77 | 105 | 350.8 | 0.471 | 18.55 | 165.3 | 28.4 | 34
RV27 | 27.5 | 8250 | 90 | 77 | 105 | 350.5 | 0.587 | 23.08 | 205.6 | 28.3 | 34
RV27 | 27.5 | 8250 | 65 | 57 | 115 | 230.2 | 0.692 | 17.89 | 159.4 | 31 | 35
RV27 | 27.5 | 8250 | 70 | 57 | 115 | 231 | 0.856 | 22.19 | 197.7 | 30.8 | 35
RV27 | 27.5 | 8250 | 75 | 57 | 115 | 235.5 | 0.962 | 25.42 | 226.5 | 30.7 | 35
RV27 | 27.5 | 8250 | 80 | 57 | 115 | 250.3 | 0.962 | 27.03 | 240.8 | 30.7 | 35
RV27 | 27.5 | 8250 | 85 | 57 | 115 | 265.3 | 0.962 | 28.64 | 255.2 | 30.8 | 35
RV27 | 27.5 | 8250 | 90 | 57 | 115 | 280.5 | 0.962 | 30.28 | 269.8 | 30.9 | 35
RV27 | 27.5 | 8250 | 65 | 62 | 115 | 252.4 | 0.481 | 13.63 | 121.4 | 31.4 | 35
RV27 | 27.5 | 8250 | 70 | 62 | 115 | 253.5 | 0.635 | 18.06 | 160.9 | 31.1 | 35
RV27 | 27.5 | 8250 | 75 | 62 | 115 | 253.9 | 0.779 | 22.21 | 197.9 | 31 | 35
RV27 | 27.5 | 8250 | 80 | 62 | 115 | 255.1 | 0.924 | 26.44 | 235.6 | 30.8 | 35
RV27 | 27.5 | 8250 | 85 | 62 | 115 | 265.4 | 0.962 | 28.65 | 255.3 | 30.8 | 35
RV27 | 27.5 | 8250 | 90 | 62 | 115 | 280.6 | 0.962 | 30.29 | 269.9 | 30.9 | 35
RV27 | 27.5 | 8250 | 70 | 67 | 115 | 277.7 | 0.443 | 13.79 | 122.9 | 31.4 | 35
RV27 | 27.5 | 8250 | 75 | 67 | 115 | 278.7 | 0.577 | 18.06 | 160.9 | 31.2 | 35
RV27 | 27.5 | 8250 | 80 | 67 | 115 | 282.1 | 0.712 | 22.54 | 200.8 | 31.1 | 35
RV27 | 27.5 | 8250 | 85 | 67 | 115 | 280 | 0.846 | 26.6 | 237 | 31 | 35
RV27 | 27.5 | 8250 | 90 | 67 | 115 | 280.8 | 0.962 | 30.31 | 270.1 | 30.9 | 35
RV27 | 27.5 | 8250 | 75 | 72 | 115 | 304 | 0.404 | 13.78 | 122.8 | 31.5 | 35
RV27 | 27.5 | 8250 | 80 | 72 | 115 | 304.8 | 0.529 | 18.09 | 161.2 | 31.3 | 35
RV27 | 27.5 | 8250 | 85 | 72 | 115 | 305.1 | 0.654 | 22.4 | 199.6 | 31.2 | 35
RV27 | 27.5 | 8250 | 90 | 72 | 115 | 304.9 | 0.779 | 26.67 | 237.6 | 31.1 | 35
RV27 | 27.5 | 8250 | 80 | 77 | 115 | 331.4 | 0.366 | 13.6 | 121.2 | 31.6 | 35
RV27 | 27.5 | 8250 | 85 | 77 | 115 | 332.2 | 0.481 | 17.93 | 159.8 | 31.4 | 35
RV27 | 27.5 | 8250 | 90 | 77 | 115 | 332.2 | 0.596 | 22.23 | 198.1 | 31.3 | 35
RV27 | 27.5 | 8250 | 65 | 57 | 125 | 215.3 | 0.702 | 16.97 | 151.2 | 34.3 | 35
RV27 | 27.5 | 8250 | 70 | 57 | 125 | 216.5 | 0.875 | 21.27 | 189.5 | 33.9 | 35
RV27 | 27.5 | 8250 | 75 | 57 | 125 | 223.2 | 0.962 | 24.1 | 214.7 | 33.8 | 35
RV27 | 27.5 | 8250 | 80 | 57 | 125 | 237.7 | 0.962 | 25.67 | 228.7 | 33.8 | 35
RV27 | 27.5 | 8250 | 85 | 57 | 125 | 252.4 | 0.962 | 27.25 | 242.8 | 33.9 | 35
RV27 | 27.5 | 8250 | 90 | 57 | 125 | 267.3 | 0.962 | 28.86 | 257.1 | 33.9 | 35
RV27 | 27.5 | 8250 | 65 | 62 | 125 | 236.4 | 0.481 | 12.76 | 113.7 | 34.8 | 35
RV27 | 27.5 | 8250 | 70 | 62 | 125 | 237.8 | 0.645 | 17.21 | 153.3 | 34.4 | 35
RV27 | 27.5 | 8250 | 75 | 62 | 125 | 238.5 | 0.798 | 21.37 | 190.4 | 34.2 | 35
RV27 | 27.5 | 8250 | 80 | 62 | 125 | 238.8 | 0.952 | 25.52 | 227.4 | 33.8 | 35
RV27 | 27.5 | 8250 | 85 | 62 | 125 | 252.6 | 0.962 | 27.27 | 243 | 33.9 | 35
RV27 | 27.5 | 8250 | 90 | 62 | 125 | 267.4 | 0.962 | 28.87 | 257.2 | 33.9 | 35
RV27 | 27.5 | 8250 | 70 | 67 | 125 | 260.2 | 0.442 | 12.92 | 115.1 | 34.8 | 35
RV27 | 27.5 | 8250 | 75 | 67 | 125 | 261.6 | 0.587 | 17.23 | 153.5 | 34.4 | 35
RV27 | 27.5 | 8250 | 80 | 67 | 125 | 262 | 0.731 | 21.5 | 191.6 | 34.3 | 35
RV27 | 27.5 | 8250 | 85 | 67 | 125 | 263.2 | 0.875 | 25.86 | 230.4 | 34 | 35
RV27 | 27.5 | 8250 | 90 | 67 | 125 | 267.6 | 0.962 | 28.89 | 257.4 | 33.9 | 35
RV27 | 27.5 | 8250 | 75 | 72 | 125 | 285.6 | 0.404 | 12.95 | 115.4 | 34.9 | 35
RV27 | 27.5 | 8250 | 80 | 72 | 125 | 286.5 | 0.539 | 17.32 | 154.3 | 34.5 | 35
RV27 | 27.5 | 8250 | 85 | 72 | 125 | 287 | 0.673 | 21.68 | 193.2 | 34.3 | 35
RV27 | 27.5 | 8250 | 90 | 72 | 125 | 287.2 | 0.798 | 25.74 | 229.3 | 34.2 | 35
RV27 | 27.5 | 8250 | 80 | 77 | 125 | 311.7 | 0.365 | 12.78 | 113.9 | 34.9 | 35
RV27 | 27.5 | 8250 | 85 | 77 | 125 | 312.5 | 0.491 | 17.21 | 153.3 | 34.6 | 35
RV27 | 27.5 | 8250 | 90 | 77 | 125 | 312.7 | 0.616 | 21.6 | 192.5 | 34.5 | 35
RV27 | 27.5 | 9625 | 65 | 57 | 75 | 288.9 | 0.673 | 18.71 | 194.5 | 22 | 33
RV27 | 27.5 | 9625 | 70 | 57 | 75 | 289.3 | 0.827 | 23.02 | 239.3 | 22 | 33
RV27 | 27.5 | 9625 | 75 | 57 | 75 | 291.1 | 0.962 | 26.94 | 280 | 21.9 | 33
RV27 | 27.5 | 9625 | 80 | 57 | 75 | 308.1 | 0.962 | 28.51 | 296.4 | 21.8 | 33
RV27 | 27.5 | 9625 | 85 | 57 | 75 | 325.2 | 0.962 | 30.09 | 312.8 | 21.7 | 33
RV27 | 27.5 | 9625 | 90 | 57 | 75 | 342.1 | 0.962 | 31.66 | 329.1 | 21.6 | 33
RV27 | 27.5 | 9625 | 65 | 62 | 75 | 315.9 | 0.481 | 14.61 | 151.9 | 22 | 33
RV27 | 27.5 | 9625 | 70 | 62 | 75 | 316.8 | 0.616 | 18.76 | 195 | 21.9 | 33
RV27 | 27.5 | 9625 | 75 | 62 | 75 | 317.1 | 0.76 | 23.17 | 240.9 | 21.9 | 33
RV27 | 27.5 | 9625 | 80 | 62 | 75 | 317.7 | 0.904 | 27.63 | 287.2 | 21.8 | 33
RV27 | 27.5 | 9625 | 85 | 62 | 75 | 325.3 | 0.962 | 30.1 | 312.9 | 21.7 | 33
RV27 | 27.5 | 9625 | 90 | 62 | 75 | 342.1 | 0.962 | 31.66 | 329.1 | 21.6 | 33
RV27 | 27.5 | 9625 | 70 | 67 | 75 | 345 | 0.433 | 14.37 | 149.4 | 21.9 | 33
RV27 | 27.5 | 9625 | 75 | 67 | 75 | 345.6 | 0.567 | 18.86 | 196.1 | 21.8 | 33
RV27 | 27.5 | 9625 | 80 | 67 | 75 | 345.7 | 0.693 | 23.03 | 239.4 | 21.8 | 33
RV27 | 27.5 | 9625 | 85 | 67 | 75 | 345.8 | 0.827 | 27.51 | 286 | 21.7 | 33
RV27 | 27.5 | 9625 | 90 | 67 | 75 | 346.2 | 0.943 | 31.4 | 326.4 | 21.6 | 33
RV27 | 27.5 | 9625 | 75 | 72 | 75 | 375.7 | 0.394 | 14.26 | 148.2 | 21.8 | 33
RV27 | 27.5 | 9625 | 80 | 72 | 75 | 375.7 | 0.52 | 18.78 | 195.2 | 21.7 | 33
RV27 | 27.5 | 9625 | 85 | 72 | 75 | 375.6 | 0.635 | 22.94 | 238.5 | 21.6 | 33
RV27 | 27.5 | 9625 | 90 | 72 | 75 | 374.9 | 0.76 | 27.41 | 284.9 | 21.6 | 33
RV27 | 27.5 | 9625 | 80 | 77 | 75 | 408.3 | 0.366 | 14.36 | 149.3 | 21.6 | 33
RV27 | 27.5 | 9625 | 85 | 77 | 75 | 407.9 | 0.471 | 18.5 | 192.3 | 21.5 | 33
RV27 | 27.5 | 9625 | 90 | 77 | 75 | 407.1 | 0.587 | 22.98 | 238.9 | 21.4 | 33
RV27 | 27.5 | 9625 | 65 | 57 | 85 | 276.8 | 0.683 | 18.18 | 189 | 24.3 | 33
RV27 | 27.5 | 9625 | 70 | 57 | 85 | 277.7 | 0.847 | 22.62 | 235.1 | 24.2 | 33
RV27 | 27.5 | 9625 | 75 | 57 | 85 | 281.3 | 0.962 | 26.03 | 270.6 | 24.1 | 33
RV27 | 27.5 | 9625 | 80 | 57 | 85 | 298.2 | 0.962 | 27.59 | 286.8 | 24.1 | 33
RV27 | 27.5 | 9625 | 85 | 57 | 85 | 315.1 | 0.962 | 29.16 | 303.1 | 24 | 33
RV27 | 27.5 | 9625 | 90 | 57 | 85 | 332 | 0.962 | 30.73 | 319.4 | 24 | 33
RV27 | 27.5 | 9625 | 65 | 62 | 85 | 303 | 0.481 | 14.02 | 145.7 | 24.4 | 33
RV27 | 27.5 | 9625 | 70 | 62 | 85 | 304 | 0.625 | 18.28 | 190 | 24.3 | 33
RV27 | 27.5 | 9625 | 75 | 62 | 85 | 304.3 | 0.769 | 22.52 | 234.1 | 24.3 | 33
RV27 | 27.5 | 9625 | 80 | 62 | 85 | 305 | 0.914 | 26.81 | 278.7 | 24.1 | 33
RV27 | 27.5 | 9625 | 85 | 62 | 85 | 315.3 | 0.962 | 29.18 | 303.3 | 24.1 | 33
RV27 | 27.5 | 9625 | 90 | 62 | 85 | 332.1 | 0.962 | 30.73 | 319.4 | 24 | 33
RV27 | 27.5 | 9625 | 70 | 67 | 85 | 331.2 | 0.443 | 14.1 | 146.6 | 24.4 | 33
RV27 | 27.5 | 9625 | 75 | 67 | 85 | 332 | 0.577 | 18.43 | 191.6 | 24.3 | 33
RV27 | 27.5 | 9625 | 80 | 67 | 85 | 332.4 | 0.712 | 22.76 | 236.6 | 24.2 | 33
RV27 | 27.5 | 9625 | 85 | 67 | 85 | 333 | 0.837 | 26.81 | 278.7 | 24.1 | 33
RV27 | 27.5 | 9625 | 90 | 67 | 85 | 332.8 | 0.962 | 30.79 | 320.1 | 24 | 33
RV27 | 27.5 | 9625 | 75 | 72 | 85 | 361.6 | 0.404 | 14.05 | 146.1 | 24.3 | 33
RV27 | 27.5 | 9625 | 80 | 72 | 85 | 361.9 | 0.519 | 18.09 | 188 | 24.2 | 33
RV27 | 27.5 | 9625 | 85 | 72 | 85 | 361.8 | 0.645 | 22.43 | 233.2 | 24.1 | 33
RV27 | 27.5 | 9625 | 90 | 72 | 85 | 361 | 0.77 | 26.72 | 277.8 | 24.1 | 33
RV27 | 27.5 | 9625 | 80 | 77 | 85 | 392.1 | 0.365 | 13.79 | 143.3 | 24.2 | 33
RV27 | 27.5 | 9625 | 85 | 77 | 85 | 392.5 | 0.481 | 18.16 | 188.8 | 24.1 | 33
RV27 | 27.5 | 9625 | 90 | 77 | 85 | 392.3 | 0.596 | 22.51 | 234 | 24 | 33
RV27 | 27.5 | 9625 | 65 | 57 | 95 | 264 | 0.692 | 17.59 | 182.8 | 26.7 | 34
RV27 | 27.5 | 9625 | 70 | 57 | 95 | 265.1 | 0.856 | 21.84 | 227 | 26.7 | 34
RV27 | 27.5 | 9625 | 75 | 57 | 95 | 270.6 | 0.962 | 25.04 | 260.3 | 26.6 | 34
RV27 | 27.5 | 9625 | 80 | 57 | 95 | 287.2 | 0.962 | 26.58 | 276.3 | 26.6 | 34
RV27 | 27.5 | 9625 | 85 | 57 | 95 | 303.4 | 0.962 | 28.07 | 291.8 | 26.6 | 34
RV27 | 27.5 | 9625 | 90 | 57 | 95 | 320.8 | 0.962 | 29.69 | 308.6 | 26.6 | 34
RV27 | 27.5 | 9625 | 65 | 62 | 95 | 289.1 | 0.481 | 13.37 | 139 | 26.9 | 34
RV27 | 27.5 | 9625 | 70 | 62 | 95 | 290.2 | 0.635 | 17.72 | 184.2 | 26.8 | 34
RV27 | 27.5 | 9625 | 75 | 62 | 95 | 290.5 | 0.789 | 22.04 | 229.1 | 26.8 | 34
RV27 | 27.5 | 9625 | 80 | 62 | 95 | 292 | 0.933 | 26.21 | 272.5 | 26.6 | 34
RV27 | 27.5 | 9625 | 85 | 62 | 95 | 304.2 | 0.962 | 28.15 | 292.6 | 26.6 | 34
RV27 | 27.5 | 9625 | 90 | 62 | 95 | 321 | 0.962 | 29.71 | 308.8 | 26.6 | 34
RV27 | 27.5 | 9625 | 70 | 67 | 95 | 316.3 | 0.443 | 13.47 | 140 | 27 | 34
RV27 | 27.5 | 9625 | 75 | 67 | 95 | 317.3 | 0.577 | 17.61 | 183.1 | 26.9 | 34
RV27 | 27.5 | 9625 | 80 | 67 | 95 | 317.8 | 0.722 | 22.06 | 229.3 | 26.8 | 34
RV27 | 27.5 | 9625 | 85 | 67 | 95 | 318.7 | 0.856 | 26.24 | 272.8 | 26.7 | 34
RV27 | 27.5 | 9625 | 90 | 67 | 95 | 321.2 | 0.962 | 29.72 | 308.9 | 26.6 | 34
RV27 | 27.5 | 9625 | 75 | 72 | 95 | 345.7 | 0.404 | 13.44 | 139.7 | 27 | 34
RV27 | 27.5 | 9625 | 80 | 72 | 95 | 346.2 | 0.529 | 17.62 | 183.2 | 26.9 | 34
RV27 | 27.5 | 9625 | 85 | 72 | 95 | 346.4 | 0.664 | 22.12 | 229.9 | 26.8 | 34
RV27 | 27.5 | 9625 | 90 | 72 | 95 | 346.3 | 0.789 | 26.27 | 273.1 | 26.7 | 34
RV27 | 27.5 | 9625 | 80 | 77 | 95 | 375.7 | 0.365 | 13.21 | 137.3 | 27 | 34
RV27 | 27.5 | 9625 | 85 | 77 | 95 | 376.2 | 0.49 | 17.75 | 184.5 | 26.9 | 34
RV27 | 27.5 | 9625 | 90 | 77 | 95 | 375.8 | 0.606 | 21.91 | 227.8 | 26.7 | 34
RV27 | 27.5 | 9625 | 65 | 57 | 105 | 250.6 | 0.702 | 16.93 | 176 | 29.4 | 34
RV27 | 27.5 | 9625 | 70 | 57 | 105 | 252.1 | 0.875 | 21.23 | 220.7 | 29.2 | 34
RV27 | 27.5 | 9625 | 75 | 57 | 105 | 259.4 | 0.962 | 24 | 249.5 | 29.1 | 34
RV27 | 27.5 | 9625 | 80 | 57 | 105 | 275.8 | 0.962 | 25.52 | 265.3 | 29.2 | 34
RV27 | 27.5 | 9625 | 85 | 57 | 105 | 292.3 | 0.962 | 27.05 | 281.2 | 29.2 | 34
RV27 | 27.5 | 9625 | 90 | 57 | 105 | 308.9 | 0.962 | 28.58 | 297.1 | 29.2 | 34
RV27 | 27.5 | 9625 | 65 | 62 | 105 | 274.6 | 0.481 | 12.71 | 132.1 | 29.6 | 34
RV27 | 27.5 | 9625 | 70 | 62 | 105 | 275.9 | 0.644 | 17.1 | 177.8 | 29.4 | 34
RV27 | 27.5 | 9625 | 75 | 62 | 105 | 276.4 | 0.808 | 21.49 | 223.4 | 29.3 | 34
RV27 | 27.5 | 9625 | 80 | 62 | 105 | 277.2 | 0.952 | 25.4 | 264 | 29.2 | 34
RV27 | 27.5 | 9625 | 85 | 62 | 105 | 292.5 | 0.962 | 27.06 | 281.3 | 29.2 | 34
RV27 | 27.5 | 9625 | 90 | 62 | 105 | 309.2 | 0.962 | 28.61 | 297.4 | 29.2 | 34
RV27 | 27.5 | 9625 | 70 | 67 | 105 | 300.7 | 0.443 | 12.8 | 133.1 | 29.7 | 34
RV27 | 27.5 | 9625 | 75 | 67 | 105 | 301.9 | 0.587 | 17.04 | 177.1 | 29.5 | 34
RV27 | 27.5 | 9625 | 80 | 67 | 105 | 302.3 | 0.741 | 21.54 | 223.9 | 29.5 | 34
RV27 | 27.5 | 9625 | 85 | 67 | 105 | 303.4 | 0.875 | 25.55 | 265.6 | 29.3 | 34
RV27 | 27.5 | 9625 | 90 | 67 | 105 | 309.4 | 0.962 | 28.63 | 297.6 | 29.3 | 34
RV27 | 27.5 | 9625 | 75 | 72 | 105 | 328.9 | 0.404 | 12.78 | 132.9 | 29.8 | 34
RV27 | 27.5 | 9625 | 80 | 72 | 105 | 329.9 | 0.539 | 17.09 | 177.7 | 29.6 | 34
RV27 | 27.5 | 9625 | 85 | 72 | 105 | 329.9 | 0.673 | 21.37 | 222.1 | 29.5 | 34
RV27 | 27.5 | 9625 | 90 | 72 | 105 | 330.7 | 0.808 | 25.7 | 267.2 | 29.4 | 34
RV27 | 27.5 | 9625 | 80 | 77 | 105 | 358.2 | 0.365 | 12.59 | 130.9 | 29.8 | 34
RV27 | 27.5 | 9625 | 85 | 77 | 105 | 358.9 | 0.491 | 16.94 | 176.1 | 29.7 | 34
RV27 | 27.5 | 9625 | 90 | 77 | 105 | 359 | 0.616 | 21.26 | 221 | 29.5 | 34
RV27 | 27.5 | 9625 | 65 | 57 | 115 | 235.8 | 0.721 | 16.36 | 170.1 | 32.4 | 35
RV27 | 27.5 | 9625 | 70 | 57 | 115 | 236.8 | 0.904 | 20.6 | 214.1 | 32.1 | 35
RV27 | 27.5 | 9625 | 75 | 57 | 115 | 247 | 0.962 | 22.86 | 237.6 | 32 | 35
RV27 | 27.5 | 9625 | 80 | 57 | 115 | 262.9 | 0.962 | 24.33 | 252.9 | 32.1 | 35
RV27 | 27.5 | 9625 | 85 | 57 | 115 | 279.1 | 0.962 | 25.83 | 268.5 | 32.2 | 35
RV27 | 27.5 | 9625 | 90 | 57 | 115 | 295.3 | 0.962 | 27.33 | 284.1 | 32.2 | 35
RV27 | 27.5 | 9625 | 65 | 62 | 115 | 258.3 | 0.491 | 12.19 | 126.7 | 32.8 | 35
RV27 | 27.5 | 9625 | 70 | 62 | 115 | 259.8 | 0.654 | 16.34 | 169.9 | 32.5 | 35
RV27 | 27.5 | 9625 | 75 | 62 | 115 | 260.9 | 0.828 | 20.77 | 215.9 | 32.2 | 35
RV27 | 27.5 | 9625 | 80 | 62 | 115 | 263.1 | 0.962 | 24.35 | 253.1 | 32.1 | 35
RV27 | 27.5 | 9625 | 85 | 62 | 115 | 279.3 | 0.962 | 25.84 | 268.6 | 32.2 | 35
RV27 | 27.5 | 9625 | 90 | 62 | 115 | 295.8 | 0.962 | 27.37 | 284.5 | 32.2 | 35
RV27 | 27.5 | 9625 | 70 | 67 | 115 | 283.3 | 0.442 | 12.05 | 125.3 | 32.8 | 35
RV27 | 27.5 | 9625 | 75 | 67 | 115 | 284.9 | 0.596 | 16.34 | 169.9 | 32.5 | 35
RV27 | 27.5 | 9625 | 80 | 67 | 115 | 285.2 | 0.76 | 20.85 | 216.7 | 32.4 | 35
RV27 | 27.5 | 9625 | 85 | 67 | 115 | 286.2 | 0.904 | 24.9 | 258.8 | 32.3 | 35
RV27 | 27.5 | 9625 | 90 | 67 | 115 | 296 | 0.962 | 27.39 | 284.7 | 32.2 | 35
RV27 | 27.5 | 9625 | 75 | 72 | 115 | 310.4 | 0.404 | 12.06 | 125.4 | 32.8 | 35
RV27 | 27.5 | 9625 | 80 | 72 | 115 | 311.6 | 0.548 | 16.43 | 170.8 | 32.6 | 35
RV27 | 27.5 | 9625 | 85 | 72 | 115 | 311.9 | 0.693 | 20.78 | 216 | 32.5 | 35
RV27 | 27.5 | 9625 | 90 | 72 | 115 | 313.1 | 0.827 | 24.92 | 259 | 32.4 | 35
RV27 | 27.5 | 9625 | 80 | 77 | 115 | 338.3 | 0.375 | 12.21 | 126.9 | 32.9 | 35
RV27 | 27.5 | 9625 | 85 | 77 | 115 | 339.3 | 0.5 | 16.33 | 169.7 | 32.7 | 35
RV27 | 27.5 | 9625 | 90 | 77 | 115 | 339.7 | 0.635 | 20.75 | 215.7 | 32.6 | 35
RV27 | 27.5 | 9625 | 65 | 57 | 125 | 220.2 | 0.731 | 15.49 | 161 | 35.7 | 35
RV27 | 27.5 | 9625 | 70 | 57 | 125 | 221.5 | 0.933 | 19.87 | 206.6 | 35.1 | 35
RV27 | 27.5 | 9625 | 75 | 57 | 125 | 233.6 | 0.962 | 21.62 | 224.7 | 35.2 | 35
RV27 | 27.5 | 9625 | 80 | 57 | 125 | 249.4 | 0.962 | 23.08 | 239.9 | 35.2 | 35
RV27 | 27.5 | 9625 | 85 | 57 | 125 | 265.1 | 0.962 | 24.53 | 255 | 35.2 | 35
RV27 | 27.5 | 9625 | 90 | 57 | 125 | 281 | 0.962 | 26 | 270.3 | 35.3 | 35
RV27 | 27.5 | 9625 | 70 | 62 | 125 | 242.9 | 0.673 | 15.73 | 163.5 | 35.7 | 35
RV27 | 27.5 | 9625 | 75 | 62 | 125 | 244.5 | 0.847 | 19.91 | 207 | 35.4 | 35
RV27 | 27.5 | 9625 | 80 | 62 | 125 | 249.5 | 0.962 | 23.09 | 240 | 35.2 | 35
RV27 | 27.5 | 9625 | 85 | 62 | 125 | 265.3 | 0.962 | 24.55 | 255.2 | 35.2 | 35
RV27 | 27.5 | 9625 | 90 | 62 | 125 | 281.5 | 0.962 | 26.05 | 270.8 | 35.3 | 35
RV27 | 27.5 | 9625 | 70 | 67 | 125 | 265.2 | 0.452 | 11.53 | 119.9 | 36.2 | 35
RV27 | 27.5 | 9625 | 75 | 67 | 125 | 266.9 | 0.616 | 15.81 | 164.3 | 35.8 | 35
RV27 | 27.5 | 9625 | 80 | 67 | 125 | 267.7 | 0.779 | 20.07 | 208.6 | 35.5 | 35
RV27 | 27.5 | 9625 | 85 | 67 | 125 | 269 | 0.933 | 24.15 | 251 | 35.3 | 35
RV27 | 27.5 | 9625 | 90 | 67 | 125 | 281.6 | 0.962 | 26.06 | 270.9 | 35.3 | 35
RV27 | 27.5 | 9625 | 75 | 72 | 125 | 291 | 0.413 | 11.57 | 120.3 | 36.3 | 35
RV27 | 27.5 | 9625 | 80 | 72 | 125 | 292.4 | 0.558 | 15.69 | 163.1 | 35.9 | 35
RV27 | 27.5 | 9625 | 85 | 72 | 125 | 292.6 | 0.712 | 20.04 | 208.3 | 35.7 | 35
RV27 | 27.5 | 9625 | 90 | 72 | 125 | 294.3 | 0.856 | 24.23 | 251.9 | 35.5 | 35
RV27 | 27.5 | 9625 | 80 | 77 | 125 | 317.5 | 0.375 | 11.46 | 119.1 | 36.3 | 35
RV27 | 27.5 | 9625 | 85 | 77 | 125 | 318.6 | 0.51 | 15.62 | 162.4 | 35.9 | 35
RV27 | 27.5 | 9625 | 90 | 77 | 125 | 319.3 | 0.654 | 20.1 | 208.9 | 35.8 | 35
RV27 | 27.5 | 11000 | 65 | 57 | 75 | 295.9 | 0.702 | 17.48 | 207.7 | 22.9 | 33
RV27 | 27.5 | 11000 | 70 | 57 | 75 | 297.1 | 0.866 | 21.65 | 257.2 | 22.8 | 33
RV27 | 27.5 | 11000 | 75 | 57 | 75 | 303.7 | 0.962 | 24.6 | 292.2 | 22.7 | 33
RV27 | 27.5 | 11000 | 80 | 57 | 75 | 321.7 | 0.962 | 26.04 | 309.4 | 22.6 | 33
RV27 | 27.5 | 11000 | 85 | 57 | 75 | 339.7 | 0.962 | 27.51 | 326.8 | 22.5 | 33
RV27 | 27.5 | 11000 | 90 | 57 | 75 | 357.9 | 0.962 | 28.98 | 344.3 | 22.3 | 33
RV27 | 27.5 | 11000 | 65 | 62 | 75 | 322.5 | 0.481 | 13.06 | 155.1 | 22.9 | 33
RV27 | 27.5 | 11000 | 70 | 62 | 75 | 323.6 | 0.635 | 17.29 | 205.4 | 22.8 | 33
RV27 | 27.5 | 11000 | 75 | 62 | 75 | 323.7 | 0.799 | 21.76 | 258.5 | 22.7 | 33
RV27 | 27.5 | 11000 | 80 | 62 | 75 | 325.5 | 0.943 | 25.82 | 306.8 | 22.6 | 33
RV27 | 27.5 | 11000 | 85 | 62 | 75 | 339.9 | 0.962 | 27.52 | 326.9 | 22.5 | 33
RV27 | 27.5 | 11000 | 90 | 62 | 75 | 358.1 | 0.962 | 28.99 | 344.4 | 22.3 | 33
RV27 | 27.5 | 11000 | 70 | 67 | 75 | 352.5 | 0.443 | 13.13 | 156 | 22.8 | 33
RV27 | 27.5 | 11000 | 75 | 67 | 75 | 353.2 | 0.587 | 17.44 | 207.2 | 22.7 | 33
RV27 | 27.5 | 11000 | 80 | 67 | 75 | 353.3 | 0.731 | 21.74 | 258.3 | 22.6 | 33
RV27 | 27.5 | 11000 | 85 | 67 | 75 | 353.8 | 0.866 | 25.78 | 306.3 | 22.5 | 33
RV27 | 27.5 | 11000 | 90 | 67 | 75 | 358.2 | 0.962 | 29.01 | 344.6 | 22.4 | 33
RV27 | 27.5 | 11000 | 75 | 72 | 75 | 383.4 | 0.404 | 13.04 | 154.9 | 22.6 | 33
RV27 | 27.5 | 11000 | 80 | 72 | 75 | 383.6 | 0.539 | 17.4 | 206.7 | 22.5 | 33
RV27 | 27.5 | 11000 | 85 | 72 | 75 | 383.7 | 0.664 | 21.43 | 254.6 | 22.4 | 33
RV27 | 27.5 | 11000 | 90 | 72 | 75 | 383.7 | 0.798 | 25.78 | 306.3 | 22.4 | 33
RV27 | 27.5 | 11000 | 80 | 77 | 75 | 415.3 | 0.366 | 12.78 | 151.8 | 22.4 | 33
RV27 | 27.5 | 11000 | 85 | 77 | 75 | 416 | 0.491 | 17.18 | 204.1 | 22.3 | 33
RV27 | 27.5 | 11000 | 90 | 77 | 75 | 416.2 | 0.616 | 21.57 | 256.2 | 22.3 | 33
RV27 | 27.5 | 11000 | 65 | 57 | 85 | 283.5 | 0.712 | 16.99 | 201.8 | 25.2 | 34
RV27 | 27.5 | 11000 | 70 | 57 | 85 | 284.9 | 0.885 | 21.22 | 252.1 | 25.1 | 34
RV27 | 27.5 | 11000 | 75 | 57 | 85 | 293.3 | 0.962 | 23.75 | 282.1 | 25 | 34
RV27 | 27.5 | 11000 | 80 | 57 | 85 | 311.3 | 0.962 | 25.2 | 299.4 | 24.9 | 34
RV27 | 27.5 | 11000 | 85 | 57 | 85 | 329.2 | 0.962 | 26.66 | 316.7 | 24.9 | 34
RV27 | 27.5 | 11000 | 90 | 57 | 85 | 346.9 | 0.962 | 28.09 | 333.7 | 24.8 | 34
RV27 | 27.5 | 11000 | 65 | 62 | 85 | 309.1 | 0.481 | 12.52 | 148.7 | 25.3 | 34
RV27 | 27.5 | 11000 | 70 | 62 | 85 | 310.1 | 0.645 | 16.83 | 199.9 | 25.2 | 34
RV27 | 27.5 | 11000 | 75 | 62 | 85 | 310.9 | 0.808 | 21.14 | 251.2 | 25.1 | 34
RV27 | 27.5 | 11000 | 80 | 62 | 85 | 312.3 | 0.952 | 25.03 | 297.4 | 25 | 34
RV27 | 27.5 | 11000 | 85 | 62 | 85 | 329.3 | 0.962 | 26.67 | 316.8 | 24.9 | 34
RV27 | 27.5 | 11000 | 90 | 62 | 85 | 347.1 | 0.962 | 28.11 | 333.9 | 24.8 | 34
RV27 | 27.5 | 11000 | 70 | 67 | 85 | 338.3 | 0.443 | 12.6 | 149.7 | 25.2 | 34
RV27 | 27.5 | 11000 | 75 | 67 | 85 | 339.3 | 0.597 | 17.04 | 202.4 | 25.1 | 34
RV27 | 27.5 | 11000 | 80 | 67 | 85 | 339.3 | 0.741 | 21.15 | 251.3 | 25.1 | 34
RV27 | 27.5 | 11000 | 85 | 67 | 85 | 339.9 | 0.885 | 25.32 | 300.8 | 24.9 | 34
RV27 | 27.5 | 11000 | 90 | 67 | 85 | 347.2 | 0.962 | 28.11 | 334 | 24.8 | 34
RV27 | 27.5 | 11000 | 75 | 72 | 85 | 368.6 | 0.404 | 12.53 | 148.9 | 25.2 | 34
RV27 | 27.5 | 11000 | 80 | 72 | 85 | 369.2 | 0.539 | 16.74 | 198.9 | 25 | 34
RV27 | 27.5 | 11000 | 85 | 72 | 85 | 369.2 | 0.683 | 21.23 | 252.2 | 25 | 34
RV27 | 27.5 | 11000 | 90 | 72 | 85 | 369.1 | 0.818 | 25.4 | 301.8 | 24.8 | 34
RV27 | 27.5 | 11000 | 80 | 77 | 85 | 399.3 | 0.375 | 12.61 | 149.8 | 25 | 34
RV27 | 27.5 | 11000 | 85 | 77 | 85 | 399.9 | 0.5 | 16.84 | 200 | 24.9 | 34
RV27 | 27.5 | 11000 | 90 | 77 | 85 | 400.3 | 0.625 | 21.07 | 250.3 | 24.8 | 34
RV27 | 27.5 | 11000 | 65 | 57 | 95 | 270 | 0.721 | 16.4 | 194.8 | 27.6 | 34
RV27 | 27.5 | 11000 | 70 | 57 | 95 | 271.1 | 0.904 | 20.63 | 245.1 | 27.5 | 34
RV27 | 27.5 | 11000 | 75 | 57 | 95 | 282 | 0.962 | 22.84 | 271.3 | 27.5 | 34
RV27 | 27.5 | 11000 | 80 | 57 | 95 | 299.7 | 0.962 | 24.26 | 288.2 | 27.5 | 34
RV27 | 27.5 | 11000 | 85 | 57 | 95 | 317.4 | 0.962 | 25.7 | 305.3 | 27.5 | 34
RV27 | 27.5 | 11000 | 90 | 57 | 95 | 335 | 0.962 | 27.12 | 322.2 | 27.4 | 34
RV27 | 27.5 | 11000 | 65 | 62 | 95 | 294.4 | 0.49 | 12.15 | 144.4 | 27.8 | 34
RV27 | 27.5 | 11000 | 70 | 62 | 95 | 296 | 0.654 | 16.3 | 193.6 | 27.7 | 34
RV27 | 27.5 | 11000 | 75 | 62 | 95 | 297 | 0.827 | 20.68 | 245.7 | 27.6 | 34
RV27 | 27.5 | 11000 | 80 | 62 | 95 | 299.8 | 0.962 | 24.28 | 288.4 | 27.5 | 34
RV27 | 27.5 | 11000 | 85 | 62 | 95 | 317.5 | 0.962 | 25.71 | 305.4 | 27.5 | 34
RV27 | 27.5 | 11000 | 90 | 62 | 95 | 335.2 | 0.962 | 27.14 | 322.4 | 27.4 | 34
RV27 | 27.5 | 11000 | 70 | 67 | 95 | 322.6 | 0.442 | 12.01 | 142.7 | 27.9 | 34
RV27 | 27.5 | 11000 | 75 | 67 | 95 | 324 | 0.606 | 16.52 | 196.3 | 27.8 | 34
RV27 | 27.5 | 11000 | 80 | 67 | 95 | 324.2 | 0.76 | 20.73 | 246.3 | 27.7 | 34
RV27 | 27.5 | 11000 | 85 | 67 | 95 | 325.1 | 0.904 | 24.75 | 294 | 27.5 | 34
RV27 | 27.5 | 11000 | 90 | 67 | 95 | 335.3 | 0.962 | 27.15 | 322.5 | 27.4 | 34
RV27 | 27.5 | 11000 | 75 | 72 | 95 | 352.1 | 0.404 | 11.98 | 142.3 | 27.9 | 34
RV27 | 27.5 | 11000 | 80 | 72 | 95 | 353.2 | 0.548 | 16.3 | 193.6 | 27.7 | 34
RV27 | 27.5 | 11000 | 85 | 72 | 95 | 353.3 | 0.693 | 20.6 | 244.7 | 27.6 | 34
RV27 | 27.5 | 11000 | 90 | 72 | 95 | 353.7 | 0.837 | 24.92 | 296 | 27.5 | 34
RV27 | 27.5 | 11000 | 80 | 77 | 95 | 382 | 0.375 | 12.06 | 143.3 | 27.8 | 34
RV27 | 27.5 | 11000 | 85 | 77 | 95 | 382.7 | 0.5 | 16.11 | 191.4 | 27.7 | 34
RV27 | 27.5 | 11000 | 90 | 77 | 95 | 382.3 | 0.635 | 20.43 | 242.7 | 27.6 | 34
RV27 | 27.5 | 11000 | 65 | 57 | 105 | 256.1 | 0.731 | 15.76 | 187.2 | 30.2 | 34
RV27 | 27.5 | 11000 | 70 | 57 | 105 | 257.5 | 0.923 | 20.01 | 237.7 | 30 | 34
RV27 | 27.5 | 11000 | 75 | 57 | 105 | 270 | 0.962 | 21.86 | 259.7 | 30.1 | 34
RV27 | 27.5 | 11000 | 80 | 57 | 105 | 287.5 | 0.962 | 23.27 | 276.5 | 30.1 | 34
RV27 | 27.5 | 11000 | 85 | 57 | 105 | 304.9 | 0.962 | 24.69 | 293.3 | 30.1 | 34
RV27 | 27.5 | 11000 | 90 | 57 | 105 | 322.3 | 0.962 | 26.09 | 310 | 30.1 | 34
RV27 | 27.5 | 11000 | 65 | 62 | 105 | 279.3 | 0.491 | 11.53 | 137 | 30.6 | 34
RV27 | 27.5 | 11000 | 70 | 62 | 105 | 281 | 0.673 | 15.93 | 189.2 | 30.3 | 34
RV27 | 27.5 | 11000 | 75 | 62 | 105 | 282.5 | 0.846 | 20.13 | 239.1 | 30.2 | 34
RV27 | 27.5 | 11000 | 80 | 62 | 105 | 287.6 | 0.962 | 23.29 | 276.7 | 30.1 | 34
RV27 | 27.5 | 11000 | 85 | 62 | 105 | 305 | 0.962 | 24.7 | 293.4 | 30.1 | 34
RV27 | 27.5 | 11000 | 90 | 62 | 105 | 322.5 | 0.962 | 26.11 | 310.2 | 30.1 | 34
RV27 | 27.5 | 11000 | 70 | 67 | 105 | 306.6 | 0.452 | 11.67 | 138.6 | 30.6 | 34
RV27 | 27.5 | 11000 | 75 | 67 | 105 | 308.6 | 0.616 | 15.99 | 190 | 30.5 | 34
RV27 | 27.5 | 11000 | 80 | 67 | 105 | 308.4 | 0.779 | 20.23 | 240.3 | 30.3 | 34
RV27 | 27.5 | 11000 | 85 | 67 | 105 | 309.9 | 0.924 | 24.09 | 286.2 | 30.2 | 34
RV27 | 27.5 | 11000 | 90 | 67 | 105 | 322.6 | 0.962 | 26.12 | 310.3 | 30.1 | 34
RV27 | 27.5 | 11000 | 75 | 72 | 105 | 335 | 0.414 | 11.67 | 138.6 | 30.7 | 34
RV27 | 27.5 | 11000 | 80 | 72 | 105 | 336.1 | 0.558 | 15.78 | 187.5 | 30.5 | 34
RV27 | 27.5 | 11000 | 85 | 72 | 105 | 336.1 | 0.712 | 20.14 | 239.3 | 30.4 | 34
RV27 | 27.5 | 11000 | 90 | 72 | 105 | 337.1 | 0.856 | 24.29 | 288.6 | 30.2 | 34
RV27 | 27.5 | 11000 | 80 | 77 | 105 | 363.8 | 0.375 | 11.49 | 136.5 | 30.7 | 34
RV27 | 27.5 | 11000 | 85 | 77 | 105 | 364.8 | 0.51 | 15.66 | 186 | 30.5 | 34
RV27 | 27.5 | 11000 | 90 | 77 | 105 | 364.6 | 0.654 | 20.08 | 238.5 | 30.4 | 34
RV27 | 27.5 | 11000 | 65 | 57 | 115 | 240.6 | 0.75 | 15.19 | 180.5 | 33.3 | 35
RV27 | 27.5 | 11000 | 70 | 57 | 115 | 242.1 | 0.943 | 19.22 | 228.3 | 33 | 35
RV27 | 27.5 | 11000 | 75 | 57 | 115 | 256.9 | 0.962 | 20.8 | 247.1 | 33 | 35
RV27 | 27.5 | 11000 | 80 | 57 | 115 | 273.8 | 0.962 | 22.16 | 263.3 | 33 | 35
RV27 | 27.5 | 11000 | 85 | 57 | 115 | 290.8 | 0.962 | 23.54 | 279.7 | 33.1 | 35
RV27 | 27.5 | 11000 | 90 | 57 | 115 | 307.9 | 0.962 | 24.93 | 296.2 | 33.1 | 35
RV27 | 27.5 | 11000 | 65 | 62 | 115 | 262.5 | 0.491 | 10.84 | 128.8 | 33.7 | 35
RV27 | 27.5 | 11000 | 70 | 62 | 115 | 264.3 | 0.683 | 15.19 | 180.5 | 33.3 | 35
RV27 | 27.5 | 11000 | 75 | 62 | 115 | 266 | 0.866 | 19.39 | 230.3 | 33.1 | 35
RV27 | 27.5 | 11000 | 80 | 62 | 115 | 273.9 | 0.962 | 22.18 | 263.5 | 33 | 35
RV27 | 27.5 | 11000 | 85 | 62 | 115 | 291.1 | 0.962 | 23.57 | 280 | 33.1 | 35
RV27 | 27.5 | 11000 | 90 | 62 | 115 | 308 | 0.962 | 24.94 | 296.3 | 33.1 | 35
RV27 | 27.5 | 11000 | 70 | 67 | 115 | 288.4 | 0.452 | 10.98 | 130.4 | 33.8 | 35
RV27 | 27.5 | 11000 | 75 | 67 | 115 | 289.8 | 0.625 | 15.25 | 181.2 | 33.4 | 35
RV27 | 27.5 | 11000 | 80 | 67 | 115 | 291.1 | 0.798 | 19.56 | 232.4 | 33.3 | 35
RV27 | 27.5 | 11000 | 85 | 67 | 115 | 292 | 0.952 | 23.4 | 278 | 33.1 | 35
RV27 | 27.5 | 11000 | 90 | 67 | 115 | 308.2 | 0.962 | 24.95 | 296.4 | 33.1 | 35
RV27 | 27.5 | 11000 | 75 | 72 | 115 | 315.7 | 0.414 | 10.99 | 130.6 | 33.8 | 35
RV27 | 27.5 | 11000 | 80 | 72 | 115 | 317.2 | 0.567 | 15.15 | 180 | 33.5 | 35
RV27 | 27.5 | 11000 | 85 | 72 | 115 | 317.3 | 0.731 | 19.53 | 232 | 33.4 | 35
RV27 | 27.5 | 11000 | 90 | 72 | 115 | 317.8 | 0.885 | 23.67 | 281.2 | 33.2 | 35
RV27 | 27.5 | 11000 | 80 | 77 | 115 | 343.4 | 0.375 | 10.84 | 128.8 | 33.8 | 35
RV27 | 27.5 | 11000 | 85 | 77 | 115 | 344.7 | 0.529 | 15.35 | 182.4 | 33.6 | 35
RV27 | 27.5 | 11000 | 90 | 77 | 115 | 344.4 | 0.673 | 19.52 | 231.9 | 33.5 | 35
RV27 | 27.5 | 11000 | 65 | 57 | 125 | 224.1 | 0.77 | 14.52 | 172.5 | 36.6 | 35
RV27 | 27.5 | 11000 | 70 | 57 | 125 | 226.7 | 0.962 | 18.35 | 218 | 36.2 | 35
RV27 | 27.5 | 11000 | 75 | 57 | 125 | 242.8 | 0.962 | 19.66 | 233.6 | 36.1 | 35
RV27 | 27.5 | 11000 | 80 | 57 | 125 | 259.2 | 0.962 | 20.99 | 249.4 | 36.2 | 35
RV27 | 27.5 | 11000 | 85 | 57 | 125 | 275.8 | 0.962 | 22.33 | 265.3 | 36.2 | 35
RV27 | 27.5 | 11000 | 90 | 57 | 125 | 292.7 | 0.962 | 23.7 | 281.5 | 36.2 | 35
RV27 | 27.5 | 11000 | 65 | 62 | 125 | 244.9 | 0.5 | 10.31 | 122.5 | 37.2 | 35
RV27 | 27.5 | 11000 | 70 | 62 | 125 | 247 | 0.702 | 14.6 | 173.5 | 36.7 | 35
RV27 | 27.5 | 11000 | 75 | 62 | 125 | 248.4 | 0.904 | 18.91 | 224.6 | 36.2 | 35
RV27 | 27.5 | 11000 | 80 | 62 | 125 | 259.3 | 0.962 | 21 | 249.5 | 36.2 | 35
RV27 | 27.5 | 11000 | 85 | 62 | 125 | 276 | 0.962 | 22.35 | 265.5 | 36.2 | 35
RV27 | 27.5 | 11000 | 90 | 62 | 125 | 292.8 | 0.962 | 23.71 | 281.7 | 36.2 | 35
RV27 | 27.5 | 11000 | 70 | 67 | 125 | 269.7 | 0.462 | 10.48 | 124.5 | 37.2 | 35
RV27 | 27.5 | 11000 | 75 | 67 | 125 | 271.6 | 0.644 | 14.73 | 175 | 36.7 | 35
RV27 | 27.5 | 11000 | 80 | 67 | 125 | 273 | 0.818 | 18.79 | 223.2 | 36.3 | 35
RV27 | 27.5 | 11000 | 85 | 67 | 125 | 276 | 0.962 | 22.35 | 265.5 | 36.2 | 35
RV27 | 27.5 | 11000 | 90 | 67 | 125 | 293 | 0.962 | 23.72 | 281.8 | 36.2 | 35
RV27 | 27.5 | 11000 | 75 | 72 | 125 | 295.5 | 0.423 | 10.52 | 125 | 37.2 | 35
RV27 | 27.5 | 11000 | 80 | 72 | 125 | 297.4 | 0.587 | 14.69 | 174.5 | 36.8 | 35
RV27 | 27.5 | 11000 | 85 | 72 | 125 | 297.8 | 0.76 | 19.05 | 226.3 | 36.5 | 35
RV27 | 27.5 | 11000 | 90 | 72 | 125 | 298.7 | 0.914 | 22.98 | 273 | 36.3 | 35
RV27 | 27.5 | 11000 | 80 | 77 | 125 | 322.1 | 0.385 | 10.43 | 123.9 | 37.2 | 35
RV27 | 27.5 | 11000 | 85 | 77 | 125 | 323.6 | 0.539 | 14.67 | 174.3 | 36.8 | 35
RV27 | 27.5 | 11000 | 90 | 77 | 125 | 323.3 | 0.693 | 18.85 | 223.9 | 36.7 | 35
RV27 | 27.5 | 12375 | 65 | 57 | 75 | 301.3 | 0.722 | 16.27 | 217.4 | 23.8 | 33
RV27 | 27.5 | 12375 | 70 | 57 | 75 | 302.5 | 0.904 | 20.46 | 273.5 | 23.7 | 33
RV27 | 27.5 | 12375 | 75 | 57 | 75 | 314.5 | 0.962 | 22.63 | 302.5 | 23.6 | 33
RV27 | 27.5 | 12375 | 80 | 57 | 75 | 333.4 | 0.962 | 24 | 320.7 | 23.5 | 33
RV27 | 27.5 | 12375 | 85 | 57 | 75 | 352 | 0.962 | 25.33 | 338.6 | 23.3 | 33
RV27 | 27.5 | 12375 | 90 | 57 | 75 | 371.4 | 0.962 | 26.73 | 357.3 | 23.2 | 33
RV27 | 27.5 | 12375 | 65 | 62 | 75 | 328 | 0.491 | 12.04 | 160.9 | 23.8 | 33
RV27 | 27.5 | 12375 | 70 | 62 | 75 | 329.4 | 0.664 | 16.36 | 218.6 | 23.7 | 33
RV27 | 27.5 | 12375 | 75 | 62 | 75 | 330.4 | 0.827 | 20.45 | 273.3 | 23.6 | 33
RV27 | 27.5 | 12375 | 80 | 62 | 75 | 333.5 | 0.962 | 24 | 320.8 | 23.5 | 33
RV27 | 27.5 | 12375 | 85 | 62 | 75 | 352.3 | 0.962 | 25.36 | 338.9 | 23.3 | 33
RV27 | 27.5 | 12375 | 90 | 62 | 75 | 371.6 | 0.962 | 26.74 | 357.4 | 23.2 | 33
RV27 | 27.5 | 12375 | 70 | 67 | 75 | 358.1 | 0.443 | 11.86 | 158.5 | 23.7 | 33
RV27 | 27.5 | 12375 | 75 | 67 | 75 | 359 | 0.606 | 16.28 | 217.6 | 23.6 | 33
RV27 | 27.5 | 12375 | 80 | 67 | 75 | 359 | 0.76 | 20.41 | 272.8 | 23.5 | 33
RV27 | 27.5 | 12375 | 85 | 67 | 75 | 359.8 | 0.914 | 24.59 | 328.7 | 23.3 | 33
RV27 | 27.5 | 12375 | 90 | 67 | 75 | 371.8 | 0.962 | 26.76 | 357.6 | 23.2 | 33
RV27 | 27.5 | 12375 | 75 | 72 | 75 | 389.3 | 0.404 | 11.77 | 157.3 | 23.5 | 33
RV27 | 27.5 | 12375 | 80 | 72 | 75 | 390 | 0.558 | 16.28 | 217.6 | 23.4 | 33
RV27 | 27.5 | 12375 | 85 | 72 | 75 | 389.6 | 0.702 | 20.47 | 273.6 | 23.3 | 33
RV27 | 27.5 | 12375 | 90 | 72 | 75 | 390.5 | 0.837 | 24.45 | 326.8 | 23.2 | 33
RV27 | 27.5 | 12375 | 80 | 77 | 75 | 422 | 0.375 | 11.84 | 158.3 | 23.3 | 33
RV27 | 27.5 | 12375 | 85 | 77 | 75 | 422.2 | 0.51 | 16.11 | 215.3 | 23.2 | 33
RV27 | 27.5 | 12375 | 90 | 77 | 75 | 422 | 0.645 | 20.35 | 272 | 23.1 | 33
RV27 | 27.5 | 12375 | 65 | 57 | 85 | 289.3 | 0.731 | 15.82 | 211.5 | 26.1 | 34
RV27 | 27.5 | 12375 | 70 | 57 | 85 | 290.6 | 0.924 | 20.08 | 268.4 | 26 | 34
RV27 | 27.5 | 12375 | 75 | 57 | 85 | 304.5 | 0.962 | 21.92 | 292.9 | 25.9 | 34
RV27 | 27.5 | 12375 | 80 | 57 | 85 | 323.2 | 0.962 | 23.26 | 310.9 | 25.9 | 34
RV27 | 27.5 | 12375 | 85 | 57 | 85 | 341.8 | 0.962 | 24.6 | 328.8 | 25.8 | 34
RV27 | 27.5 | 12375 | 90 | 57 | 85 | 360.3 | 0.962 | 25.93 | 346.6 | 25.6 | 34
RV27 | 27.5 | 12375 | 65 | 62 | 85 | 315 | 0.49 | 11.56 | 154.5 | 26.2 | 34
RV27 | 27.5 | 12375 | 70 | 62 | 85 | 316.6 | 0.673 | 15.95 | 213.2 | 26.1 | 34
RV27 | 27.5 | 12375 | 75 | 62 | 85 | 317.9 | 0.846 | 20.13 | 269.1 | 26 | 34
RV27 | 27.5 | 12375 | 80 | 62 | 85 | 323.2 | 0.962 | 23.26 | 310.9 | 25.9 | 34
RV27 | 27.5 | 12375 | 85 | 62 | 85 | 342 | 0.962 | 24.61 | 328.9 | 25.8 | 34
RV27 | 27.5 | 12375 | 90 | 62 | 85 | 360.5 | 0.962 | 25.95 | 346.8 | 25.7 | 34
RV27 | 27.5 | 12375 | 70 | 67 | 85 | 344.4 | 0.452 | 11.65 | 155.7 | 26.2 | 34
RV27 | 27.5 | 12375 | 75 | 67 | 85 | 345.4 | 0.616 | 15.91 | 212.7 | 26.1 | 34
RV27 | 27.5 | 12375 | 80 | 67 | 85 | 345.9 | 0.779 | 20.16 | 269.5 | 26 | 34
RV27 | 27.5 | 12375 | 85 | 67 | 85 | 347.2 | 0.923 | 23.99 | 320.6 | 25.8 | 34
RV27 | 27.5 | 12375 | 90 | 67 | 85 | 360.7 | 0.962 | 25.96 | 347 | 25.7 | 34
RV27 | 27.5 | 12375 | 75 | 72 | 85 | 374.8 | 0.414 | 11.6 | 155 | 26.1 | 34
RV27 | 27.5 | 12375 | 80 | 72 | 85 | 375.8 | 0.558 | 15.68 | 209.6 | 26 | 34
RV27 | 27.5 | 12375 | 85 | 72 | 85 | 375.2 | 0.712 | 19.99 | 267.1 | 25.9 | 34
RV27 | 27.5 | 12375 | 90 | 72 | 85 | 376.2 | 0.856 | 24.09 | 322 | 25.7 | 34
RV27 | 27.5 | 12375 | 80 | 77 | 85 | 406.1 | 0.375 | 11.4 | 152.3 | 26 | 34
RV27 | 27.5 | 12375 | 85 | 77 | 85 | 406.5 | 0.52 | 15.8 | 211.2 | 25.8 | 34
RV27 | 27.5 | 12375 | 90 | 77 | 85 | 407.8 | 0.654 | 19.96 | 266.7 | 25.8 | 34
RV27 | 27.5 | 12375 | 65 | 57 | 95 | 276.4 | 0.741 | 15.32 | 204.7 | 28.5 | 34
RV27 | 27.5 | 12375 | 70 | 57 | 95 | 278 | 0.933 | 19.41 | 259.4 | 28.4 | 34
RV27 | 27.5 | 12375 | 75 | 57 | 95 | 293.3 | 0.962 | 21.11 | 282.2 | 28.4 | 34
RV27 | 27.5 | 12375 | 80 | 57 | 95 | 311.9 | 0.962 | 22.45 | 300 | 28.4 | 34
RV27 | 27.5 | 12375 | 85 | 57 | 95 | 330.2 | 0.962 | 23.76 | 317.6 | 28.4 | 34
RV27 | 27.5 | 12375 | 90 | 57 | 95 | 348.6 | 0.962 | 25.09 | 335.3 | 28.3 | 34
RV27 | 27.5 | 12375 | 65 | 62 | 95 | 301.1 | 0.491 | 11.05 | 147.7 | 28.8 | 34
RV27 | 27.5 | 12375 | 70 | 62 | 95 | 302.8 | 0.683 | 15.47 | 206.8 | 28.6 | 34
RV27 | 27.5 | 12375 | 75 | 62 | 95 | 304.1 | 0.866 | 19.7 | 263.3 | 28.5 | 34
RV27 | 27.5 | 12375 | 80 | 62 | 95 | 312 | 0.962 | 22.45 | 300.1 | 28.4 | 34
RV27 | 27.5 | 12375 | 85 | 62 | 95 | 330.4 | 0.962 | 23.78 | 317.8 | 28.4 | 34
RV27 | 27.5 | 12375 | 90 | 62 | 95 | 348.7 | 0.962 | 25.1 | 335.5 | 28.3 | 34
RV27 | 27.5 | 12375 | 70 | 67 | 95 | 329.3 | 0.452 | 11.14 | 148.9 | 28.8 | 34
RV27 | 27.5 | 12375 | 75 | 67 | 95 | 330.7 | 0.625 | 15.47 | 206.7 | 28.7 | 34
RV27 | 27.5 | 12375 | 80 | 67 | 95 | 331.5 | 0.798 | 19.81 | 264.7 | 28.6 | 34
RV27 | 27.5 | 12375 | 85 | 67 | 95 | 332.2 | 0.952 | 23.67 | 316.4 | 28.4 | 34
RV27 | 27.5 | 12375 | 90 | 67 | 95 | 348.9 | 0.962 | 25.11 | 335.6 | 28.3 | 34
RV27 | 27.5 | 12375 | 75 | 72 | 95 | 359 | 0.414 | 11.11 | 148.5 | 28.8 | 34
RV27 | 27.5 | 12375 | 80 | 72 | 95 | 359.9 | 0.567 | 15.28 | 204.2 | 28.7 | 34
RV27 | 27.5 | 12375 | 85 | 72 | 95 | 359.6 | 0.731 | 19.67 | 262.9 | 28.6 | 34
RV27 | 27.5 | 12375 | 90 | 72 | 95 | 359.7 | 0.885 | 23.82 | 318.3 | 28.4 | 34
RV27 | 27.5 | 12375 | 80 | 77 | 95 | 389.3 | 0.375 | 10.92 | 146 | 28.8 | 34
RV27 | 27.5 | 12375 | 85 | 77 | 95 | 390 | 0.519 | 15.16 | 202.6 | 28.6 | 34
RV27 | 27.5 | 12375 | 90 | 77 | 95 | 389.3 | 0.673 | 19.61 | 262.1 | 28.5 | 34
RV27 | 27.5 | 12375 | 65 | 57 | 105 | 262.7 | 0.76 | 14.94 | 199.7 | 31.2 | 35
RV27 | 27.5 | 12375 | 70 | 57 | 105 | 264.3 | 0.962 | 19.03 | 254.3 | 31 | 35
RV27 | 27.5 | 12375 | 75 | 57 | 105 | 281.7 | 0.962 | 20.28 | 271 | 31 | 35
RV27 | 27.5 | 12375 | 80 | 57 | 105 | 299.7 | 0.962 | 21.57 | 288.3 | 31.1 | 35
RV27 | 27.5 | 12375 | 85 | 57 | 105 | 317.9 | 0.962 | 22.88 | 305.8 | 31.1 | 35
RV27 | 27.5 | 12375 | 90 | 57 | 105 | 335.9 | 0.962 | 24.18 | 323.1 | 31.1 | 35
RV27 | 27.5 | 12375 | 65 | 62 | 105 | 286.5 | 0.5 | 10.72 | 143.3 | 31.5 | 35
RV27 | 27.5 | 12375 | 70 | 62 | 105 | 288.2 | 0.693 | 14.93 | 199.6 | 31.3 | 35
RV27 | 27.5 | 12375 | 75 | 62 | 105 | 289.4 | 0.885 | 19.16 | 256.1 | 31.1 | 35
RV27 | 27.5 | 12375 | 80 | 62 | 105 | 299.7 | 0.962 | 21.57 | 288.3 | 31.1 | 35
RV27 | 27.5 | 12375 | 85 | 62 | 105 | 318.1 | 0.962 | 22.9 | 306 | 31.1 | 35
RV27 | 27.5 | 12375 | 90 | 62 | 105 | 336.1 | 0.962 | 24.19 | 323.3 | 31.1 | 35
RV27 | 27.5 | 12375 | 70 | 67 | 105 | 313.5 | 0.452 | 10.6 | 141.7 | 31.5 | 35
RV27 | 27.5 | 12375 | 75 | 67 | 105 | 315 | 0.635 | 14.96 | 200 | 31.4 | 35
RV27 | 27.5 | 12375 | 80 | 67 | 105 | 316.2 | 0.808 | 19.12 | 255.5 | 31.2 | 35
RV27 | 27.5 | 12375 | 85 | 67 | 105 | 318.2 | 0.962 | 22.9 | 306.1 | 31.1 | 35
RV27 | 27.5 | 12375 | 90 | 67 | 105 | 336.3 | 0.962 | 24.21 | 323.5 | 31.1 | 35
RV27 | 27.5 | 12375 | 75 | 72 | 105 | 342.1 | 0.414 | 10.59 | 141.5 | 31.6 | 35
RV27 | 27.5 | 12375 | 80 | 72 | 105 | 343.3 | 0.577 | 14.83 | 198.2 | 31.4 | 35
RV27 | 27.5 | 12375 | 85 | 72 | 105 | 343.2 | 0.75 | 19.27 | 257.5 | 31.3 | 35
RV27 | 27.5 | 12375 | 90 | 72 | 105 | 343.8 | 0.904 | 23.26 | 310.9 | 31.1 | 35
RV27 | 27.5 | 12375 | 80 | 77 | 105 | 371.4 | 0.385 | 10.69 | 142.9 | 31.6 | 35
RV27 | 27.5 | 12375 | 85 | 77 | 105 | 372.2 | 0.529 | 14.73 | 196.9 | 31.4 | 35
RV27 | 27.5 | 12375 | 90 | 77 | 105 | 371.7 | 0.683 | 19 | 253.9 | 31.3 | 35
RV27 | 27.5 | 12375 | 65 | 57 | 115 | 247.8 | 0.779 | 14.45 | 193.1 | 34.2 | 35
RV27 | 27.5 | 12375 | 70 | 57 | 115 | 251.4 | 0.962 | 18.09 | 241.8 | 33.9 | 35
RV27 | 27.5 | 12375 | 75 | 57 | 115 | 268.5 | 0.962 | 19.33 | 258.3 | 33.9 | 35
RV27 | 27.5 | 12375 | 80 | 57 | 115 | 286.1 | 0.962 | 20.59 | 275.2 | 34 | 35
RV27 | 27.5 | 12375 | 85 | 57 | 115 | 303.8 | 0.962 | 21.86 | 292.2 | 34.1 | 35
RV27 | 27.5 | 12375 | 90 | 57 | 115 | 321.6 | 0.962 | 23.15 | 309.4 | 34.1 | 35
RV27 | 27.5 | 12375 | 65 | 62 | 115 | 270.2 | 0.5 | 10.11 | 135.1 | 34.7 | 35
RV27 | 27.5 | 12375 | 70 | 62 | 115 | 272 | 0.712 | 14.49 | 193.6 | 34.3 | 35
RV27 | 27.5 | 12375 | 75 | 62 | 115 | 273.6 | 0.914 | 18.71 | 250 | 34 | 35
RV27 | 27.5 | 12375 | 80 | 62 | 115 | 286.2 | 0.962 | 20.6 | 275.3 | 34 | 35
RV27 | 27.5 | 12375 | 85 | 62 | 115 | 304 | 0.962 | 21.88 | 292.4 | 34.1 | 35
RV27 | 27.5 | 12375 | 90 | 62 | 115 | 321.7 | 0.962 | 23.16 | 309.5 | 34.1 | 35
RV27 | 27.5 | 12375 | 70 | 67 | 115 | 295.8 | 0.462 | 10.22 | 136.6 | 34.8 | 35
RV27 | 27.5 | 12375 | 75 | 67 | 115 | 297.8 | 0.654 | 14.58 | 194.8 | 34.4 | 35
RV27 | 27.5 | 12375 | 80 | 67 | 115 | 299 | 0.837 | 18.72 | 250.2 | 34.2 | 35
RV27 | 27.5 | 12375 | 85 | 67 | 115 | 304 | 0.962 | 21.88 | 292.4 | 34.1 | 35
RV27 | 27.5 | 12375 | 90 | 67 | 115 | 321.9 | 0.962 | 23.16 | 309.6 | 34.1 | 35
RV27 | 27.5 | 12375 | 75 | 72 | 115 | 323.1 | 0.423 | 10.24 | 136.8 | 34.8 | 35
RV27 | 27.5 | 12375 | 80 | 72 | 115 | 324.5 | 0.596 | 14.48 | 193.5 | 34.5 | 35
RV27 | 27.5 | 12375 | 85 | 72 | 115 | 324.9 | 0.769 | 18.71 | 250 | 34.3 | 35
RV27 | 27.5 | 12375 | 90 | 72 | 115 | 325.9 | 0.933 | 22.75 | 304.1 | 34.1 | 35
RV27 | 27.5 | 12375 | 80 | 77 | 115 | 351 | 0.385 | 10.1 | 135 | 34.8 | 35
RV27 | 27.5 | 12375 | 85 | 77 | 115 | 352.5 | 0.548 | 14.46 | 193.3 | 34.6 | 35
RV27 | 27.5 | 12375 | 90 | 77 | 115 | 351.9 | 0.712 | 18.74 | 250.5 | 34.4 | 35
RV27 | 27.5 | 12375 | 65 | 57 | 125 | 232.4 | 0.799 | 13.89 | 185.6 | 37.6 | 35
RV27 | 27.5 | 12375 | 70 | 57 | 125 | 237.8 | 0.962 | 17.12 | 228.8 | 37.2 | 35
RV27 | 27.5 | 12375 | 75 | 57 | 125 | 254.7 | 0.962 | 18.33 | 245 | 37.1 | 35
RV27 | 27.5 | 12375 | 80 | 57 | 125 | 271.6 | 0.962 | 19.54 | 261.2 | 37.1 | 35
RV27 | 27.5 | 12375 | 85 | 57 | 125 | 288.9 | 0.962 | 20.79 | 277.9 | 37.2 | 35
RV27 | 27.5 | 12375 | 90 | 57 | 125 | 306 | 0.962 | 22.02 | 294.3 | 37.2 | 35
RV27 | 27.5 | 12375 | 65 | 62 | 125 | 253.1 | 0.51 | 9.65 | 129 | 38.2 | 35
RV27 | 27.5 | 12375 | 70 | 62 | 125 | 254.9 | 0.731 | 13.95 | 186.4 | 37.6 | 35
RV27 | 27.5 | 12375 | 75 | 62 | 125 | 256.5 | 0.943 | 18.09 | 241.8 | 37.2 | 35
RV27 | 27.5 | 12375 | 80 | 62 | 125 | 271.7 | 0.962 | 19.55 | 261.3 | 37.1 | 35
RV27 | 27.5 | 12375 | 85 | 62 | 125 | 289 | 0.962 | 20.8 | 278 | 37.2 | 35
RV27 | 27.5 | 12375 | 90 | 62 | 125 | 306 | 0.962 | 22.02 | 294.3 | 37.2 | 35
RV27 | 27.5 | 12375 | 70 | 67 | 125 | 277.5 | 0.462 | 9.58 | 128.1 | 38.2 | 35
RV27 | 27.5 | 12375 | 75 | 67 | 125 | 279.5 | 0.664 | 13.88 | 185.5 | 37.8 | 35
RV27 | 27.5 | 12375 | 80 | 67 | 125 | 280.3 | 0.866 | 18.15 | 242.6 | 37.3 | 35
RV27 | 27.5 | 12375 | 85 | 67 | 125 | 289.1 | 0.962 | 20.81 | 278.1 | 37.2 | 35
RV27 | 27.5 | 12375 | 90 | 67 | 125 | 306.4 | 0.962 | 22.05 | 294.7 | 37.2 | 35
RV27 | 27.5 | 12375 | 75 | 72 | 125 | 303.3 | 0.423 | 9.61 | 128.4 | 38.2 | 35
RV27 | 27.5 | 12375 | 80 | 72 | 125 | 305 | 0.615 | 14.04 | 187.7 | 37.7 | 35
RV27 | 27.5 | 12375 | 85 | 72 | 125 | 306.1 | 0.789 | 18.06 | 241.4 | 37.4 | 35
RV27 | 27.5 | 12375 | 90 | 72 | 125 | 306.3 | 0.962 | 22.04 | 294.6 | 37.2 | 35
RV27 | 27.5 | 12375 | 80 | 77 | 125 | 329.9 | 0.394 | 9.73 | 130.1 | 38.2 | 35
RV27 | 27.5 | 12375 | 85 | 77 | 125 | 331.2 | 0.558 | 13.83 | 184.8 | 37.8 | 35
RV27 | 27.5 | 12375 | 90 | 77 | 125 | 331.2 | 0.731 | 18.11 | 242.1 | 37.6 | 35
RV30 | 30 | 7500 | 65 | 57 | 75 | 290.8 | 0.641 | 23.02 | 186.5 | 24.5 | 36
RV30 | 30 | 7500 | 70 | 57 | 75 | 291.2 | 0.758 | 27.25 | 220.7 | 24.4 | 36
RV30 | 30 | 7500 | 75 | 57 | 75 | 291.1 | 0.875 | 31.44 | 254.7 | 24.4 | 36
RV30 | 30 | 7500 | 80 | 57 | 75 | 292.7 | 0.972 | 35.12 | 284.5 | 24.3 | 36
RV30 | 30 | 7500 | 85 | 57 | 75 | 308.3 | 0.972 | 36.99 | 299.6 | 24.4 | 36
RV30 | 30 | 7500 | 90 | 57 | 75 | 324.1 | 0.972 | 38.89 | 315 | 24.5 | 36
RV30 | 30 | 7500 | 65 | 62 | 75 | 318.2 | 0.476 | 18.72 | 151.6 | 24.7 | 36
RV30 | 30 | 7500 | 70 | 62 | 75 | 318.8 | 0.583 | 22.95 | 185.9 | 24.6 | 36
RV30 | 30 | 7500 | 75 | 62 | 75 | 319 | 0.7 | 27.57 | 223.3 | 24.6 | 36
RV30 | 30 | 7500 | 80 | 62 | 75 | 319 | 0.807 | 31.77 | 257.3 | 24.6 | 36
RV30 | 30 | 7500 | 85 | 62 | 75 | 319.5 | 0.914 | 36.04 | 291.9 | 24.5 | 36
RV30 | 30 | 7500 | 90 | 62 | 75 | 324.3 | 0.972 | 38.91 | 315.2 | 24.5 | 36
RV30 | 30 | 7500 | 70 | 67 | 75 | 348.9 | 0.437 | 18.84 | 152.6 | 24.8 | 36
RV30 | 30 | 7500 | 75 | 67 | 75 | 349.2 | 0.535 | 23.05 | 186.7 | 24.8 | 36
RV30 | 30 | 7500 | 80 | 67 | 75 | 349.4 | 0.632 | 27.25 | 220.7 | 24.7 | 36
RV30 | 30 | 7500 | 85 | 67 | 75 | 349.4 | 0.739 | 31.86 | 258.1 | 24.7 | 36
RV30 | 30 | 7500 | 90 | 67 | 75 | 348.7 | 0.836 | 35.98 | 291.4 | 24.7 | 36
RV30 | 30 | 7500 | 75 | 72 | 75 | 382.4 | 0.399 | 18.81 | 152.4 | 24.9 | 36
RV30 | 30 | 7500 | 80 | 72 | 75 | 382.3 | 0.486 | 22.94 | 185.8 | 24.8 | 36
RV30 | 30 | 7500 | 85 | 72 | 75 | 382.4 | 0.583 | 27.53 | 223 | 24.8 | 36
RV30 | 30 | 7500 | 90 | 72 | 75 | 382.3 | 0.671 | 31.65 | 256.4 | 24.7 | 36
RV30 | 30 | 7500 | 80 | 77 | 75 | 416.9 | 0.36 | 18.51 | 149.9 | 24.9 | 36
RV30 | 30 | 7500 | 85 | 77 | 75 | 417.3 | 0.447 | 23.04 | 186.6 | 24.8 | 36
RV30 | 30 | 7500 | 90 | 77 | 75 | 416.7 | 0.535 | 27.51 | 222.8 | 24.7 | 36
RV30 | 30 | 7500 | 65 | 57 | 85 | 279.4 | 0.641 | 22.12 | 179.2 | 27 | 36
RV30 | 30 | 7500 | 70 | 57 | 85 | 279.9 | 0.768 | 26.53 | 214.9 | 26.9 | 36
RV30 | 30 | 7500 | 75 | 57 | 85 | 280.1 | 0.894 | 30.93 | 250.5 | 26.9 | 36
RV30 | 30 | 7500 | 80 | 57 | 85 | 283.6 | 0.972 | 34.04 | 275.7 | 26.8 | 36
RV30 | 30 | 7500 | 85 | 57 | 85 | 299.1 | 0.972 | 35.89 | 290.7 | 26.9 | 36
RV30 | 30 | 7500 | 90 | 57 | 85 | 314.7 | 0.972 | 37.75 | 305.8 | 27 | 36
RV30 | 30 | 7500 | 65 | 62 | 85 | 306.1 | 0.476 | 18 | 145.8 | 27.3 | 36
RV30 | 30 | 7500 | 70 | 62 | 85 | 306.6 | 0.593 | 22.44 | 181.8 | 27.2 | 36
RV30 | 30 | 7500 | 75 | 62 | 85 | 306.9 | 0.7 | 26.52 | 214.8 | 27.1 | 36
RV30 | 30 | 7500 | 80 | 62 | 85 | 306.8 | 0.816 | 30.93 | 250.5 | 27.1 | 36
RV30 | 30 | 7500 | 85 | 62 | 85 | 307.4 | 0.923 | 35.04 | 283.8 | 27 | 36
RV30 | 30 | 7500 | 90 | 62 | 85 | 314.9 | 0.972 | 37.79 | 306.1 | 27 | 36
RV30 | 30 | 7500 | 70 | 67 | 85 | 335.8 | 0.437 | 18.14 | 146.9 | 27.4 | 36
RV30 | 30 | 7500 | 75 | 67 | 85 | 336 | 0.544 | 22.58 | 182.9 | 27.4 | 36
RV30 | 30 | 7500 | 80 | 67 | 85 | 336.3 | 0.641 | 26.63 | 215.7 | 27.3 | 36
RV30 | 30 | 7500 | 85 | 67 | 85 | 336.4 | 0.749 | 31.09 | 251.8 | 27.3 | 36
RV30 | 30 | 7500 | 90 | 67 | 85 | 336.2 | 0.846 | 35.1 | 284.3 | 27.3 | 36
RV30 | 30 | 7500 | 75 | 72 | 85 | 368.1 | 0.399 | 18.11 | 146.7 | 27.6 | 36
RV30 | 30 | 7500 | 80 | 72 | 85 | 368.4 | 0.496 | 22.54 | 182.6 | 27.6 | 36
RV30 | 30 | 7500 | 85 | 72 | 85 | 368.5 | 0.583 | 26.53 | 214.9 | 27.5 | 36
RV30 | 30 | 7500 | 90 | 72 | 85 | 368.4 | 0.681 | 30.95 | 250.7 | 27.5 | 36
RV30 | 30 | 7500 | 80 | 77 | 85 | 401.4 | 0.36 | 17.83 | 144.4 | 27.8 | 36
RV30 | 30 | 7500 | 85 | 77 | 85 | 402 | 0.447 | 22.19 | 179.7 | 27.7 | 36
RV30 | 30 | 7500 | 90 | 77 | 85 | 401.8 | 0.535 | 26.52 | 214.8 | 27.6 | 36
RV30 | 30 | 7500 | 65 | 57 | 95 | 267.3 | 0.651 | 21.49 | 174.1 | 29.9 | 36
RV30 | 30 | 7500 | 70 | 57 | 95 | 267.9 | 0.778 | 25.72 | 208.3 | 29.8 | 36
RV30 | 30 | 7500 | 75 | 57 | 95 | 268.4 | 0.904 | 29.95 | 242.6 | 29.7 | 36
RV30 | 30 | 7500 | 80 | 57 | 95 | 273.9 | 0.972 | 32.86 | 266.2 | 29.6 | 36
RV30 | 30 | 7500 | 85 | 57 | 95 | 289.1 | 0.972 | 34.69 | 281 | 29.7 | 36
RV30 | 30 | 7500 | 90 | 57 | 95 | 304.5 | 0.972 | 36.54 | 296 | 29.8 | 36
RV30 | 30 | 7500 | 65 | 62 | 95 | 292.8 | 0.476 | 17.21 | 139.4 | 30.3 | 36
RV30 | 30 | 7500 | 70 | 62 | 95 | 293.5 | 0.593 | 21.48 | 174 | 30.1 | 36
RV30 | 30 | 7500 | 75 | 62 | 95 | 294 | 0.71 | 25.75 | 208.6 | 30 | 36
RV30 | 30 | 7500 | 80 | 62 | 95 | 293.4 | 0.836 | 30.28 | 245.3 | 30 | 36
RV30 | 30 | 7500 | 85 | 62 | 95 | 294.1 | 0.943 | 34.23 | 277.3 | 29.8 | 36
RV30 | 30 | 7500 | 90 | 62 | 95 | 304.7 | 0.972 | 36.57 | 296.2 | 29.8 | 36
RV30 | 30 | 7500 | 70 | 67 | 95 | 321.4 | 0.437 | 17.36 | 140.6 | 30.5 | 36
RV30 | 30 | 7500 | 75 | 67 | 95 | 322 | 0.544 | 21.63 | 175.2 | 30.4 | 36
RV30 | 30 | 7500 | 80 | 67 | 95 | 322.4 | 0.651 | 25.91 | 209.9 | 30.2 | 36
RV30 | 30 | 7500 | 85 | 67 | 95 | 322.5 | 0.758 | 30.19 | 244.5 | 30.2 | 36
RV30 | 30 | 7500 | 90 | 67 | 95 | 322.7 | 0.865 | 34.47 | 279.2 | 30.1 | 36
RV30 | 30 | 7500 | 75 | 72 | 95 | 352.9 | 0.399 | 17.37 | 140.7 | 30.7 | 36
RV30 | 30 | 7500 | 80 | 72 | 95 | 353.1 | 0.496 | 21.6 | 175 | 30.5 | 36
RV30 | 30 | 7500 | 85 | 72 | 95 | 353.4 | 0.593 | 25.86 | 209.5 | 30.5 | 36
RV30 | 30 | 7500 | 90 | 72 | 95 | 353.4 | 0.69 | 30.11 | 243.9 | 30.4 | 36
RV30 | 30 | 7500 | 80 | 77 | 95 | 385.2 | 0.36 | 17.1 | 138.5 | 30.8 | 36
RV30 | 30 | 7500 | 85 | 77 | 95 | 385.5 | 0.457 | 21.74 | 176.1 | 30.8 | 36
RV30 | 30 | 7500 | 90 | 77 | 95 | 385.5 | 0.544 | 25.9 | 209.8 | 30.7 | 36
RV30 | 30 | 7500 | 65 | 57 | 105 | 254.8 | 0.661 | 20.79 | 168.4 | 33.2 | 37
RV30 | 30 | 7500 | 70 | 57 | 105 | 255.4 | 0.787 | 24.81 | 201 | 33.1 | 37
RV30 | 30 | 7500 | 75 | 57 | 105 | 255.8 | 0.923 | 29.16 | 236.2 | 32.8 | 37
RV30 | 30 | 7500 | 80 | 57 | 105 | 263.7 | 0.972 | 31.64 | 256.3 | 32.8 | 37
RV30 | 30 | 7500 | 85 | 57 | 105 | 278.7 | 0.972 | 33.44 | 270.9 | 32.9 | 37
RV30 | 30 | 7500 | 90 | 57 | 105 | 293.9 | 0.972 | 35.26 | 285.6 | 33 | 37
RV30 | 30 | 7500 | 65 | 62 | 105 | 279.3 | 0.476 | 16.42 | 133 | 33.6 | 37
RV30 | 30 | 7500 | 70 | 62 | 105 | 280 | 0.602 | 20.83 | 168.7 | 33.4 | 37
RV30 | 30 | 7500 | 75 | 62 | 105 | 280.4 | 0.729 | 25.23 | 204.4 | 33.3 | 37
RV30 | 30 | 7500 | 80 | 62 | 105 | 280 | 0.846 | 29.23 | 236.8 | 33.2 | 37
RV30 | 30 | 7500 | 85 | 62 | 105 | 280.8 | 0.962 | 33.36 | 270.2 | 32.9 | 37
RV30 | 30 | 7500 | 90 | 62 | 105 | 294.1 | 0.972 | 35.28 | 285.8 | 33 | 37
RV30 | 30 | 7500 | 70 | 67 | 105 | 306.8 | 0.437 | 16.57 | 134.2 | 33.8 | 37
RV30 | 30 | 7500 | 75 | 67 | 105 | 307.3 | 0.554 | 21.02 | 170.3 | 33.7 | 37
RV30 | 30 | 7500 | 80 | 67 | 105 | 307.7 | 0.661 | 25.11 | 203.4 | 33.5 | 37
RV30 | 30 | 7500 | 85 | 67 | 105 | 308 | 0.778 | 29.57 | 239.5 | 33.4 | 37
RV30 | 30 | 7500 | 90 | 67 | 105 | 308.8 | 0.884 | 33.72 | 273.1 | 33.2 | 37
RV30 | 30 | 7500 | 75 | 72 | 105 | 336.8 | 0.398 | 16.57 | 134.2 | 34 | 37
RV30 | 30 | 7500 | 80 | 72 | 105 | 337.4 | 0.505 | 21.05 | 170.5 | 33.8 | 37
RV30 | 30 | 7500 | 85 | 72 | 105 | 337.7 | 0.603 | 25.12 | 203.5 | 33.7 | 37
RV30 | 30 | 7500 | 90 | 72 | 105 | 337.7 | 0.71 | 29.58 | 239.6 | 33.6 | 37
RV30 | 30 | 7500 | 80 | 77 | 105 | 367.8 | 0.36 | 16.33 | 132.3 | 34.1 | 37
RV30 | 30 | 7500 | 85 | 77 | 105 | 368.4 | 0.457 | 20.78 | 168.3 | 34 | 37
RV30 | 30 | 7500 | 90 | 77 | 105 | 368.5 | 0.554 | 25.21 | 204.2 | 33.9 | 37
RV30 | 30 | 7500 | 65 | 57 | 115 | 240.7 | 0.671 | 19.94 | 161.5 | 37.3 | 37
RV30 | 30 | 7500 | 70 | 57 | 115 | 241.4 | 0.807 | 24.04 | 194.7 | 37 | 37
RV30 | 30 | 7500 | 75 | 57 | 115 | 241.7 | 0.943 | 28.14 | 227.9 | 36.6 | 37
RV30 | 30 | 7500 | 80 | 57 | 115 | 252.4 | 0.972 | 30.3 | 245.4 | 36.7 | 37
RV30 | 30 | 7500 | 85 | 57 | 115 | 267.1 | 0.972 | 32.05 | 259.6 | 36.7 | 37
RV30 | 30 | 7500 | 90 | 57 | 115 | 282 | 0.972 | 33.84 | 274.1 | 36.8 | 37
RV30 | 30 | 7500 | 65 | 62 | 115 | 264 | 0.477 | 15.53 | 125.8 | 37.6 | 37
RV30 | 30 | 7500 | 70 | 62 | 115 | 264.9 | 0.612 | 20.02 | 162.2 | 37.3 | 37
RV30 | 30 | 7500 | 75 | 62 | 115 | 265.3 | 0.738 | 24.19 | 195.9 | 37.1 | 37
RV30 | 30 | 7500 | 80 | 62 | 115 | 265.6 | 0.865 | 28.37 | 229.8 | 37 | 37
RV30 | 30 | 7500 | 85 | 62 | 115 | 267.2 | 0.972 | 32.07 | 259.8 | 36.7 | 37
RV30 | 30 | 7500 | 90 | 62 | 115 | 282.2 | 0.972 | 33.85 | 274.2 | 36.8 | 37
RV30 | 30 | 7500 | 70 | 67 | 115 | 290.2 | 0.437 | 15.67 | 126.9 | 37.8 | 37
RV30 | 30 | 7500 | 75 | 67 | 115 | 291.1 | 0.554 | 19.91 | 161.3 | 37.5 | 37
RV30 | 30 | 7500 | 80 | 67 | 115 | 291.8 | 0.671 | 24.16 | 195.7 | 37.3 | 37
RV30 | 30 | 7500 | 85 | 67 | 115 | 291.5 | 0.787 | 28.33 | 229.5 | 37.2 | 37
RV30 | 30 | 7500 | 90 | 67 | 115 | 292.7 | 0.904 | 32.67 | 264.6 | 36.8 | 37
RV30 | 30 | 7500 | 75 | 72 | 115 | 319.3 | 0.399 | 15.72 | 127.3 | 37.9 | 37
RV30 | 30 | 7500 | 80 | 72 | 115 | 319.8 | 0.505 | 19.95 | 161.6 | 37.7 | 37
RV30 | 30 | 7500 | 85 | 72 | 115 | 320.2 | 0.612 | 24.21 | 196.1 | 37.5 | 37
RV30 | 30 | 7500 | 90 | 72 | 115 | 320.3 | 0.719 | 28.44 | 230.4 | 37.3 | 37
RV30 | 30 | 7500 | 80 | 77 | 115 | 348.7 | 0.369 | 15.9 | 128.8 | 38 | 37
RV30 | 30 | 7500 | 85 | 77 | 115 | 349.5 | 0.466 | 20.12 | 163 | 37.8 | 37
RV30 | 30 | 7500 | 90 | 77 | 115 | 349.7 | 0.564 | 24.33 | 197.1 | 37.7 | 37
RV30 | 30 | 7500 | 65 | 57 | 125 | 226 | 0.681 | 18.99 | 153.8 | 42.2 | 38
RV30 | 30 | 7500 | 70 | 57 | 125 | 226.3 | 0.826 | 23.09 | 187 | 41.9 | 38
RV30 | 30 | 7500 | 75 | 57 | 125 | 226.3 | 0.972 | 27.16 | 220 | 41.2 | 38
RV30 | 30 | 7500 | 80 | 57 | 125 | 240.4 | 0.972 | 28.85 | 233.7 | 41.1 | 38
RV30 | 30 | 7500 | 85 | 57 | 125 | 254.9 | 0.972 | 30.58 | 247.7 | 41 | 38
RV30 | 30 | 7500 | 90 | 57 | 125 | 269.5 | 0.972 | 32.33 | 261.9 | 41 | 38
RV30 | 30 | 7500 | 65 | 62 | 125 | 247.9 | 0.486 | 14.88 | 120.5 | 42.4 | 38
RV30 | 30 | 7500 | 70 | 62 | 125 | 248.9 | 0.622 | 19.11 | 154.8 | 41.9 | 38
RV30 | 30 | 7500 | 75 | 62 | 125 | 249.5 | 0.758 | 23.36 | 189.2 | 41.6 | 38
RV30 | 30 | 7500 | 80 | 62 | 125 | 250.6 | 0.894 | 27.67 | 224.1 | 41.2 | 38
RV30 | 30 | 7500 | 85 | 62 | 125 | 255 | 0.972 | 30.6 | 247.9 | 41 | 38
RV30 | 30 | 7500 | 90 | 62 | 125 | 269.6 | 0.972 | 32.36 | 262.1 | 41 | 38
RV30 | 30 | 7500 | 70 | 67 | 125 | 273.3 | 0.437 | 14.75 | 119.5 | 42.3 | 38
RV30 | 30 | 7500 | 75 | 67 | 125 | 274.3 | 0.564 | 19.09 | 154.6 | 41.9 | 38
RV30 | 30 | 7500 | 80 | 67 | 125 | 274.9 | 0.69 | 23.42 | 189.7 | 41.6 | 38
RV30 | 30 | 7500 | 85 | 67 | 125 | 274.9 | 0.816 | 27.7 | 224.4 | 41.5 | 38
RV30 | 30 | 7500 | 90 | 67 | 125 | 275.6 | 0.933 | 31.75 | 257.2 | 40.9 | 38
RV30 | 30 | 7500 | 75 | 72 | 125 | 300.8 | 0.399 | 14.8 | 119.9 | 42.3 | 38
RV30 | 30 | 7500 | 80 | 72 | 125 | 301.4 | 0.515 | 19.16 | 155.2 | 42 | 38
RV30 | 30 | 7500 | 85 | 72 | 125 | 301.9 | 0.632 | 23.54 | 190.7 | 41.7 | 38
RV30 | 30 | 7500 | 90 | 72 | 125 | 302 | 0.739 | 27.54 | 223.1 | 41.5 | 38
RV30 | 30 | 7500 | 80 | 77 | 125 | 328.9 | 0.369 | 15 | 121.5 | 42.3 | 38
RV30 | 30 | 7500 | 85 | 77 | 125 | 329.7 | 0.466 | 18.99 | 153.8 | 42.1 | 38
RV30 | 30 | 7500 | 90 | 77 | 125 | 330.1 | 0.573 | 23.37 | 189.3 | 41.8 | 38
RV30 | 30 | 9000 | 65 | 57 | 75 | 303.3 | 0.661 | 20.62 | 200.4 | 25.1 | 36
RV30 | 30 | 9000 | 70 | 57 | 75 | 303.8 | 0.797 | 24.91 | 242.1 | 25 | 36
RV30 | 30 | 9000 | 75 | 57 | 75 | 304.2 | 0.923 | 28.89 | 280.8 | 25 | 36
RV30 | 30 | 9000 | 80 | 57 | 75 | 314.2 | 0.972 | 31.42 | 305.4 | 25 | 36
RV30 | 30 | 9000 | 85 | 57 | 75 | 331.5 | 0.972 | 33.15 | 322.2 | 25.1 | 36
RV30 | 30 | 9000 | 90 | 57 | 75 | 349 | 0.972 | 34.9 | 339.2 | 25.1 | 36
RV30 | 30 | 9000 | 65 | 62 | 75 | 331.8 | 0.476 | 16.26 | 158 | 25.3 | 36
RV30 | 30 | 9000 | 70 | 62 | 75 | 332.4 | 0.603 | 20.61 | 200.3 | 25.2 | 36
RV30 | 30 | 9000 | 75 | 62 | 75 | 332.9 | 0.729 | 24.96 | 242.6 | 25.2 | 36
RV30 | 30 | 9000 | 80 | 62 | 75 | 332.9 | 0.846 | 28.96 | 281.5 | 25.2 | 36
RV30 | 30 | 9000 | 85 | 62 | 75 | 333.7 | 0.962 | 33.03 | 321.1 | 25.1 | 36
RV30 | 30 | 9000 | 90 | 62 | 75 | 349.2 | 0.972 | 34.92 | 339.4 | 25.1 | 36
RV30 | 30 | 9000 | 70 | 67 | 75 | 363.7 | 0.437 | 16.37 | 159.1 | 25.4 | 36
RV30 | 30 | 9000 | 75 | 67 | 75 | 364.2 | 0.554 | 20.76 | 201.8 | 25.4 | 36
RV30 | 30 | 9000 | 80 | 67 | 75 | 364.5 | 0.661 | 24.78 | 240.9 | 25.3 | 36
RV30 | 30 | 9000 | 85 | 67 | 75 | 364.3 | 0.778 | 29.15 | 283.3 | 25.3 | 36
RV30 | 30 | 9000 | 90 | 67 | 75 | 365.2 | 0.885 | 33.24 | 323.1 | 25.2 | 36
RV30 | 30 | 9000 | 75 | 72 | 75 | 397.3 | 0.398 | 16.29 | 158.3 | 25.5 | 36
RV30 | 30 | 9000 | 80 | 72 | 75 | 397.5 | 0.505 | 20.67 | 200.9 | 25.4 | 36
RV30 | 30 | 9000 | 85 | 72 | 75 | 397.7 | 0.603 | 24.66 | 239.7 | 25.3 | 36
RV30 | 30 | 9000 | 90 | 72 | 75 | 397.5 | 0.709 | 29.01 | 282 | 25.3 | 36
RV30 | 30 | 9000 | 80 | 77 | 75 | 432.6 | 0.369 | 16.44 | 159.8 | 25.4 | 36
RV30 | 30 | 9000 | 85 | 77 | 75 | 433 | 0.457 | 20.35 | 197.8 | 25.3 | 36
RV30 | 30 | 9000 | 90 | 77 | 75 | 432.8 | 0.554 | 24.67 | 239.8 | 25.3 | 36
RV30 | 30 | 9000 | 65 | 57 | 85 | 291.1 | 0.661 | 19.79 | 192.4 | 27.7 | 36
RV30 | 30 | 9000 | 70 | 57 | 85 | 291.5 | 0.807 | 24.19 | 235.1 | 27.6 | 36
RV30 | 30 | 9000 | 75 | 57 | 85 | 291.9 | 0.943 | 28.31 | 275.2 | 27.5 | 36
RV30 | 30 | 9000 | 80 | 57 | 85 | 304.3 | 0.972 | 30.42 | 295.7 | 27.5 | 36
RV30 | 30 | 9000 | 85 | 57 | 85 | 321.2 | 0.972 | 32.12 | 312.2 | 27.6 | 36
RV30 | 30 | 9000 | 90 | 57 | 85 | 338.5 | 0.972 | 33.85 | 329 | 27.7 | 36
RV30 | 30 | 9000 | 65 | 62 | 85 | 318.5 | 0.476 | 15.61 | 151.7 | 28 | 36
RV30 | 30 | 9000 | 70 | 62 | 85 | 319.1 | 0.612 | 20.1 | 195.4 | 27.9 | 36
RV30 | 30 | 9000 | 75 | 62 | 85 | 319.8 | 0.739 | 24.3 | 236.2 | 27.8 | 36
RV30 | 30 | 9000 | 80 | 62 | 85 | 320.3 | 0.865 | 28.51 | 277.1 | 27.7 | 36
RV30 | 30 | 9000 | 85 | 62 | 85 | 321.4 | 0.972 | 32.14 | 312.4 | 27.6 | 36
RV30 | 30 | 9000 | 90 | 62 | 85 | 338.7 | 0.972 | 33.87 | 329.2 | 27.7 | 36
RV30 | 30 | 9000 | 70 | 67 | 85 | 349.4 | 0.437 | 15.72 | 152.8 | 28.1 | 36
RV30 | 30 | 9000 | 75 | 67 | 85 | 350.1 | 0.554 | 19.96 | 194 | 28 | 36
RV30 | 30 | 9000 | 80 | 67 | 85 | 350.5 | 0.671 | 24.19 | 235.1 | 28 | 36
RV30 | 30 | 9000 | 85 | 67 | 85 | 349.9 | 0.787 | 28.34 | 275.5 | 27.9 | 36
RV30 | 30 | 9000 | 90 | 67 | 85 | 351.6 | 0.904 | 32.7 | 317.8 | 27.8 | 36
RV30 | 30 | 9000 | 75 | 72 | 85 | 382 | 0.398 | 15.66 | 152.2 | 28.3 | 36
RV30 | 30 | 9000 | 80 | 72 | 85 | 382.5 | 0.505 | 19.89 | 193.3 | 28.2 | 36
RV30 | 30 | 9000 | 85 | 72 | 85 | 382.6 | 0.612 | 24.1 | 234.3 | 28.1 | 36
RV30 | 30 | 9000 | 90 | 72 | 85 | 382.6 | 0.719 | 28.31 | 275.2 | 28.1 | 36
RV30 | 30 | 9000 | 80 | 77 | 85 | 416.7 | 0.369 | 15.83 | 153.9 | 28.4 | 36
RV30 | 30 | 9000 | 85 | 77 | 85 | 417 | 0.466 | 20.01 | 194.5 | 28.3 | 36
RV30 | 30 | 9000 | 90 | 77 | 85 | 416.9 | 0.564 | 24.18 | 235 | 28.2 | 36
RV30 | 30 | 9000 | 65 | 57 | 95 | 278 | 0.671 | 19.18 | 186.4 | 30.6 | 37
RV30 | 30 | 9000 | 70 | 57 | 95 | 278 | 0.817 | 23.35 | 227 | 30.5 | 37
RV30 | 30 | 9000 | 75 | 57 | 95 | 279.3 | 0.952 | 27.37 | 266 | 30.3 | 37
RV30 | 30 | 9000 | 80 | 57 | 95 | 293.4 | 0.972 | 29.34 | 285.2 | 30.4 | 37
RV30 | 30 | 9000 | 85 | 57 | 95 | 310 | 0.972 | 31 | 301.3 | 30.4 | 37
RV30 | 30 | 9000 | 90 | 57 | 95 | 327.2 | 0.972 | 32.72 | 318 | 30.5 | 37
RV30 | 30 | 9000 | 65 | 62 | 95 | 304.2 | 0.476 | 14.91 | 144.9 | 31 | 37
RV30 | 30 | 9000 | 70 | 62 | 95 | 305.1 | 0.612 | 19.22 | 186.8 | 30.9 | 37
RV30 | 30 | 9000 | 75 | 62 | 95 | 305.8 | 0.749 | 23.55 | 228.9 | 30.7 | 37
RV30 | 30 | 9000 | 80 | 62 | 95 | 306.8 | 0.884 | 27.91 | 271.3 | 30.6 | 37
RV30 | 30 | 9000 | 85 | 62 | 95 | 310.4 | 0.972 | 31.04 | 301.7 | 30.5 | 37
RV30 | 30 | 9000 | 90 | 62 | 95 | 327.4 | 0.972 | 32.74 | 318.2 | 30.5 | 37
RV30 | 30 | 9000 | 70 | 67 | 95 | 334 | 0.437 | 15.03 | 146.1 | 31.2 | 37
RV30 | 30 | 9000 | 75 | 67 | 95 | 335 | 0.564 | 19.42 | 188.8 | 31 | 37
RV30 | 30 | 9000 | 80 | 67 | 95 | 335.3 | 0.681 | 23.48 | 228.2 | 30.9 | 37
RV30 | 30 | 9000 | 85 | 67 | 95 | 334.9 | 0.807 | 27.79 | 270.1 | 30.8 | 37
RV30 | 30 | 9000 | 90 | 67 | 95 | 335.3 | 0.923 | 31.85 | 309.6 | 30.7 | 37
RV30 | 30 | 9000 | 75 | 72 | 95 | 365.4 | 0.398 | 14.98 | 145.6 | 31.3 | 37
RV30 | 30 | 9000 | 80 | 72 | 95 | 365.9 | 0.515 | 19.39 | 188.5 | 31.2 | 37
RV30 | 30 | 9000 | 85 | 72 | 95 | 366.3 | 0.622 | 23.45 | 227.9 | 31.1 | 37
RV30 | 30 | 9000 | 90 | 72 | 95 | 366.2 | 0.739 | 27.83 | 270.5 | 31.1 | 37
RV30 | 30 | 9000 | 80 | 77 | 95 | 398.5 | 0.369 | 15.14 | 147.2 | 31.5 | 37
RV30 | 30 | 9000 | 85 | 77 | 95 | 399.2 | 0.466 | 19.16 | 186.2 | 31.4 | 37
RV30 | 30 | 9000 | 90 | 77 | 95 | 399.3 | 0.574 | 23.56 | 229 | 31.4 | 37
RV30 | 30 | 9000 | 65 | 57 | 105 | 264.4 | 0.68 | 18.51 | 179.9 | 33.9 | 37
RV30 | 30 | 9000 | 70 | 57 | 105 | 264.6 | 0.836 | 22.76 | 221.2 | 33.8 | 37
RV30 | 30 | 9000 | 75 | 57 | 105 | 266 | 0.972 | 26.6 | 258.6 | 33.5 | 37
RV30 | 30 | 9000 | 80 | 57 | 105 | 282.2 | 0.972 | 28.22 | 274.3 | 33.6 | 37
RV30 | 30 | 9000 | 85 | 57 | 105 | 298.7 | 0.972 | 29.87 | 290.3 | 33.6 | 37
RV30 | 30 | 9000 | 90 | 57 | 105 | 315.4 | 0.972 | 31.54 | 306.6 | 33.7 | 37
RV30 | 30 | 9000 | 65 | 62 | 105 | 289.5 | 0.486 | 14.48 | 140.7 | 34.4 | 37
RV30 | 30 | 9000 | 70 | 62 | 105 | 290.6 | 0.622 | 18.6 | 180.8 | 34.1 | 37
RV30 | 30 | 9000 | 75 | 62 | 105 | 291.2 | 0.768 | 23 | 223.6 | 34 | 37
RV30 | 30 | 9000 | 80 | 62 | 105 | 292.5 | 0.904 | 27.2 | 264.4 | 33.7 | 37
RV30 | 30 | 9000 | 85 | 62 | 105 | 298.9 | 0.972 | 29.89 | 290.5 | 33.6 | 37
RV30 | 30 | 9000 | 90 | 62 | 105 | 315.6 | 0.972 | 31.55 | 306.7 | 33.7 | 37
RV30 | 30 | 9000 | 70 | 67 | 105 | 318.1 | 0.437 | 14.31 | 139.1 | 34.6 | 37
RV30 | 30 | 9000 | 75 | 67 | 105 | 319.1 | 0.573 | 18.83 | 183 | 34.4 | 37
RV30 | 30 | 9000 | 80 | 67 | 105 | 319.7 | 0.7 | 23.01 | 223.7 | 34.2 | 37
RV30 | 30 | 9000 | 85 | 67 | 105 | 319.5 | 0.826 | 27.16 | 264 | 34 | 37
RV30 | 30 | 9000 | 90 | 67 | 105 | 321.2 | 0.943 | 31.16 | 302.9 | 33.8 | 37
RV30 | 30 | 9000 | 75 | 72 | 105 | 348.4 | 0.398 | 14.28 | 138.8 | 34.6 | 37
RV30 | 30 | 9000 | 80 | 72 | 105 | 348.9 | 0.515 | 18.49 | 179.7 | 34.5 | 37
RV30 | 30 | 9000 | 85 | 72 | 105 | 349.4 | 0.641 | 23.06 | 224.1 | 34.4 | 37
RV30 | 30 | 9000 | 90 | 72 | 105 | 349.3 | 0.758 | 27.24 | 264.8 | 34.3 | 37
RV30 | 30 | 9000 | 80 | 77 | 105 | 380.1 | 0.369 | 14.44 | 140.4 | 34.8 | 37
RV30 | 30 | 9000 | 85 | 77 | 105 | 380.9 | 0.476 | 18.66 | 181.4 | 34.7 | 37
RV30 | 30 | 9000 | 90 | 77 | 105 | 381.2 | 0.583 | 22.87 | 222.3 | 34.6 | 37
RV30 | 30 | 9000 | 65 | 57 | 115 | 249.2 | 0.69 | 17.7 | 172 | 38 | 37
RV30 | 30 | 9000 | 70 | 57 | 115 | 249.8 | 0.855 | 21.99 | 213.7 | 37.7 | 37
RV30 | 30 | 9000 | 75 | 57 | 115 | 253.8 | 0.972 | 25.38 | 246.7 | 37.4 | 37
RV30 | 30 | 9000 | 80 | 57 | 115 | 269.7 | 0.972 | 26.97 | 262.1 | 37.4 | 37
RV30 | 30 | 9000 | 85 | 57 | 115 | 285.8 | 0.972 | 28.58 | 277.8 | 37.5 | 37
RV30 | 30 | 9000 | 90 | 57 | 115 | 302.3 | 0.972 | 30.23 | 293.8 | 37.5 | 37
RV30 | 30 | 9000 | 65 | 62 | 115 | 273.1 | 0.486 | 13.65 | 132.7 | 38.4 | 37
RV30 | 30 | 9000 | 70 | 62 | 115 | 274.3 | 0.632 | 17.83 | 173.3 | 38.1 | 37
RV30 | 30 | 9000 | 75 | 62 | 115 | 274.9 | 0.778 | 22 | 213.8 | 37.9 | 37
RV30 | 30 | 9000 | 80 | 62 | 115 | 275.7 | 0.923 | 26.18 | 254.5 | 37.5 | 37
RV30 | 30 | 9000 | 85 | 62 | 115 | 286 | 0.972 | 28.6 | 278 | 37.5 | 37
RV30 | 30 | 9000 | 90 | 62 | 115 | 302.4 | 0.972 | 30.24 | 293.9 | 37.5 | 37
RV30 | 30 | 9000 | 70 | 67 | 115 | 300.5 | 0.447 | 13.83 | 134.4 | 38.6 | 37
RV30 | 30 | 9000 | 75 | 67 | 115 | 301.7 | 0.583 | 18.1 | 175.9 | 38.2 | 37
RV30 | 30 | 9000 | 80 | 67 | 115 | 302.3 | 0.71 | 22.07 | 214.5 | 38 | 37
RV30 | 30 | 9000 | 85 | 67 | 115 | 303 | 0.846 | 26.36 | 256.2 | 37.8 | 37
RV30 | 30 | 9000 | 90 | 67 | 115 | 302.6 | 0.972 | 30.26 | 294.1 | 37.5 | 37
RV30 | 30 | 9000 | 75 | 72 | 115 | 329.4 | 0.408 | 13.84 | 134.5 | 38.6 | 37
RV30 | 30 | 9000 | 80 | 72 | 115 | 330.3 | 0.525 | 17.83 | 173.3 | 38.4 | 37
RV30 | 30 | 9000 | 85 | 72 | 115 | 330.8 | 0.651 | 22.16 | 215.4 | 38.2 | 37
RV30 | 30 | 9000 | 90 | 72 | 115 | 330.4 | 0.778 | 26.43 | 256.9 | 38 | 37
RV30 | 30 | 9000 | 80 | 77 | 115 | 359.6 | 0.369 | 13.66 | 132.8 | 38.8 | 37
RV30 | 30 | 9000 | 85 | 77 | 115 | 360.9 | 0.486 | 18.05 | 175.4 | 38.5 | 37
RV30 | 30 | 9000 | 90 | 77 | 115 | 361.1 | 0.593 | 22.03 | 214.1 | 38.4 | 37
RV30 | 30 | 9000 | 65 | 57 | 125 | 233.3 | 0.71 | 17.04 | 165.6 | 42.8 | 38
RV30 | 30 | 9000 | 70 | 57 | 125 | 234.6 | 0.875 | 21.11 | 205.2 | 42.1 | 38
RV30 | 30 | 9000 | 75 | 57 | 125 | 240.9 | 0.972 | 24.08 | 234.1 | 41.8 | 38
RV30 | 30 | 9000 | 80 | 57 | 125 | 256.4 | 0.972 | 25.65 | 249.3 | 41.7 | 38
RV30 | 30 | 9000 | 85 | 57 | 125 | 272.3 | 0.972 | 27.23 | 264.7 | 41.7 | 38
RV30 | 30 | 9000 | 90 | 57 | 125 | 288.4 | 0.972 | 28.84 | 280.3 | 41.6 | 38
RV30 | 30 | 9000 | 65 | 62 | 125 | 256.3 | 0.486 | 12.81 | 124.5 | 43 | 38
RV30 | 30 | 9000 | 70 | 62 | 125 | 257.6 | 0.642 | 17.01 | 165.3 | 42.6 | 38
RV30 | 30 | 9000 | 75 | 62 | 125 | 258 | 0.807 | 21.41 | 208.1 | 42.2 | 38
RV30 | 30 | 9000 | 80 | 62 | 125 | 259.5 | 0.952 | 25.42 | 247.1 | 41.7 | 38
RV30 | 30 | 9000 | 85 | 62 | 125 | 272.5 | 0.972 | 27.24 | 264.8 | 41.7 | 38
RV30 | 30 | 9000 | 90 | 62 | 125 | 288.6 | 0.972 | 28.86 | 280.5 | 41.6 | 38
RV30 | 30 | 9000 | 70 | 67 | 125 | 282 | 0.447 | 12.97 | 126.1 | 43.1 | 38
RV30 | 30 | 9000 | 75 | 67 | 125 | 283.4 | 0.593 | 17.28 | 168 | 42.6 | 38
RV30 | 30 | 9000 | 80 | 67 | 125 | 284.1 | 0.729 | 21.31 | 207.1 | 42.3 | 38
RV30 | 30 | 9000 | 85 | 67 | 125 | 285.6 | 0.875 | 25.7 | 249.8 | 41.9 | 38
RV30 | 30 | 9000 | 90 | 67 | 125 | 288.7 | 0.972 | 28.87 | 280.6 | 41.6 | 38
RV30 | 30 | 9000 | 75 | 72 | 125 | 309.4 | 0.408 | 12.99 | 126.3 | 43.4 | 38
RV30 | 30 | 9000 | 80 | 72 | 125 | 310.9 | 0.535 | 17.1 | 166.2 | 42.7 | 38
RV30 | 30 | 9000 | 85 | 72 | 125 | 311.6 | 0.671 | 21.5 | 209 | 42.4 | 38
RV30 | 30 | 9000 | 90 | 72 | 125 | 311.7 | 0.797 | 25.56 | 248.4 | 42.1 | 38
RV30 | 30 | 9000 | 80 | 77 | 125 | 338.6 | 0.369 | 12.86 | 125 | 43 | 38
RV30 | 30 | 9000 | 85 | 77 | 125 | 339.7 | 0.496 | 17.33 | 168.4 | 42.8 | 38
RV30 | 30 | 9000 | 90 | 77 | 125 | 340.3 | 0.612 | 21.44 | 208.4 | 42.5 | 38
RV30 | 30 | 10500 | 65 | 57 | 75 | 312.5 | 0.68 | 18.75 | 212.6 | 26.1 | 36
RV30 | 30 | 10500 | 70 | 57 | 75 | 312.8 | 0.836 | 23.05 | 261.4 | 26.1 | 36
RV30 | 30 | 10500 | 75 | 57 | 75 | 313.8 | 0.972 | 26.9 | 305 | 25.9 | 36
RV30 | 30 | 10500 | 80 | 57 | 75 | 332.2 | 0.972 | 28.47 | 322.9 | 26 | 36
RV30 | 30 | 10500 | 85 | 57 | 75 | 351 | 0.972 | 30.09 | 341.2 | 26 | 36
RV30 | 30 | 10500 | 90 | 57 | 75 | 369.9 | 0.972 | 31.7 | 359.5 | 26 | 36
RV30 | 30 | 10500 | 65 | 62 | 75 | 342.1 | 0.486 | 14.66 | 166.2 | 26.3 | 36
RV30 | 30 | 10500 | 70 | 62 | 75 | 343 | 0.622 | 18.82 | 213.4 | 26.2 | 36
RV30 | 30 | 10500 | 75 | 62 | 75 | 343.7 | 0.758 | 22.97 | 260.5 | 26.2 | 36
RV30 | 30 | 10500 | 80 | 62 | 75 | 344.9 | 0.894 | 27.2 | 308.4 | 26.1 | 36
RV30 | 30 | 10500 | 85 | 62 | 75 | 351.1 | 0.972 | 30.1 | 341.3 | 26.1 | 36
RV30 | 30 | 10500 | 90 | 62 | 75 | 369.9 | 0.972 | 31.7 | 359.5 | 26.1 | 36
RV30 | 30 | 10500 | 70 | 67 | 75 | 374.1 | 0.437 | 14.43 | 163.6 | 26.4 | 36
RV30 | 30 | 10500 | 75 | 67 | 75 | 374.9 | 0.564 | 18.63 | 211.3 | 26.3 | 36
RV30 | 30 | 10500 | 80 | 67 | 75 | 375.3 | 0.7 | 23.16 | 262.6 | 26.3 | 36
RV30 | 30 | 10500 | 85 | 67 | 75 | 375.2 | 0.826 | 27.34 | 310 | 26.2 | 36
RV30 | 30 | 10500 | 90 | 67 | 75 | 376.7 | 0.943 | 31.31 | 355.1 | 26.1 | 36
RV30 | 30 | 10500 | 75 | 72 | 75 | 408.6 | 0.398 | 14.36 | 162.8 | 26.5 | 36
RV30 | 30 | 10500 | 80 | 72 | 75 | 409.3 | 0.515 | 18.59 | 210.8 | 26.4 | 36
RV30 | 30 | 10500 | 85 | 72 | 75 | 409.5 | 0.632 | 22.81 | 258.7 | 26.3 | 36
RV30 | 30 | 10500 | 90 | 72 | 75 | 409.2 | 0.749 | 27.01 | 306.3 | 26.3 | 36
RV30 | 30 | 10500 | 80 | 77 | 75 | 444.1 | 0.369 | 14.46 | 164 | 26.4 | 36
RV30 | 30 | 10500 | 85 | 77 | 75 | 444.9 | 0.476 | 18.69 | 211.9 | 26.3 | 36
RV30 | 30 | 10500 | 90 | 77 | 75 | 444.6 | 0.583 | 22.87 | 259.3 | 26.2 | 36
RV30 | 30 | 10500 | 65 | 57 | 85 | 299.5 | 0.69 | 18.23 | 206.7 | 28.7 | 36
RV30 | 30 | 10500 | 70 | 57 | 85 | 300.2 | 0.845 | 22.38 | 253.8 | 28.6 | 36
RV30 | 30 | 10500 | 75 | 57 | 85 | 303.1 | 0.972 | 25.98 | 294.6 | 28.5 | 36
RV30 | 30 | 10500 | 80 | 57 | 85 | 321.2 | 0.972 | 27.53 | 312.2 | 28.5 | 36
RV30 | 30 | 10500 | 85 | 57 | 85 | 339.8 | 0.972 | 29.12 | 330.2 | 28.6 | 36
RV30 | 30 | 10500 | 90 | 57 | 85 | 358.4 | 0.972 | 30.71 | 348.3 | 28.7 | 36
RV30 | 30 | 10500 | 65 | 62 | 85 | 327.7 | 0.486 | 14.05 | 159.3 | 29.1 | 36
RV30 | 30 | 10500 | 70 | 62 | 85 | 329 | 0.632 | 18.33 | 207.9 | 28.9 | 36
RV30 | 30 | 10500 | 75 | 62 | 85 | 329.5 | 0.778 | 22.59 | 256.2 | 28.8 | 36
RV30 | 30 | 10500 | 80 | 62 | 85 | 330.5 | 0.914 | 26.63 | 302 | 28.7 | 36
RV30 | 30 | 10500 | 85 | 62 | 85 | 339.9 | 0.972 | 29.14 | 330.4 | 28.7 | 36
RV30 | 30 | 10500 | 90 | 62 | 85 | 358.5 | 0.972 | 30.73 | 348.5 | 28.7 | 36
RV30 | 30 | 10500 | 70 | 67 | 85 | 358.8 | 0.437 | 13.84 | 156.9 | 29.2 | 36
RV30 | 30 | 10500 | 75 | 67 | 85 | 359.8 | 0.573 | 18.19 | 206.3 | 29 | 36
RV30 | 30 | 10500 | 80 | 67 | 85 | 360.4 | 0.709 | 22.55 | 255.7 | 29 | 36
RV30 | 30 | 10500 | 85 | 67 | 85 | 360.9 | 0.836 | 26.6 | 301.7 | 28.9 | 36
RV30 | 30 | 10500 | 90 | 67 | 85 | 362.5 | 0.953 | 30.45 | 345.3 | 28.8 | 36
RV30 | 30 | 10500 | 75 | 72 | 85 | 392.4 | 0.399 | 13.79 | 156.4 | 29.3 | 36
RV30 | 30 | 10500 | 80 | 72 | 85 | 393.2 | 0.525 | 18.2 | 206.4 | 29.2 | 36
RV30 | 30 | 10500 | 85 | 72 | 85 | 393.3 | 0.641 | 22.25 | 252.3 | 29.1 | 36
RV30 | 30 | 10500 | 90 | 72 | 85 | 392.6 | 0.768 | 26.58 | 301.4 | 29.1 | 36
RV30 | 30 | 10500 | 80 | 77 | 85 | 427.1 | 0.369 | 13.91 | 157.7 | 29.4 | 36
RV30 | 30 | 10500 | 85 | 77 | 85 | 428.1 | 0.476 | 17.98 | 203.9 | 29.3 | 36
RV30 | 30 | 10500 | 90 | 77 | 85 | 428.1 | 0.593 | 22.38 | 253.8 | 29.2 | 36
RV30 | 30 | 10500 | 65 | 57 | 95 | 285.6 | 0.7 | 17.63 | 199.9 | 31.7 | 37
RV30 | 30 | 10500 | 70 | 57 | 95 | 286.6 | 0.856 | 21.62 | 245.2 | 31.5 | 37
RV30 | 30 | 10500 | 75 | 57 | 95 | 291.5 | 0.972 | 24.98 | 283.3 | 31.3 | 37
RV30 | 30 | 10500 | 80 | 57 | 95 | 309.4 | 0.972 | 26.52 | 300.7 | 31.4 | 37
RV30 | 30 | 10500 | 85 | 57 | 95 | 327.6 | 0.972 | 28.08 | 318.4 | 31.5 | 37
RV30 | 30 | 10500 | 90 | 57 | 95 | 346.1 | 0.972 | 29.66 | 336.4 | 31.6 | 37
RV30 | 30 | 10500 | 65 | 62 | 95 | 312.5 | 0.486 | 13.4 | 151.9 | 32.1 | 37
RV30 | 30 | 10500 | 70 | 62 | 95 | 313.9 | 0.642 | 17.76 | 201.4 | 31.9 | 37
RV30 | 30 | 10500 | 75 | 62 | 95 | 314.1 | 0.787 | 21.81 | 247.3 | 31.8 | 37
RV30 | 30 | 10500 | 80 | 62 | 95 | 315.7 | 0.933 | 25.98 | 294.6 | 31.5 | 37
RV30 | 30 | 10500 | 85 | 62 | 95 | 327.8 | 0.972 | 28.1 | 318.6 | 31.5 | 37
RV30 | 30 | 10500 | 90 | 62 | 95 | 346.3 | 0.972 | 29.68 | 336.6 | 31.7 | 37
RV30 | 30 | 10500 | 70 | 67 | 95 | 342.4 | 0.447 | 13.5 | 153.1 | 32.2 | 37
RV30 | 30 | 10500 | 75 | 67 | 95 | 343.4 | 0.583 | 17.65 | 200.2 | 32.1 | 37
RV30 | 30 | 10500 | 80 | 67 | 95 | 344.2 | 0.719 | 21.83 | 247.6 | 31.9 | 37
RV30 | 30 | 10500 | 85 | 67 | 95 | 345.4 | 0.855 | 26.05 | 295.4 | 31.8 | 37
RV30 | 30 | 10500 | 90 | 67 | 95 | 346.5 | 0.972 | 29.7 | 336.8 | 31.7 | 37
RV30 | 30 | 10500 | 75 | 72 | 95 | 374.9 | 0.408 | 13.49 | 153 | 32.4 | 37
RV30 | 30 | 10500 | 80 | 72 | 95 | 375.5 | 0.534 | 17.7 | 200.7 | 32.2 | 37
RV30 | 30 | 10500 | 85 | 72 | 95 | 376 | 0.661 | 21.91 | 248.5 | 32.1 | 37
RV30 | 30 | 10500 | 90 | 72 | 95 | 375.7 | 0.787 | 26.08 | 295.8 | 32.1 | 37
RV30 | 30 | 10500 | 80 | 77 | 95 | 408.5 | 0.369 | 13.31 | 150.9 | 32.5 | 37
RV30 | 30 | 10500 | 85 | 77 | 95 | 409.7 | 0.486 | 17.56 | 199.1 | 32.5 | 37
RV30 | 30 | 10500 | 90 | 77 | 95 | 409.8 | 0.603 | 21.78 | 247 | 32.4 | 37
RV30 | 30 | 10500 | 65 | 57 | 105 | 271.2 | 0.709 | 16.97 | 192.4 | 35 | 37
RV30 | 30 | 10500 | 70 | 57 | 105 | 272.6 | 0.875 | 21.03 | 238.5 | 34.7 | 37
RV30 | 30 | 10500 | 75 | 57 | 105 | 279.6 | 0.972 | 23.96 | 271.7 | 34.6 | 37
RV30 | 30 | 10500 | 80 | 57 | 105 | 297.2 | 0.972 | 25.48 | 288.9 | 34.7 | 37
RV30 | 30 | 10500 | 85 | 57 | 105 | 315 | 0.972 | 27 | 306.2 | 34.7 | 37
RV30 | 30 | 10500 | 90 | 57 | 105 | 333.1 | 0.972 | 28.55 | 323.8 | 34.8 | 37
RV30 | 30 | 10500 | 65 | 62 | 105 | 296.9 | 0.486 | 12.72 | 144.3 | 35.5 | 37
RV30 | 30 | 10500 | 70 | 62 | 105 | 298.3 | 0.651 | 17.13 | 194.3 | 35.2 | 37
RV30 | 30 | 10500 | 75 | 62 | 105 | 298.7 | 0.806 | 21.24 | 240.9 | 35 | 37
RV30 | 30 | 10500 | 80 | 62 | 105 | 300.7 | 0.952 | 25.26 | 286.4 | 34.7 | 37
RV30 | 30 | 10500 | 85 | 62 | 105 | 315.2 | 0.972 | 27.01 | 306.3 | 34.7 | 37
RV30 | 30 | 10500 | 90 | 62 | 105 | 333.5 | 0.972 | 28.58 | 324.1 | 34.8 | 37
RV30 | 30 | 10500 | 70 | 67 | 105 | 325.3 | 0.447 | 12.82 | 145.4 | 35.7 | 37
RV30 | 30 | 10500 | 75 | 67 | 105 | 326.8 | 0.593 | 17.09 | 193.8 | 35.5 | 37
RV30 | 30 | 10500 | 80 | 67 | 105 | 327.6 | 0.739 | 21.34 | 242 | 35.2 | 37
RV30 | 30 | 10500 | 85 | 67 | 105 | 329 | 0.875 | 25.38 | 287.8 | 35 | 37
RV30 | 30 | 10500 | 90 | 67 | 105 | 333.7 | 0.972 | 28.6 | 324.3 | 34.8 | 37
RV30 | 30 | 10500 | 75 | 72 | 105 | 356.6 | 0.408 | 12.84 | 145.6 | 35.8 | 37
RV30 | 30 | 10500 | 80 | 72 | 105 | 357.5 | 0.544 | 17.16 | 194.6 | 35.6 | 37
RV30 | 30 | 10500 | 85 | 72 | 105 | 358.3 | 0.671 | 21.19 | 240.3 | 35.4 | 37
RV30 | 30 | 10500 | 90 | 72 | 105 | 358.7 | 0.807 | 25.51 | 289.3 | 35.2 | 37
RV30 | 30 | 10500 | 80 | 77 | 105 | 389 | 0.369 | 12.67 | 143.7 | 35.9 | 37
RV30 | 30 | 10500 | 85 | 77 | 105 | 390.1 | 0.496 | 17.05 | 193.4 | 35.7 | 37
RV30 | 30 | 10500 | 90 | 77 | 105 | 391 | 0.612 | 21.11 | 239.4 | 35.6 | 37
RV30 | 30 | 10500 | 65 | 57 | 115 | 255.2 | 0.719 | 16.19 | 183.6 | 39.1 | 38
RV30 | 30 | 10500 | 70 | 57 | 115 | 256.9 | 0.904 | 20.48 | 232.2 | 38.5 | 38
RV30 | 30 | 10500 | 75 | 57 | 115 | 266.3 | 0.972 | 22.82 | 258.8 | 38.5 | 38
RV30 | 30 | 10500 | 80 | 57 | 115 | 283.4 | 0.972 | 24.29 | 275.5 | 38.5 | 38
RV30 | 30 | 10500 | 85 | 57 | 115 | 300.9 | 0.972 | 25.79 | 292.5 | 38.5 | 38
RV30 | 30 | 10500 | 90 | 57 | 115 | 318.6 | 0.972 | 27.31 | 309.7 | 38.5 | 38
RV30 | 30 | 10500 | 65 | 62 | 115 | 279.6 | 0.496 | 12.22 | 138.6 | 39.6 | 38
RV30 | 30 | 10500 | 70 | 62 | 115 | 281.2 | 0.661 | 16.39 | 185.9 | 39.2 | 38
RV30 | 30 | 10500 | 75 | 62 | 115 | 281.9 | 0.826 | 20.54 | 232.9 | 38.9 | 38
RV30 | 30 | 10500 | 80 | 62 | 115 | 283.5 | 0.972 | 24.3 | 275.6 | 38.5 | 38
RV30 | 30 | 10500 | 85 | 62 | 115 | 301.1 | 0.972 | 25.8 | 292.6 | 38.5 | 38
RV30 | 30 | 10500 | 90 | 62 | 115 | 319.2 | 0.972 | 27.36 | 310.3 | 38.5 | 38
RV30 | 30 | 10500 | 70 | 67 | 115 | 306.8 | 0.447 | 12.1 | 137.2 | 39.7 | 38
RV30 | 30 | 10500 | 75 | 67 | 115 | 308.4 | 0.602 | 16.38 | 185.8 | 39.3 | 38
RV30 | 30 | 10500 | 80 | 67 | 115 | 308.8 | 0.758 | 20.64 | 234.1 | 39 | 38
RV30 | 30 | 10500 | 85 | 67 | 115 | 310.2 | 0.904 | 24.73 | 280.4 | 38.6 | 38
RV30 | 30 | 10500 | 90 | 67 | 115 | 319.2 | 0.972 | 27.36 | 310.3 | 38.6 | 38
RV30 | 30 | 10500 | 75 | 72 | 115 | 336.4 | 0.408 | 12.11 | 137.3 | 39.8 | 38
RV30 | 30 | 10500 | 80 | 72 | 115 | 337.8 | 0.554 | 16.51 | 187.2 | 39.4 | 38
RV30 | 30 | 10500 | 85 | 72 | 115 | 338.5 | 0.69 | 20.6 | 233.6 | 39.2 | 38
RV30 | 30 | 10500 | 90 | 72 | 115 | 339.8 | 0.826 | 24.75 | 280.7 | 38.9 | 38
RV30 | 30 | 10500 | 80 | 77 | 115 | 367.4 | 0.379 | 12.28 | 139.3 | 40 | 38
RV30 | 30 | 10500 | 85 | 77 | 115 | 368.9 | 0.505 | 16.44 | 186.4 | 39.6 | 38
RV30 | 30 | 10500 | 90 | 77 | 115 | 369.8 | 0.632 | 20.6 | 233.6 | 39.4 | 38
RV30 | 30 | 10500 | 65 | 57 | 125 | 238.7 | 0.739 | 15.55 | 176.3 | 43.9 | 38
RV30 | 30 | 10500 | 70 | 57 | 125 | 240 | 0.923 | 19.54 | 221.6 | 43 | 38
RV30 | 30 | 10500 | 75 | 57 | 125 | 252.3 | 0.972 | 21.62 | 245.2 | 42.9 | 38
RV30 | 30 | 10500 | 80 | 57 | 125 | 269 | 0.972 | 23.05 | 261.4 | 42.8 | 38
RV30 | 30 | 10500 | 85 | 57 | 125 | 286.1 | 0.972 | 24.52 | 278.1 | 42.7 | 38
RV30 | 30 | 10500 | 90 | 57 | 125 | 303.5 | 0.972 | 26.01 | 295 | 42.7 | 38
RV30 | 30 | 10500 | 65 | 62 | 125 | 261.5 | 0.496 | 11.43 | 129.6 | 44.5 | 38
RV30 | 30 | 10500 | 70 | 62 | 125 | 263.5 | 0.671 | 15.58 | 176.7 | 43.6 | 38
RV30 | 30 | 10500 | 75 | 62 | 125 | 264.9 | 0.846 | 19.75 | 224 | 43.2 | 38
RV30 | 30 | 10500 | 80 | 62 | 125 | 269.2 | 0.972 | 23.07 | 261.6 | 42.8 | 38
RV30 | 30 | 10500 | 85 | 62 | 125 | 286.3 | 0.972 | 24.54 | 278.3 | 42.7 | 38
RV30 | 30 | 10500 | 90 | 62 | 125 | 304.1 | 0.972 | 26.07 | 295.6 | 42.7 | 38
RV30 | 30 | 10500 | 70 | 67 | 125 | 287.6 | 0.457 | 11.59 | 131.4 | 44.3 | 38
RV30 | 30 | 10500 | 75 | 67 | 125 | 289.5 | 0.612 | 15.63 | 177.2 | 43.7 | 38
RV30 | 30 | 10500 | 80 | 67 | 125 | 290 | 0.778 | 19.89 | 225.5 | 43.3 | 38
RV30 | 30 | 10500 | 85 | 67 | 125 | 292 | 0.933 | 24.03 | 272.5 | 42.7 | 38
RV30 | 30 | 10500 | 90 | 67 | 125 | 304.3 | 0.972 | 26.08 | 295.7 | 42.7 | 38
RV30 | 30 | 10500 | 75 | 72 | 125 | 315.3 | 0.418 | 11.62 | 131.8 | 44.6 | 38
RV30 | 30 | 10500 | 80 | 72 | 125 | 317.1 | 0.564 | 15.76 | 178.7 | 43.6 | 38
RV30 | 30 | 10500 | 85 | 72 | 125 | 317.9 | 0.71 | 19.89 | 225.6 | 43.4 | 38
RV30 | 30 | 10500 | 90 | 72 | 125 | 319.8 | 0.855 | 24.12 | 273.5 | 43 | 38
RV30 | 30 | 10500 | 80 | 77 | 125 | 345.1 | 0.379 | 11.53 | 130.8 | 44.4 | 38
RV30 | 30 | 10500 | 85 | 77 | 125 | 346.7 | 0.515 | 15.75 | 178.6 | 43.9 | 38
RV30 | 30 | 10500 | 90 | 77 | 125 | 348.1 | 0.651 | 19.99 | 226.7 | 43.5 | 38
RV30 | 30 | 12000 | 65 | 57 | 75 | 320.5 | 0.7 | 17.31 | 224.3 | 27.4 | 36
RV30 | 30 | 12000 | 70 | 57 | 75 | 321.8 | 0.865 | 21.48 | 278.4 | 27.2 | 36
RV30 | 30 | 12000 | 75 | 57 | 75 | 327.7 | 0.972 | 24.58 | 318.5 | 27.2 | 36
RV30 | 30 | 12000 | 80 | 57 | 75 | 347.3 | 0.972 | 26.05 | 337.6 | 27.2 | 36
RV30 | 30 | 12000 | 85 | 57 | 75 | 367.3 | 0.972 | 27.55 | 357 | 27.3 | 36
RV30 | 30 | 12000 | 90 | 57 | 75 | 387.5 | 0.972 | 29.06 | 376.6 | 27.2 | 36
RV30 | 30 | 12000 | 65 | 62 | 75 | 349.5 | 0.486 | 13.1 | 169.8 | 27.5 | 36
RV30 | 30 | 12000 | 70 | 62 | 75 | 350.7 | 0.642 | 17.36 | 225 | 27.4 | 36
RV30 | 30 | 12000 | 75 | 62 | 75 | 350.6 | 0.797 | 21.56 | 279.4 | 27.4 | 36
RV30 | 30 | 12000 | 80 | 62 | 75 | 353.1 | 0.943 | 25.69 | 332.9 | 27.3 | 36
RV30 | 30 | 12000 | 85 | 62 | 75 | 367.5 | 0.972 | 27.56 | 357.2 | 27.3 | 36
RV30 | 30 | 12000 | 90 | 62 | 75 | 387.7 | 0.972 | 29.07 | 376.8 | 27.2 | 36
RV30 | 30 | 12000 | 70 | 67 | 75 | 382.5 | 0.447 | 13.19 | 171 | 27.6 | 36
RV30 | 30 | 12000 | 75 | 67 | 75 | 383.7 | 0.583 | 17.27 | 223.8 | 27.6 | 36
RV30 | 30 | 12000 | 80 | 67 | 75 | 384 | 0.729 | 21.6 | 279.9 | 27.5 | 36
RV30 | 30 | 12000 | 85 | 67 | 75 | 385.3 | 0.865 | 25.72 | 333.3 | 27.4 | 36
RV30 | 30 | 12000 | 90 | 67 | 75 | 387.9 | 0.972 | 29.09 | 377 | 27.3 | 36
RV30 | 30 | 12000 | 75 | 72 | 75 | 417.3 | 0.408 | 13.14 | 170.3 | 27.7 | 36
RV30 | 30 | 12000 | 80 | 72 | 75 | 418 | 0.534 | 17.24 | 223.4 | 27.6 | 36
RV30 | 30 | 12000 | 85 | 72 | 75 | 418.5 | 0.661 | 21.34 | 276.6 | 27.5 | 36
RV30 | 30 | 12000 | 90 | 72 | 75 | 418.1 | 0.797 | 25.71 | 333.2 | 27.4 | 36
RV30 | 30 | 12000 | 80 | 77 | 75 | 453 | 0.369 | 12.91 | 167.3 | 27.6 | 36
RV30 | 30 | 12000 | 85 | 77 | 75 | 453.8 | 0.486 | 17.01 | 220.5 | 27.4 | 36
RV30 | 30 | 12000 | 90 | 77 | 75 | 453.8 | 0.612 | 21.44 | 277.9 | 27.4 | 36
RV30 | 30 | 12000 | 65 | 57 | 85 | 306.9 | 0.709 | 16.8 | 217.7 | 30 | 36
RV30 | 30 | 12000 | 70 | 57 | 85 | 308.3 | 0.885 | 21.04 | 272.7 | 29.8 | 36
RV30 | 30 | 12000 | 75 | 57 | 85 | 316.2 | 0.972 | 23.72 | 307.4 | 29.7 | 36
RV30 | 30 | 12000 | 80 | 57 | 85 | 335.6 | 0.972 | 25.17 | 326.2 | 29.8 | 36
RV30 | 30 | 12000 | 85 | 57 | 85 | 355.2 | 0.972 | 26.64 | 345.3 | 29.9 | 36
RV30 | 30 | 12000 | 90 | 57 | 85 | 375.3 | 0.972 | 28.15 | 364.8 | 30 | 36
RV30 | 30 | 12000 | 65 | 62 | 85 | 334.7 | 0.486 | 12.55 | 162.7 | 30.3 | 36
RV30 | 30 | 12000 | 70 | 62 | 85 | 336 | 0.651 | 16.88 | 218.8 | 30.1 | 36
RV30 | 30 | 12000 | 75 | 62 | 85 | 336.2 | 0.807 | 20.93 | 271.2 | 30 | 36
RV30 | 30 | 12000 | 80 | 62 | 85 | 339 | 0.953 | 24.92 | 322.9 | 29.9 | 36
RV30 | 30 | 12000 | 85 | 62 | 85 | 355.4 | 0.972 | 26.65 | 345.4 | 29.9 | 36
RV30 | 30 | 12000 | 90 | 62 | 85 | 375.5 | 0.972 | 28.16 | 365 | 30 | 36
RV30 | 30 | 12000 | 70 | 67 | 85 | 366.7 | 0.447 | 12.65 | 163.9 | 30.4 | 36
RV30 | 30 | 12000 | 75 | 67 | 85 | 367.9 | 0.593 | 16.83 | 218.1 | 30.3 | 36
RV30 | 30 | 12000 | 80 | 67 | 85 | 368.4 | 0.739 | 21 | 272.1 | 30.2 | 36
RV30 | 30 | 12000 | 85 | 67 | 85 | 369.9 | 0.885 | 25.25 | 327.2 | 30.1 | 36
RV30 | 30 | 12000 | 90 | 67 | 85 | 375.7 | 0.972 | 28.17 | 365.1 | 30 | 36
RV30 | 30 | 12000 | 75 | 72 | 85 | 400.1 | 0.408 | 12.6 | 163.3 | 30.5 | 36
RV30 | 30 | 12000 | 80 | 72 | 85 | 401.4 | 0.544 | 16.86 | 218.5 | 30.4 | 36
RV30 | 30 | 12000 | 85 | 72 | 85 | 402 | 0.68 | 21.1 | 273.5 | 30.3 | 36
RV30 | 30 | 12000 | 90 | 72 | 85 | 402.2 | 0.807 | 25.04 | 324.5 | 30.3 | 36
RV30 | 30 | 12000 | 80 | 77 | 85 | 435.1 | 0.369 | 12.4 | 160.7 | 30.6 | 36
RV30 | 30 | 12000 | 85 | 77 | 85 | 436.3 | 0.496 | 16.69 | 216.3 | 30.5 | 36
RV30 | 30 | 12000 | 90 | 77 | 85 | 436.6 | 0.622 | 20.96 | 271.6 | 30.4 | 36
RV30 | 30 | 12000 | 65 | 57 | 95 | 292.2 | 0.719 | 16.22 | 210.2 | 33 | 37
RV30 | 30 | 12000 | 70 | 57 | 95 | 293.8 | 0.904 | 20.49 | 265.6 | 32.7 | 37
RV30 | 30 | 12000 | 75 | 57 | 95 | 303.9 | 0.972 | 22.79 | 295.4 | 32.7 | 37
RV30 | 30 | 12000 | 80 | 57 | 95 | 323 | 0.972 | 24.22 | 313.9 | 32.7 | 37
RV30 | 30 | 12000 | 85 | 57 | 95 | 342.4 | 0.972 | 25.68 | 332.8 | 32.8 | 37
RV30 | 30 | 12000 | 90 | 57 | 95 | 361.9 | 0.972 | 27.15 | 351.8 | 33 | 37
RV30 | 30 | 12000 | 65 | 62 | 95 | 318.8 | 0.496 | 12.19 | 158 | 33.4 | 37
RV30 | 30 | 12000 | 70 | 62 | 95 | 320.1 | 0.661 | 16.33 | 211.6 | 33.2 | 37
RV30 | 30 | 12000 | 75 | 62 | 95 | 321 | 0.826 | 20.46 | 265.2 | 33 | 37
RV30 | 30 | 12000 | 80 | 62 | 95 | 323.1 | 0.972 | 24.24 | 314.1 | 32.8 | 37
RV30 | 30 | 12000 | 85 | 62 | 95 | 342.5 | 0.972 | 25.69 | 332.9 | 32.8 | 37
RV30 | 30 | 12000 | 90 | 62 | 95 | 362.1 | 0.972 | 27.16 | 352 | 33 | 37
RV30 | 30 | 12000 | 70 | 67 | 95 | 349.5 | 0.447 | 12.06 | 156.3 | 33.6 | 37
RV30 | 30 | 12000 | 75 | 67 | 95 | 351 | 0.603 | 16.32 | 211.5 | 33.3 | 37
RV30 | 30 | 12000 | 80 | 67 | 95 | 351.3 | 0.758 | 20.55 | 266.3 | 33.2 | 37
RV30 | 30 | 12000 | 85 | 67 | 95 | 352.4 | 0.904 | 24.58 | 318.6 | 33 | 37
RV30 | 30 | 12000 | 90 | 67 | 95 | 362.3 | 0.972 | 27.17 | 352.1 | 33 | 37
RV30 | 30 | 12000 | 75 | 72 | 95 | 381.9 | 0.408 | 12.03 | 155.9 | 33.7 | 37
RV30 | 30 | 12000 | 80 | 72 | 95 | 383.4 | 0.554 | 16.39 | 212.4 | 33.5 | 37
RV30 | 30 | 12000 | 85 | 72 | 95 | 384 | 0.69 | 20.45 | 265 | 33.4 | 37
RV30 | 30 | 12000 | 90 | 72 | 95 | 384.8 | 0.826 | 24.53 | 317.9 | 33.3 | 37
RV30 | 30 | 12000 | 80 | 77 | 95 | 415.7 | 0.379 | 12.16 | 157.6 | 33.8 | 37
RV30 | 30 | 12000 | 85 | 77 | 95 | 417 | 0.506 | 16.27 | 210.8 | 33.7 | 37
RV30 | 30 | 12000 | 90 | 77 | 95 | 417.3 | 0.632 | 20.34 | 263.6 | 33.6 | 37
RV30 | 30 | 12000 | 65 | 57 | 105 | 277.2 | 0.729 | 15.59 | 202.1 | 36.3 | 37
RV30 | 30 | 12000 | 70 | 57 | 105 | 278.4 | 0.923 | 19.83 | 257 | 35.9 | 37
RV30 | 30 | 12000 | 75 | 57 | 105 | 291.2 | 0.972 | 21.84 | 283 | 35.9 | 37
RV30 | 30 | 12000 | 80 | 57 | 105 | 309.8 | 0.972 | 23.23 | 301.1 | 36 | 37
RV30 | 30 | 12000 | 85 | 57 | 105 | 328.8 | 0.972 | 24.66 | 319.6 | 36.1 | 37
RV30 | 30 | 12000 | 90 | 57 | 105 | 348.1 | 0.972 | 26.11 | 338.4 | 36.1 | 37
RV30 | 30 | 12000 | 65 | 62 | 105 | 302.3 | 0.496 | 11.56 | 149.8 | 36.8 | 37
RV30 | 30 | 12000 | 70 | 62 | 105 | 303.8 | 0.671 | 15.73 | 203.8 | 36.5 | 37
RV30 | 30 | 12000 | 75 | 62 | 105 | 305.6 | 0.846 | 19.94 | 258.4 | 36.2 | 37
RV30 | 30 | 12000 | 80 | 62 | 105 | 309.9 | 0.972 | 23.24 | 301.2 | 36 | 37
RV30 | 30 | 12000 | 85 | 62 | 105 | 329 | 0.972 | 24.68 | 319.8 | 36.1 | 37
RV30 | 30 | 12000 | 90 | 62 | 105 | 348.4 | 0.972 | 26.13 | 338.6 | 36.1 | 37
RV30 | 30 | 12000 | 70 | 67 | 105 | 331.9 | 0.457 | 11.7 | 151.6 | 36.9 | 37
RV30 | 30 | 12000 | 75 | 67 | 105 | 333.6 | 0.612 | 15.76 | 204.3 | 36.7 | 37
RV30 | 30 | 12000 | 80 | 67 | 105 | 333.8 | 0.777 | 20.02 | 259.5 | 36.5 | 37
RV30 | 30 | 12000 | 85 | 67 | 105 | 336 | 0.923 | 23.94 | 310.2 | 36.1 | 37
RV30 | 30 | 12000 | 90 | 67 | 105 | 348.5 | 0.972 | 26.14 | 338.8 | 36.1 | 37
RV30 | 30 | 12000 | 75 | 72 | 105 | 363.2 | 0.408 | 11.44 | 148.2 | 37.1 | 37
RV30 | 30 | 12000 | 80 | 72 | 105 | 364.9 | 0.564 | 15.87 | 205.7 | 36.8 | 37
RV30 | 30 | 12000 | 85 | 72 | 105 | 365.4 | 0.71 | 20.01 | 259.3 | 36.6 | 37
RV30 | 30 | 12000 | 90 | 72 | 105 | 366.7 | 0.846 | 23.93 | 310.1 | 36.4 | 37
RV30 | 30 | 12000 | 80 | 77 | 105 | 395.3 | 0.379 | 11.56 | 149.8 | 37.3 | 37
RV30 | 30 | 12000 | 85 | 77 | 105 | 397 | 0.515 | 15.78 | 204.5 | 37 | 37
RV30 | 30 | 12000 | 90 | 77 | 105 | 397.4 | 0.651 | 19.97 | 258.8 | 36.8 | 37
RV30 | 30 | 12000 | 65 | 57 | 115 | 260.7 | 0.748 | 15.05 | 195.1 | 40.3 | 38
RV30 | 30 | 12000 | 70 | 57 | 115 | 262.3 | 0.943 | 19.08 | 247.3 | 39.8 | 38
RV30 | 30 | 12000 | 75 | 57 | 115 | 276.9 | 0.972 | 20.76 | 269.1 | 39.8 | 38
RV30 | 30 | 12000 | 80 | 57 | 115 | 295.3 | 0.972 | 22.15 | 287 | 39.8 | 38
RV30 | 30 | 12000 | 85 | 57 | 115 | 314 | 0.972 | 23.55 | 305.2 | 39.9 | 38
RV30 | 30 | 12000 | 90 | 57 | 115 | 332.7 | 0.972 | 24.95 | 323.4 | 39.9 | 38
RV30 | 30 | 12000 | 65 | 62 | 115 | 284.3 | 0.496 | 10.87 | 140.9 | 40.8 | 38
RV30 | 30 | 12000 | 70 | 62 | 115 | 286.2 | 0.681 | 15.03 | 194.8 | 40.5 | 38
RV30 | 30 | 12000 | 75 | 62 | 115 | 288.2 | 0.865 | 19.24 | 249.3 | 40 | 38
RV30 | 30 | 12000 | 80 | 62 | 115 | 295.2 | 0.972 | 22.14 | 286.9 | 39.8 | 38
RV30 | 30 | 12000 | 85 | 62 | 115 | 314 | 0.972 | 23.55 | 305.2 | 39.8 | 38
RV30 | 30 | 12000 | 90 | 62 | 115 | 332.9 | 0.972 | 24.96 | 323.5 | 39.9 | 38
RV30 | 30 | 12000 | 70 | 67 | 115 | 312.6 | 0.457 | 11.02 | 142.8 | 41 | 38
RV30 | 30 | 12000 | 75 | 67 | 115 | 314.5 | 0.622 | 15.09 | 195.6 | 40.6 | 38
RV30 | 30 | 12000 | 80 | 67 | 115 | 315.3 | 0.797 | 19.39 | 251.3 | 40.2 | 38
RV30 | 30 | 12000 | 85 | 67 | 115 | 317.4 | 0.953 | 23.33 | 302.4 | 39.8 | 38
RV30 | 30 | 12000 | 90 | 67 | 115 | 333 | 0.972 | 24.98 | 323.7 | 39.9 | 38
RV30 | 30 | 12000 | 75 | 72 | 115 | 342.3 | 0.418 | 11.03 | 143 | 41.1 | 38
RV30 | 30 | 12000 | 80 | 72 | 115 | 344 | 0.573 | 15.22 | 197.2 | 40.8 | 38
RV30 | 30 | 12000 | 85 | 72 | 115 | 344.6 | 0.729 | 19.38 | 251.2 | 40.5 | 38
RV30 | 30 | 12000 | 90 | 72 | 115 | 346.3 | 0.875 | 23.38 | 303 | 40.1 | 38
RV30 | 30 | 12000 | 80 | 77 | 115 | 373 | 0.379 | 10.91 | 141.4 | 41.3 | 38
RV30 | 30 | 12000 | 85 | 77 | 115 | 374.8 | 0.525 | 15.18 | 196.7 | 40.9 | 38
RV30 | 30 | 12000 | 90 | 77 | 115 | 375.4 | 0.671 | 19.43 | 251.8 | 40.6 | 38
RV30 | 30 | 12000 | 65 | 57 | 125 | 243.1 | 0.768 | 14.4 | 186.6 | 45.3 | 38
RV30 | 30 | 12000 | 70 | 57 | 125 | 244.8 | 0.972 | 18.36 | 237.9 | 44.3 | 38
RV30 | 30 | 12000 | 75 | 57 | 125 | 262.2 | 0.972 | 19.67 | 254.9 | 44.1 | 38
RV30 | 30 | 12000 | 80 | 57 | 125 | 279.8 | 0.972 | 20.99 | 272 | 44.1 | 38
RV30 | 30 | 12000 | 85 | 57 | 125 | 298.2 | 0.972 | 22.36 | 289.8 | 44 | 38
RV30 | 30 | 12000 | 90 | 57 | 125 | 316.5 | 0.972 | 23.74 | 307.7 | 44 | 38
RV30 | 30 | 12000 | 65 | 62 | 125 | 265.5 | 0.505 | 10.35 | 134.2 | 45.9 | 38
RV30 | 30 | 12000 | 70 | 62 | 125 | 267.9 | 0.7 | 14.46 | 187.4 | 45 | 38
RV30 | 30 | 12000 | 75 | 62 | 125 | 269.6 | 0.894 | 18.6 | 241.1 | 44.3 | 38
RV30 | 30 | 12000 | 80 | 62 | 125 | 280.1 | 0.972 | 21.01 | 272.3 | 44.1 | 38
RV30 | 30 | 12000 | 85 | 62 | 125 | 298.3 | 0.972 | 22.37 | 289.9 | 44 | 38
RV30 | 30 | 12000 | 90 | 62 | 125 | 316.6 | 0.972 | 23.75 | 307.8 | 44 | 38
RV30 | 30 | 12000 | 70 | 67 | 125 | 292.5 | 0.457 | 10.31 | 133.6 | 45.7 | 38
RV30 | 30 | 12000 | 75 | 67 | 125 | 294.6 | 0.642 | 14.58 | 189 | 45 | 38
RV30 | 30 | 12000 | 80 | 67 | 125 | 296.3 | 0.816 | 18.67 | 241.9 | 44.5 | 38
RV30 | 30 | 12000 | 85 | 67 | 125 | 298.4 | 0.972 | 22.38 | 290 | 44 | 38
RV30 | 30 | 12000 | 90 | 67 | 125 | 316.8 | 0.972 | 23.76 | 307.9 | 44 | 38
RV30 | 30 | 12000 | 75 | 72 | 125 | 320.8 | 0.418 | 10.35 | 134.1 | 45.7 | 38
RV30 | 30 | 12000 | 80 | 72 | 125 | 322.9 | 0.583 | 14.53 | 188.3 | 45 | 38
RV30 | 30 | 12000 | 85 | 72 | 125 | 323.5 | 0.748 | 18.68 | 242.1 | 44.6 | 38
RV30 | 30 | 12000 | 90 | 72 | 125 | 325 | 0.914 | 22.92 | 297 | 44.2 | 38
RV30 | 30 | 12000 | 80 | 77 | 125 | 349.8 | 0.389 | 10.49 | 136 | 45.8 | 38
RV30 | 30 | 12000 | 85 | 77 | 125 | 351.7 | 0.535 | 14.51 | 188 | 45.1 | 38
RV30 | 30 | 12000 | 90 | 77 | 125 | 352.6 | 0.69 | 18.77 | 243.3 | 44.9 | 38
RV30 | 30 | 13500 | 65 | 57 | 75 | 326.4 | 0.719 | 16.1 | 234.8 | 28.7 | 36
RV30 | 30 | 13500 | 70 | 57 | 75 | 328.1 | 0.904 | 20.34 | 296.6 | 28.6 | 36
RV30 | 30 | 13500 | 75 | 57 | 75 | 339.4 | 0.972 | 22.63 | 329.9 | 28.6 | 36
RV30 | 30 | 13500 | 80 | 57 | 75 | 360.1 | 0.972 | 24.01 | 350 | 28.6 | 36
RV30 | 30 | 13500 | 85 | 57 | 75 | 381.3 | 0.972 | 25.42 | 370.6 | 28.6 | 36
RV30 | 30 | 13500 | 90 | 57 | 75 | 402.5 | 0.972 | 26.84 | 391.3 | 28.5 | 36
RV30 | 30 | 13500 | 65 | 62 | 75 | 355.5 | 0.496 | 12.09 | 176.2 | 28.9 | 36
RV30 | 30 | 13500 | 70 | 62 | 75 | 357 | 0.661 | 16.19 | 236 | 28.8 | 36
RV30 | 30 | 13500 | 75 | 62 | 75 | 357.9 | 0.826 | 20.28 | 295.7 | 28.7 | 36
RV30 | 30 | 13500 | 80 | 62 | 75 | 360.3 | 0.972 | 24.02 | 350.2 | 28.6 | 36
RV30 | 30 | 13500 | 85 | 62 | 75 | 381.5 | 0.972 | 25.43 | 370.8 | 28.6 | 36
RV30 | 30 | 13500 | 90 | 62 | 75 | 402.7 | 0.972 | 26.84 | 391.4 | 28.6 | 36
RV30 | 30 | 13500 | 70 | 67 | 75 | 388.6 | 0.447 | 11.92 | 173.8 | 29 | 36
RV30 | 30 | 13500 | 75 | 67 | 75 | 390 | 0.603 | 16.12 | 235 | 28.9 | 36
RV30 | 30 | 13500 | 80 | 67 | 75 | 390.2 | 0.758 | 20.29 | 295.8 | 28.8 | 36
RV30 | 30 | 13500 | 85 | 67 | 75 | 391.6 | 0.904 | 24.28 | 354 | 28.7 | 36
RV30 | 30 | 13500 | 90 | 67 | 75 | 402.9 | 0.972 | 26.86 | 391.6 | 28.6 | 36
RV30 | 30 | 13500 | 75 | 72 | 75 | 423.7 | 0.408 | 11.87 | 173 | 29 | 36
RV30 | 30 | 13500 | 80 | 72 | 75 | 424.9 | 0.554 | 16.15 | 235.4 | 28.9 | 36
RV30 | 30 | 13500 | 85 | 72 | 75 | 425.3 | 0.7 | 20.41 | 297.6 | 28.8 | 36
RV30 | 30 | 13500 | 90 | 72 | 75 | 426 | 0.836 | 24.42 | 356.1 | 28.7 | 36
RV30 | 30 | 13500 | 80 | 77 | 75 | 459.8 | 0.379 | 11.95 | 174.3 | 28.9 | 36
RV30 | 30 | 13500 | 85 | 77 | 75 | 461.2 | 0.505 | 15.99 | 233.1 | 28.8 | 36
RV30 | 30 | 13500 | 90 | 77 | 75 | 461.5 | 0.641 | 20.3 | 296 | 28.7 | 36
RV30 | 30 | 13500 | 65 | 57 | 85 | 312.2 | 0.729 | 15.61 | 227.6 | 31.4 | 36
RV30 | 30 | 13500 | 70 | 57 | 85 | 313.4 | 0.923 | 19.85 | 289.4 | 31.2 | 36
RV30 | 30 | 13500 | 75 | 57 | 85 | 327.5 | 0.972 | 21.83 | 318.3 | 31.1 | 36
RV30 | 30 | 13500 | 80 | 57 | 85 | 347.9 | 0.972 | 23.19 | 338.1 | 31.3 | 36
RV30 | 30 | 13500 | 85 | 57 | 85 | 368.7 | 0.972 | 24.57 | 358.3 | 31.3 | 36
RV30 | 30 | 13500 | 90 | 57 | 85 | 389.7 | 0.972 | 25.98 | 378.8 | 31.4 | 36
RV30 | 30 | 13500 | 65 | 62 | 85 | 340.2 | 0.496 | 11.56 | 168.6 | 31.7 | 36
RV30 | 30 | 13500 | 70 | 62 | 85 | 341.9 | 0.671 | 15.73 | 229.3 | 31.5 | 36
RV30 | 30 | 13500 | 75 | 62 | 85 | 343.4 | 0.845 | 19.91 | 290.3 | 31.4 | 36
RV30 | 30 | 13500 | 80 | 62 | 85 | 348 | 0.972 | 23.2 | 338.3 | 31.3 | 36
RV30 | 30 | 13500 | 85 | 62 | 85 | 368.8 | 0.972 | 24.59 | 358.5 | 31.3 | 36
RV30 | 30 | 13500 | 90 | 62 | 85 | 389.9 | 0.972 | 25.99 | 379 | 31.4 | 36
RV30 | 30 | 13500 | 70 | 67 | 85 | 372.2 | 0.457 | 11.66 | 170 | 31.8 | 36
RV30 | 30 | 13500 | 75 | 67 | 85 | 373.8 | 0.612 | 15.7 | 228.9 | 31.6 | 36
RV30 | 30 | 13500 | 80 | 67 | 85 | 373.9 | 0.778 | 19.95 | 290.8 | 31.6 | 36
RV30 | 30 | 13500 | 85 | 67 | 85 | 376.3 | 0.923 | 23.83 | 347.5 | 31.4 | 36
RV30 | 30 | 13500 | 90 | 67 | 85 | 390 | 0.972 | 25.99 | 379 | 31.4 | 36
RV30 | 30 | 13500 | 75 | 72 | 85 | 406.3 | 0.418 | 11.65 | 169.8 | 31.9 | 36
RV30 | 30 | 13500 | 80 | 72 | 85 | 407.8 | 0.564 | 15.77 | 229.9 | 31.8 | 36
RV30 | 30 | 13500 | 85 | 72 | 85 | 408.2 | 0.709 | 19.86 | 289.6 | 31.7 | 36
RV30 | 30 | 13500 | 90 | 72 | 85 | 409.6 | 0.845 | 23.75 | 346.3 | 31.6 | 36
RV30 | 30 | 13500 | 80 | 77 | 85 | 441.4 | 0.379 | 11.47 | 167.3 | 32 | 36
RV30 | 30 | 13500 | 85 | 77 | 85 | 443.2 | 0.515 | 15.66 | 228.3 | 31.9 | 36
RV30 | 30 | 13500 | 90 | 77 | 85 | 443.5 | 0.651 | 19.81 | 288.8 | 31.7 | 36
RV30 | 30 | 13500 | 65 | 57 | 95 | 297.2 | 0.748 | 15.25 | 222.4 | 34.3 | 37
RV30 | 30 | 13500 | 70 | 57 | 95 | 299.2 | 0.933 | 19.15 | 279.2 | 34.1 | 37
RV30 | 30 | 13500 | 75 | 57 | 95 | 314.5 | 0.972 | 20.97 | 305.7 | 34.1 | 37
RV30 | 30 | 13500 | 80 | 57 | 95 | 334.5 | 0.972 | 22.3 | 325.1 | 34.2 | 37
RV30 | 30 | 13500 | 85 | 57 | 95 | 354.9 | 0.972 | 23.66 | 344.9 | 34.3 | 37
RV30 | 30 | 13500 | 90 | 57 | 95 | 375.7 | 0.972 | 25.05 | 365.2 | 34.4 | 37
RV30 | 30 | 13500 | 65 | 62 | 95 | 323.9 | 0.496 | 11.02 | 160.6 | 34.8 | 37
RV30 | 30 | 13500 | 70 | 62 | 95 | 325.9 | 0.68 | 15.21 | 221.7 | 34.6 | 37
RV30 | 30 | 13500 | 75 | 62 | 95 | 327.4 | 0.865 | 19.42 | 283.2 | 34.3 | 37
RV30 | 30 | 13500 | 80 | 62 | 95 | 334.6 | 0.972 | 22.31 | 325.3 | 34.2 | 37
RV30 | 30 | 13500 | 85 | 62 | 95 | 355.1 | 0.972 | 23.67 | 345.1 | 34.3 | 37
RV30 | 30 | 13500 | 90 | 62 | 95 | 375.9 | 0.972 | 25.05 | 365.3 | 34.4 | 37
RV30 | 30 | 13500 | 70 | 67 | 95 | 354.6 | 0.457 | 11.11 | 162 | 35 | 37
RV30 | 30 | 13500 | 75 | 67 | 95 | 356.5 | 0.622 | 15.21 | 221.7 | 34.7 | 37
RV30 | 30 | 13500 | 80 | 67 | 95 | 357.2 | 0.787 | 19.29 | 281.2 | 34.6 | 37
RV30 | 30 | 13500 | 85 | 67 | 95 | 360 | 0.943 | 23.28 | 339.4 | 34.3 | 37
RV30 | 30 | 13500 | 90 | 67 | 95 | 376 | 0.972 | 25.07 | 365.5 | 34.4 | 37
RV30 | 30 | 13500 | 75 | 72 | 95 | 387.6 | 0.418 | 11.11 | 162 | 35.1 | 37
RV30 | 30 | 13500 | 80 | 72 | 95 | 389.2 | 0.573 | 15.31 | 223.2 | 34.8 | 37
RV30 | 30 | 13500 | 85 | 72 | 95 | 389.3 | 0.729 | 19.47 | 283.8 | 34.8 | 37
RV30 | 30 | 13500 | 90 | 72 | 95 | 391.5 | 0.875 | 23.48 | 342.4 | 34.6 | 37
RV30 | 30 | 13500 | 80 | 77 | 95 | 421.4 | 0.379 | 10.95 | 159.7 | 35.2 | 37
RV30 | 30 | 13500 | 85 | 77 | 95 | 423.4 | 0.525 | 15.24 | 222.2 | 35.1 | 37
RV30 | 30 | 13500 | 90 | 77 | 95 | 423.7 | 0.661 | 19.21 | 280.1 | 35 | 37
RV30 | 30 | 13500 | 65 | 57 | 105 | 281.6 | 0.758 | 14.64 | 213.5 | 37.7 | 37
RV30 | 30 | 13500 | 70 | 57 | 105 | 283.1 | 0.962 | 18.68 | 272.4 | 37.3 | 37
RV30 | 30 | 13500 | 75 | 57 | 105 | 300.9 | 0.972 | 20.06 | 292.5 | 37.4 | 37
RV30 | 30 | 13500 | 80 | 57 | 105 | 320.7 | 0.972 | 21.38 | 311.7 | 37.4 | 37
RV30 | 30 | 13500 | 85 | 57 | 105 | 340.7 | 0.972 | 22.72 | 331.2 | 37.5 | 37
RV30 | 30 | 13500 | 90 | 57 | 105 | 361.1 | 0.972 | 24.07 | 350.9 | 37.6 | 37
RV30 | 30 | 13500 | 65 | 62 | 105 | 307.2 | 0.506 | 10.65 | 155.3 | 38.2 | 37
RV30 | 30 | 13500 | 70 | 62 | 105 | 309.2 | 0.69 | 14.64 | 213.4 | 37.9 | 37
RV30 | 30 | 13500 | 75 | 62 | 105 | 311.1 | 0.884 | 18.87 | 275.1 | 37.6 | 37
RV30 | 30 | 13500 | 80 | 62 | 105 | 320.9 | 0.972 | 21.39 | 311.9 | 37.4 | 37
RV30 | 30 | 13500 | 85 | 62 | 105 | 340.8 | 0.972 | 22.72 | 331.3 | 37.5 | 37
RV30 | 30 | 13500 | 90 | 62 | 105 | 361.1 | 0.972 | 24.07 | 351 | 37.6 | 37
RV30 | 30 | 13500 | 70 | 67 | 105 | 336.6 | 0.457 | 10.55 | 153.8 | 38.4 | 37
RV30 | 30 | 13500 | 75 | 67 | 105 | 338.6 | 0.632 | 14.67 | 213.9 | 38.1 | 37
RV30 | 30 | 13500 | 80 | 67 | 105 | 339.9 | 0.807 | 18.81 | 274.2 | 37.8 | 37
RV30 | 30 | 13500 | 85 | 67 | 105 | 341 | 0.972 | 22.73 | 331.4 | 37.5 | 37
RV30 | 30 | 13500 | 90 | 67 | 105 | 361.3 | 0.972 | 24.09 | 351.2 | 37.6 | 37
RV30 | 30 | 13500 | 75 | 72 | 105 | 368.2 | 0.418 | 10.56 | 153.9 | 38.5 | 37
RV30 | 30 | 13500 | 80 | 72 | 105 | 369.7 | 0.583 | 14.79 | 215.6 | 38.2 | 37
RV30 | 30 | 13500 | 85 | 72 | 105 | 370 | 0.748 | 18.99 | 276.9 | 38 | 37
RV30 | 30 | 13500 | 90 | 72 | 105 | 371.3 | 0.904 | 23.02 | 335.7 | 37.8 | 37
RV30 | 30 | 13500 | 80 | 77 | 105 | 400.9 | 0.379 | 10.43 | 152 | 38.7 | 37
RV30 | 30 | 13500 | 85 | 77 | 105 | 402.7 | 0.535 | 14.77 | 215.3 | 38.3 | 37
RV30 | 30 | 13500 | 90 | 77 | 105 | 403.3 | 0.68 | 18.82 | 274.4 | 38.2 | 37
RV30 | 30 | 13500 | 65 | 57 | 115 | 264.2 | 0.777 | 14.09 | 205.4 | 41.8 | 38
RV30 | 30 | 13500 | 70 | 57 | 115 | 267.5 | 0.972 | 17.83 | 260 | 41.2 | 38
RV30 | 30 | 13500 | 75 | 57 | 115 | 286.1 | 0.972 | 19.07 | 278.1 | 41.3 | 38
RV30 | 30 | 13500 | 80 | 57 | 115 | 305.3 | 0.972 | 20.35 | 296.7 | 41.3 | 38
RV30 | 30 | 13500 | 85 | 57 | 115 | 325 | 0.972 | 21.66 | 315.8 | 41.2 | 38
RV30 | 30 | 13500 | 90 | 57 | 115 | 344.7 | 0.972 | 22.98 | 335 | 41.3 | 38
RV30 | 30 | 13500 | 65 | 62 | 115 | 288.7 | 0.505 | 10.01 | 145.9 | 42.4 | 38
RV30 | 30 | 13500 | 70 | 62 | 115 | 291 | 0.71 | 14.16 | 206.5 | 41.8 | 38
RV30 | 30 | 13500 | 75 | 62 | 115 | 292.4 | 0.914 | 18.33 | 267.2 | 41.4 | 38
RV30 | 30 | 13500 | 80 | 62 | 115 | 305.4 | 0.972 | 20.36 | 296.9 | 41.3 | 38
RV30 | 30 | 13500 | 85 | 62 | 115 | 325.1 | 0.972 | 21.67 | 316 | 41.2 | 38
RV30 | 30 | 13500 | 90 | 62 | 115 | 344.8 | 0.972 | 22.99 | 335.2 | 41.3 | 38
RV30 | 30 | 13500 | 70 | 67 | 115 | 316.8 | 0.467 | 10.14 | 147.8 | 42.5 | 38
RV30 | 30 | 13500 | 75 | 67 | 115 | 319 | 0.651 | 14.25 | 207.7 | 42 | 38
RV30 | 30 | 13500 | 80 | 67 | 115 | 320.8 | 0.836 | 18.4 | 268.2 | 41.6 | 38
RV30 | 30 | 13500 | 85 | 67 | 115 | 325.2 | 0.972 | 21.68 | 316.1 | 41.3 | 38
RV30 | 30 | 13500 | 90 | 67 | 115 | 345.1 | 0.972 | 23 | 335.4 | 41.3 | 38
RV30 | 30 | 13500 | 75 | 72 | 115 | 346.9 | 0.428 | 10.17 | 148.3 | 42.4 | 38
RV30 | 30 | 13500 | 80 | 72 | 115 | 348.9 | 0.593 | 14.19 | 206.9 | 42.1 | 38
RV30 | 30 | 13500 | 85 | 72 | 115 | 349.6 | 0.768 | 18.41 | 268.4 | 41.8 | 38
RV30 | 30 | 13500 | 90 | 72 | 115 | 351.6 | 0.923 | 22.27 | 324.7 | 41.4 | 38
RV30 | 30 | 13500 | 80 | 77 | 115 | 378 | 0.389 | 10.08 | 147 | 42.7 | 38
RV30 | 30 | 13500 | 85 | 77 | 115 | 380.4 | 0.544 | 14.2 | 207 | 42.3 | 38
RV30 | 30 | 13500 | 90 | 77 | 115 | 380.5 | 0.7 | 18.26 | 266.3 | 42.1 | 38
RV30 | 30 | 13500 | 65 | 57 | 125 | 246.9 | 0.797 | 13.49 | 196.7 | 46.6 | 38
RV30 | 30 | 13500 | 70 | 57 | 125 | 252.4 | 0.972 | 16.83 | 245.4 | 45.7 | 38
RV30 | 30 | 13500 | 75 | 57 | 125 | 270.6 | 0.972 | 18.04 | 263 | 45.6 | 38
RV30 | 30 | 13500 | 80 | 57 | 125 | 289.2 | 0.972 | 19.28 | 281.1 | 45.5 | 38
RV30 | 30 | 13500 | 85 | 57 | 125 | 308.3 | 0.972 | 20.55 | 299.6 | 45.5 | 38
RV30 | 30 | 13500 | 90 | 57 | 125 | 327.6 | 0.972 | 21.84 | 318.4 | 45.5 | 38
RV30 | 30 | 13500 | 65 | 62 | 125 | 269.4 | 0.515 | 9.52 | 138.8 | 47.4 | 38
RV30 | 30 | 13500 | 70 | 62 | 125 | 271.8 | 0.729 | 13.59 | 198.1 | 46.3 | 38
RV30 | 30 | 13500 | 75 | 62 | 125 | 274.1 | 0.943 | 17.72 | 258.4 | 45.6 | 38
RV30 | 30 | 13500 | 80 | 62 | 125 | 289.3 | 0.972 | 19.29 | 281.2 | 45.5 | 38
RV30 | 30 | 13500 | 85 | 62 | 125 | 308.3 | 0.972 | 20.56 | 299.7 | 45.5 | 38
RV30 | 30 | 13500 | 90 | 62 | 125 | 327.4 | 0.972 | 21.83 | 318.3 | 45.5 | 38
RV30 | 30 | 13500 | 70 | 67 | 125 | 296.2 | 0.467 | 9.48 | 138.2 | 47.2 | 38
RV30 | 30 | 13500 | 75 | 67 | 125 | 298.9 | 0.67 | 13.74 | 200.4 | 46.4 | 38
RV30 | 30 | 13500 | 80 | 67 | 125 | 300.7 | 0.865 | 17.84 | 260.1 | 45.8 | 38
RV30 | 30 | 13500 | 85 | 67 | 125 | 308.4 | 0.972 | 20.56 | 299.8 | 45.5 | 38
RV30 | 30 | 13500 | 90 | 67 | 125 | 327.7 | 0.972 | 21.84 | 318.5 | 45.5 | 38
RV30 | 30 | 13500 | 75 | 72 | 125 | 324.7 | 0.428 | 9.53 | 138.9 | 47.1 | 38
RV30 | 30 | 13500 | 80 | 72 | 125 | 327.1 | 0.612 | 13.74 | 200.3 | 46.4 | 38
RV30 | 30 | 13500 | 85 | 72 | 125 | 328.2 | 0.787 | 17.72 | 258.4 | 45.9 | 38
RV30 | 30 | 13500 | 90 | 72 | 125 | 330 | 0.952 | 21.56 | 314.3 | 45.5 | 38
RV30 | 30 | 13500 | 80 | 77 | 125 | 354.3 | 0.389 | 9.45 | 137.8 | 47.2 | 38
RV30 | 30 | 13500 | 85 | 77 | 125 | 357.1 | 0.554 | 13.57 | 197.8 | 46.5 | 38
RV30 | 30 | 13500 | 90 | 77 | 125 | 357.2 | 0.729 | 17.86 | 260.4 | 46.2 | 38
RV35 | 35 | 8750 | 65 | 57 | 75 | 361.2 | 0.657 | 25.11 | 237.3 | 28.5 | 39
RV35 | 35 | 8750 | 70 | 57 | 75 | 361.3 | 0.776 | 29.68 | 280.5 | 28.4 | 39
RV35 | 35 | 8750 | 75 | 57 | 75 | 361 | 0.906 | 34.59 | 326.9 | 28.3 | 39
RV35 | 35 | 8750 | 80 | 57 | 75 | 364.8 | 0.995 | 38.41 | 363 | 28.2 | 39
RV35 | 35 | 8750 | 85 | 57 | 75 | 383.1 | 0.995 | 40.34 | 381.2 | 28.2 | 39
RV35 | 35 | 8750 | 90 | 57 | 75 | 401.3 | 0.995 | 42.25 | 399.3 | 28.2 | 39
RV35 | 35 | 8750 | 65 | 62 | 75 | 394.7 | 0.488 | 20.37 | 192.5 | 28.7 | 39
RV35 | 35 | 8750 | 70 | 62 | 75 | 394.7 | 0.597 | 24.94 | 235.7 | 28.6 | 39
RV35 | 35 | 8750 | 75 | 62 | 75 | 394.3 | 0.717 | 29.9 | 282.6 | 28.5 | 39
RV35 | 35 | 8750 | 80 | 62 | 75 | 393.7 | 0.826 | 34.41 | 325.2 | 28.4 | 39
RV35 | 35 | 8750 | 85 | 62 | 75 | 393.1 | 0.935 | 38.91 | 367.7 | 28.3 | 39
RV35 | 35 | 8750 | 90 | 62 | 75 | 401.6 | 0.995 | 42.29 | 399.6 | 28.2 | 39
RV35 | 35 | 8750 | 70 | 67 | 75 | 431.1 | 0.448 | 20.43 | 193.1 | 28.8 | 39
RV35 | 35 | 8750 | 75 | 67 | 75 | 430.8 | 0.547 | 24.95 | 235.8 | 28.7 | 39
RV35 | 35 | 8750 | 80 | 67 | 75 | 430.2 | 0.647 | 29.45 | 278.3 | 28.6 | 39
RV35 | 35 | 8750 | 85 | 67 | 75 | 429.1 | 0.756 | 34.35 | 324.6 | 28.5 | 39
RV35 | 35 | 8750 | 90 | 67 | 75 | 428.2 | 0.856 | 38.77 | 366.4 | 28.4 | 39
RV35 | 35 | 8750 | 75 | 72 | 75 | 468.6 | 0.408 | 20.23 | 191.2 | 28.8 | 39
RV35 | 35 | 8750 | 80 | 72 | 75 | 467.5 | 0.498 | 24.61 | 232.6 | 28.7 | 39
RV35 | 35 | 8750 | 85 | 72 | 75 | 466 | 0.597 | 29.44 | 278.2 | 28.7 | 39
RV35 | 35 | 8750 | 90 | 72 | 75 | 464.5 | 0.687 | 33.76 | 319 | 28.6 | 39
RV35 | 35 | 8750 | 80 | 77 | 75 | 506.7 | 0.368 | 19.75 | 186.6 | 29 | 39
RV35 | 35 | 8750 | 85 | 77 | 75 | 505.5 | 0.458 | 24.49 | 231.4 | 28.9 | 39
RV35 | 35 | 8750 | 90 | 77 | 75 | 503.4 | 0.547 | 29.16 | 275.6 | 28.8 | 39
RV35 | 35 | 8750 | 65 | 57 | 85 | 347.6 | 0.657 | 24.16 | 228.3 | 31.5 | 39
RV35 | 35 | 8750 | 70 | 57 | 85 | 347.4 | 0.786 | 28.91 | 273.2 | 31.4 | 39
RV35 | 35 | 8750 | 75 | 57 | 85 | 347.3 | 0.916 | 33.65 | 318 | 31.3 | 39
RV35 | 35 | 8750 | 80 | 57 | 85 | 353.9 | 0.995 | 37.27 | 352.2 | 31.3 | 39
RV35 | 35 | 8750 | 85 | 57 | 85 | 372.1 | 0.995 | 39.19 | 370.3 | 31.3 | 39
RV35 | 35 | 8750 | 90 | 57 | 85 | 390.2 | 0.995 | 41.1 | 388.4 | 31.3 | 39
RV35 | 35 | 8750 | 65 | 62 | 85 | 379.8 | 0.488 | 19.6 | 185.2 | 31.8 | 39
RV35 | 35 | 8750 | 70 | 62 | 85 | 380 | 0.607 | 24.41 | 230.7 | 31.7 | 39
RV35 | 35 | 8750 | 75 | 62 | 85 | 379.9 | 0.717 | 28.8 | 272.2 | 31.6 | 39
RV35 | 35 | 8750 | 80 | 62 | 85 | 379.5 | 0.836 | 33.58 | 317.3 | 31.5 | 39
RV35 | 35 | 8750 | 85 | 62 | 85 | 379.1 | 0.955 | 38.32 | 362.1 | 31.4 | 39
RV35 | 35 | 8750 | 90 | 62 | 85 | 390.5 | 0.995 | 41.12 | 388.6 | 31.3 | 39
RV35 | 35 | 8750 | 70 | 67 | 85 | 415.7 | 0.448 | 19.69 | 186.1 | 32 | 39
RV35 | 35 | 8750 | 75 | 67 | 85 | 415.3 | 0.547 | 24.05 | 227.3 | 31.8 | 39
RV35 | 35 | 8750 | 80 | 67 | 85 | 414.9 | 0.657 | 28.84 | 272.5 | 31.7 | 39
RV35 | 35 | 8750 | 85 | 67 | 85 | 414.1 | 0.766 | 33.58 | 317.3 | 31.6 | 39
RV35 | 35 | 8750 | 90 | 67 | 85 | 413.5 | 0.866 | 37.88 | 358 | 31.5 | 39
RV35 | 35 | 8750 | 75 | 72 | 85 | 452.2 | 0.408 | 19.52 | 184.5 | 32.1 | 39
RV35 | 35 | 8750 | 80 | 72 | 85 | 451.5 | 0.508 | 24.25 | 229.2 | 32 | 39
RV35 | 35 | 8750 | 85 | 72 | 85 | 450.3 | 0.607 | 28.93 | 273.4 | 31.8 | 39
RV35 | 35 | 8750 | 90 | 72 | 85 | 449 | 0.697 | 33.1 | 312.8 | 31.8 | 39
RV35 | 35 | 8750 | 80 | 77 | 85 | 490 | 0.368 | 19.09 | 180.4 | 32.2 | 39
RV35 | 35 | 8750 | 85 | 77 | 85 | 489 | 0.458 | 23.69 | 223.9 | 32.1 | 39
RV35 | 35 | 8750 | 90 | 77 | 85 | 487.3 | 0.547 | 28.22 | 266.7 | 32 | 39
RV35 | 35 | 8750 | 65 | 57 | 95 | 332.8 | 0.667 | 23.48 | 221.9 | 34.9 | 39
RV35 | 35 | 8750 | 70 | 57 | 95 | 332.9 | 0.796 | 28.04 | 265 | 34.8 | 39
RV35 | 35 | 8750 | 75 | 57 | 95 | 332.7 | 0.935 | 32.93 | 311.2 | 34.6 | 39
RV35 | 35 | 8750 | 80 | 57 | 95 | 341.9 | 0.995 | 36 | 340.2 | 34.6 | 39
RV35 | 35 | 8750 | 85 | 57 | 95 | 359.9 | 0.995 | 37.9 | 358.2 | 34.7 | 39
RV35 | 35 | 8750 | 90 | 57 | 95 | 377.8 | 0.995 | 39.79 | 376 | 34.7 | 39
RV35 | 35 | 8750 | 65 | 62 | 95 | 363.8 | 0.488 | 18.77 | 177.4 | 35.2 | 39
RV35 | 35 | 8750 | 70 | 62 | 95 | 364 | 0.607 | 23.39 | 221 | 35.1 | 39
RV35 | 35 | 8750 | 75 | 62 | 95 | 364 | 0.727 | 27.99 | 264.5 | 35 | 39
RV35 | 35 | 8750 | 80 | 62 | 95 | 364 | 0.846 | 32.58 | 307.9 | 34.9 | 39
RV35 | 35 | 8750 | 85 | 62 | 95 | 364.1 | 0.965 | 37.19 | 351.4 | 34.8 | 39
RV35 | 35 | 8750 | 90 | 62 | 95 | 378.1 | 0.995 | 39.82 | 376.3 | 34.7 | 39
RV35 | 35 | 8750 | 70 | 67 | 95 | 398.3 | 0.448 | 18.88 | 178.4 | 35.5 | 39
RV35 | 35 | 8750 | 75 | 67 | 95 | 398.3 | 0.557 | 23.49 | 222 | 35.3 | 39
RV35 | 35 | 8750 | 80 | 67 | 95 | 398 | 0.667 | 28.07 | 265.3 | 35.2 | 39
RV35 | 35 | 8750 | 85 | 67 | 95 | 397.2 | 0.776 | 32.63 | 308.4 | 35.1 | 39
RV35 | 35 | 8750 | 90 | 67 | 95 | 396.9 | 0.886 | 37.2 | 351.5 | 35 | 39
RV35 | 35 | 8750 | 75 | 72 | 95 | 433.8 | 0.408 | 18.73 | 177 | 35.7 | 39
RV35 | 35 | 8750 | 80 | 72 | 95 | 433.3 | 0.508 | 23.27 | 219.9 | 35.5 | 39
RV35 | 35 | 8750 | 85 | 72 | 95 | 432.5 | 0.607 | 27.78 | 262.5 | 35.4 | 39
RV35 | 35 | 8750 | 90 | 72 | 95 | 431.5 | 0.707 | 32.26 | 304.9 | 35.3 | 39
RV35 | 35 | 8750 | 80 | 77 | 95 | 470.8 | 0.368 | 18.35 | 173.4 | 35.8 | 39
RV35 | 35 | 8750 | 85 | 77 | 95 | 470.3 | 0.468 | 23.28 | 220 | 35.7 | 39
RV35 | 35 | 8750 | 90 | 77 | 95 | 468.7 | 0.557 | 27.64 | 261.2 | 35.6 | 39
RV35 | 35 | 8750 | 65 | 57 | 105 | 317.4 | 0.677 | 22.73 | 214.8 | 38.4 | 40
RV35 | 35 | 8750 | 70 | 57 | 105 | 317.4 | 0.806 | 27.08 | 255.9 | 38.3 | 40
RV35 | 35 | 8750 | 75 | 57 | 105 | 317.4 | 0.945 | 31.76 | 300.1 | 38.1 | 40
RV35 | 35 | 8750 | 80 | 57 | 105 | 329.3 | 0.995 | 34.68 | 327.7 | 38.2 | 40
RV35 | 35 | 8750 | 85 | 57 | 105 | 347 | 0.995 | 36.55 | 345.4 | 38.3 | 40
RV35 | 35 | 8750 | 90 | 57 | 105 | 364.8 | 0.995 | 38.41 | 363 | 38.4 | 40
RV35 | 35 | 8750 | 65 | 62 | 105 | 347 | 0.488 | 17.9 | 169.2 | 38.8 | 40
RV35 | 35 | 8750 | 70 | 62 | 105 | 347.3 | 0.617 | 22.68 | 214.3 | 38.7 | 40
RV35 | 35 | 8750 | 75 | 62 | 105 | 347.5 | 0.746 | 27.44 | 259.3 | 38.6 | 40
RV35 | 35 | 8750 | 80 | 62 | 105 | 347.3 | 0.866 | 31.82 | 300.7 | 38.4 | 40
RV35 | 35 | 8750 | 85 | 62 | 105 | 348.9 | 0.985 | 36.37 | 343.7 | 38.3 | 40
RV35 | 35 | 8750 | 90 | 62 | 105 | 365 | 0.995 | 38.44 | 363.3 | 38.4 | 40
RV35 | 35 | 8750 | 70 | 67 | 105 | 380.2 | 0.448 | 18.02 | 170.3 | 39.1 | 40
RV35 | 35 | 8750 | 75 | 67 | 105 | 380.4 | 0.557 | 22.43 | 212 | 39 | 40
RV35 | 35 | 8750 | 80 | 67 | 105 | 380.2 | 0.677 | 27.23 | 257.3 | 38.8 | 40
RV35 | 35 | 8750 | 85 | 67 | 105 | 379.7 | 0.796 | 31.99 | 302.3 | 38.7 | 40
RV35 | 35 | 8750 | 90 | 67 | 105 | 379 | 0.906 | 36.32 | 343.2 | 38.6 | 40
RV35 | 35 | 8750 | 75 | 72 | 105 | 414.5 | 0.408 | 17.89 | 169.1 | 39.4 | 40
RV35 | 35 | 8750 | 80 | 72 | 105 | 414 | 0.517 | 22.67 | 214.2 | 39.2 | 40
RV35 | 35 | 8750 | 85 | 72 | 105 | 413.4 | 0.617 | 26.99 | 255.1 | 39.1 | 40
RV35 | 35 | 8750 | 90 | 72 | 105 | 412.7 | 0.726 | 31.72 | 299.8 | 39 | 40
RV35 | 35 | 8750 | 80 | 77 | 105 | 450.4 | 0.368 | 17.54 | 165.8 | 39.7 | 40
RV35 | 35 | 8750 | 85 | 77 | 105 | 449.9 | 0.468 | 22.26 | 210.4 | 39.5 | 40
RV35 | 35 | 8750 | 90 | 77 | 105 | 448.6 | 0.567 | 26.93 | 254.5 | 39.3 | 40
RV35 | 35 | 8750 | 65 | 57 | 115 | 300.1 | 0.677 | 21.49 | 203.1 | 42.4 | 40
RV35 | 35 | 8750 | 70 | 57 | 115 | 300.3 | 0.826 | 26.25 | 248.1 | 42.2 | 40
RV35 | 35 | 8750 | 75 | 57 | 115 | 300.5 | 0.975 | 31.01 | 293 | 42 | 40
RV35 | 35 | 8750 | 80 | 57 | 115 | 315 | 0.995 | 33.17 | 313.5 | 42.1 | 40
RV35 | 35 | 8750 | 85 | 57 | 115 | 332.5 | 0.995 | 35.02 | 330.9 | 42.3 | 40
RV35 | 35 | 8750 | 90 | 57 | 115 | 350 | 0.995 | 36.86 | 348.3 | 42.4 | 40
RV35 | 35 | 8750 | 65 | 62 | 115 | 328.1 | 0.488 | 16.93 | 160 | 42.9 | 40
RV35 | 35 | 8750 | 70 | 62 | 115 | 328.8 | 0.627 | 21.82 | 206.2 | 42.6 | 40
RV35 | 35 | 8750 | 75 | 62 | 115 | 329 | 0.757 | 26.34 | 248.9 | 42.5 | 40
RV35 | 35 | 8750 | 80 | 62 | 115 | 328.9 | 0.886 | 30.83 | 291.3 | 42.4 | 40
RV35 | 35 | 8750 | 85 | 62 | 115 | 332.7 | 0.995 | 35.04 | 331.1 | 42.3 | 40
RV35 | 35 | 8750 | 90 | 62 | 115 | 350.2 | 0.995 | 36.88 | 348.5 | 42.4 | 40
RV35 | 35 | 8750 | 70 | 67 | 115 | 360.1 | 0.448 | 17.06 | 161.2 | 43.2 | 40
RV35 | 35 | 8750 | 75 | 67 | 115 | 360.3 | 0.567 | 21.63 | 204.4 | 43 | 40
RV35 | 35 | 8750 | 80 | 67 | 115 | 360.3 | 0.687 | 26.18 | 247.4 | 42.9 | 40
RV35 | 35 | 8750 | 85 | 67 | 115 | 360.1 | 0.816 | 31.1 | 293.9 | 42.7 | 40
RV35 | 35 | 8750 | 90 | 67 | 115 | 359.4 | 0.935 | 35.58 | 336.2 | 42.6 | 40
RV35 | 35 | 8750 | 75 | 72 | 115 | 392.6 | 0.408 | 16.95 | 160.2 | 43.6 | 40
RV35 | 35 | 8750 | 80 | 72 | 115 | 392.5 | 0.517 | 21.49 | 203.1 | 43.4 | 40
RV35 | 35 | 8750 | 85 | 72 | 115 | 392.2 | 0.627 | 26.02 | 245.9 | 43.2 | 40
RV35 | 35 | 8750 | 90 | 72 | 115 | 391.4 | 0.746 | 30.91 | 292.1 | 43.1 | 40
RV35 | 35 | 8750 | 80 | 77 | 115 | 427 | 0.368 | 16.63 | 157.2 | 43.9 | 40
RV35 | 35 | 8750 | 85 | 77 | 115 | 426.9 | 0.478 | 21.58 | 203.9 | 43.7 | 40
RV35 | 35 | 8750 | 90 | 77 | 115 | 426 | 0.577 | 26.02 | 245.9 | 43.5 | 40
RV35 | 35 | 8750 | 65 | 57 | 125 | 281.6 | 0.697 | 20.76 | 196.2 | 7.1 | 41
RV35 | 35 | 8750 | 70 | 57 | 125 | 281.8 | 0.846 | 25.23 | 238.4 | 7.1 | 41
RV35 | 35 | 8750 | 75 | 57 | 125 | 283.1 | 0.995 | 29.82 | 281.8 | 7.1 | 41
RV35 | 35 | 8750 | 80 | 57 | 125 | 299.9 | 0.995 | 31.58 | 298.4 | 7.1 | 41
RV35 | 35 | 8750 | 85 | 57 | 125 | 317 | 0.995 | 33.39 | 315.5 | 7.1 | 41
RV35 | 35 | 8750 | 90 | 57 | 125 | 334.1 | 0.995 | 35.19 | 332.5 | 7.1 | 41
RV35 | 35 | 8750 | 65 | 62 | 125 | 308.5 | 0.488 | 15.93 | 150.5 | 7.1 | 41
RV35 | 35 | 8750 | 70 | 62 | 125 | 309.3 | 0.637 | 20.85 | 197 | 7.1 | 41
RV35 | 35 | 8750 | 75 | 62 | 125 | 309.5 | 0.776 | 25.42 | 240.2 | 7.1 | 41
RV35 | 35 | 8750 | 80 | 62 | 125 | 309.5 | 0.915 | 29.98 | 283.3 | 7.1 | 41
RV35 | 35 | 8750 | 85 | 62 | 125 | 317.2 | 0.995 | 33.41 | 315.7 | 7.1 | 41
RV35 | 35 | 8750 | 90 | 62 | 125 | 334.3 | 0.995 | 35.21 | 332.7 | 7.1 | 41
RV35 | 35 | 8750 | 70 | 67 | 125 | 338.9 | 0.448 | 16.06 | 151.8 | 7.1 | 41
RV35 | 35 | 8750 | 75 | 67 | 125 | 339.4 | 0.577 | 20.73 | 195.9 | 7.1 | 41
RV35 | 35 | 8750 | 80 | 67 | 125 | 339.3 | 0.707 | 25.38 | 239.8 | 7.1 | 41
RV35 | 35 | 8750 | 85 | 67 | 125 | 339.1 | 0.836 | 30 | 283.5 | 7.1 | 41
RV35 | 35 | 8750 | 90 | 67 | 125 | 339.1 | 0.965 | 34.63 | 327.3 | 7.1 | 41
RV35 | 35 | 8750 | 75 | 72 | 125 | 369.7 | 0.408 | 15.97 | 150.9 | 7.1 | 41
RV35 | 35 | 8750 | 80 | 72 | 125 | 369.9 | 0.527 | 20.65 | 195.1 | 7.1 | 41
RV35 | 35 | 8750 | 85 | 72 | 125 | 369.7 | 0.647 | 25.3 | 239.1 | 7.1 | 41
RV35 | 35 | 8750 | 90 | 72 | 125 | 369.3 | 0.766 | 29.95 | 283 | 7.1 | 41
RV35 | 35 | 8750 | 80 | 77 | 125 | 402.4 | 0.378 | 16.11 | 152.2 | 7.1 | 41
RV35 | 35 | 8750 | 85 | 77 | 125 | 402.5 | 0.478 | 20.35 | 192.3 | 7.1 | 41
RV35 | 35 | 8750 | 90 | 77 | 125 | 401.9 | 0.587 | 24.96 | 235.9 | 7.1 | 41
RV35 | 35 | 10500 | 65 | 57 | 75 | 376.6 | 0.677 | 22.47 | 254.8 | 29.7 | 39
RV35 | 35 | 10500 | 70 | 57 | 75 | 376.3 | 0.816 | 27.08 | 307.1 | 29.7 | 39
RV35 | 35 | 10500 | 75 | 57 | 75 | 376.6 | 0.955 | 31.73 | 359.8 | 29.5 | 39
RV35 | 35 | 10500 | 80 | 57 | 75 | 391 | 0.995 | 34.31 | 389.1 | 29.5 | 39
RV35 | 35 | 10500 | 85 | 57 | 75 | 410.9 | 0.995 | 36.06 | 408.9 | 29.5 | 39
RV35 | 35 | 10500 | 90 | 57 | 75 | 430.5 | 0.995 | 37.78 | 428.4 | 29.5 | 39
RV35 | 35 | 10500 | 65 | 62 | 75 | 411.5 | 0.488 | 17.7 | 200.7 | 30 | 39
RV35 | 35 | 10500 | 70 | 62 | 75 | 411.7 | 0.617 | 22.4 | 254 | 29.8 | 39
RV35 | 35 | 10500 | 75 | 62 | 75 | 411.5 | 0.746 | 27.08 | 307.1 | 29.7 | 39
RV35 | 35 | 10500 | 80 | 62 | 75 | 411.2 | 0.876 | 31.75 | 360.1 | 29.6 | 39
RV35 | 35 | 10500 | 85 | 62 | 75 | 412.1 | 0.985 | 35.8 | 406 | 29.5 | 39
RV35 | 35 | 10500 | 90 | 62 | 75 | 430.8 | 0.995 | 37.8 | 428.7 | 29.5 | 39
RV35 | 35 | 10500 | 70 | 67 | 75 | 448.1 | 0.448 | 17.7 | 200.7 | 30 | 39
RV35 | 35 | 10500 | 75 | 67 | 75 | 447.7 | 0.567 | 22.39 | 253.9 | 29.9 | 39
RV35 | 35 | 10500 | 80 | 67 | 75 | 446.8 | 0.687 | 27.05 | 306.8 | 29.8 | 39
RV35 | 35 | 10500 | 85 | 67 | 75 | 445.8 | 0.796 | 31.3 | 354.9 | 29.7 | 39
RV35 | 35 | 10500 | 90 | 67 | 75 | 445 | 0.916 | 35.93 | 407.4 | 29.6 | 39
RV35 | 35 | 10500 | 75 | 72 | 75 | 486.6 | 0.408 | 17.5 | 198.5 | 30.1 | 39
RV35 | 35 | 10500 | 80 | 72 | 75 | 485.3 | 0.517 | 22.14 | 251.1 | 30 | 39
RV35 | 35 | 10500 | 85 | 72 | 75 | 483.8 | 0.627 | 26.75 | 303.3 | 29.9 | 39
RV35 | 35 | 10500 | 90 | 72 | 75 | 482 | 0.737 | 31.31 | 355 | 29.8 | 39
RV35 | 35 | 10500 | 80 | 77 | 75 | 524.7 | 0.368 | 17.04 | 193.2 | 30.2 | 39
RV35 | 35 | 10500 | 85 | 77 | 75 | 523.4 | 0.478 | 22.05 | 250 | 30.1 | 39
RV35 | 35 | 10500 | 90 | 77 | 75 | 521.3 | 0.577 | 26.53 | 300.9 | 30.1 | 39
RV35 | 35 | 10500 | 65 | 57 | 85 | 361.7 | 0.677 | 21.59 | 244.8 | 32.8 | 39
RV35 | 35 | 10500 | 70 | 57 | 85 | 361.9 | 0.826 | 26.36 | 298.9 | 32.7 | 39
RV35 | 35 | 10500 | 75 | 57 | 85 | 362.2 | 0.965 | 30.84 | 349.7 | 32.6 | 39
RV35 | 35 | 10500 | 80 | 57 | 85 | 378.9 | 0.995 | 33.25 | 377.1 | 32.5 | 39
RV35 | 35 | 10500 | 85 | 57 | 85 | 398.8 | 0.995 | 35 | 396.9 | 32.6 | 39
RV35 | 35 | 10500 | 90 | 57 | 85 | 418.5 | 0.995 | 36.73 | 416.5 | 32.6 | 39
RV35 | 35 | 10500 | 65 | 62 | 85 | 395.5 | 0.488 | 17.01 | 192.9 | 33.1 | 39
RV35 | 35 | 10500 | 70 | 62 | 85 | 395.8 | 0.627 | 21.89 | 248.2 | 33 | 39
RV35 | 35 | 10500 | 75 | 62 | 85 | 395.8 | 0.756 | 26.4 | 299.4 | 32.9 | 39
RV35 | 35 | 10500 | 80 | 62 | 85 | 395.9 | 0.886 | 30.92 | 350.6 | 32.7 | 39
RV35 | 35 | 10500 | 85 | 62 | 85 | 399 | 0.995 | 35.02 | 397.1 | 32.6 | 39
RV35 | 35 | 10500 | 90 | 62 | 85 | 418.5 | 0.995 | 36.72 | 416.4 | 32.6 | 39
RV35 | 35 | 10500 | 70 | 67 | 85 | 431.2 | 0.448 | 17.03 | 193.1 | 33.2 | 39
RV35 | 35 | 10500 | 75 | 67 | 85 | 430.9 | 0.567 | 21.55 | 244.4 | 33.1 | 39
RV35 | 35 | 10500 | 80 | 67 | 85 | 430.5 | 0.697 | 26.45 | 299.9 | 33 | 39
RV35 | 35 | 10500 | 85 | 67 | 85 | 430.4 | 0.816 | 30.97 | 351.2 | 32.9 | 39
RV35 | 35 | 10500 | 90 | 67 | 85 | 429.1 | 0.935 | 35.4 | 401.4 | 32.7 | 39
RV35 | 35 | 10500 | 75 | 72 | 85 | 469 | 0.408 | 16.88 | 191.4 | 33.4 | 39
RV35 | 35 | 10500 | 80 | 72 | 85 | 468.1 | 0.518 | 21.37 | 242.3 | 33.2 | 39
RV35 | 35 | 10500 | 85 | 72 | 85 | 467 | 0.637 | 26.23 | 297.4 | 33.1 | 39
RV35 | 35 | 10500 | 90 | 72 | 85 | 465.6 | 0.746 | 30.64 | 347.5 | 33 | 39
RV35 | 35 | 10500 | 80 | 77 | 85 | 507 | 0.378 | 16.9 | 191.7 | 33.5 | 39
RV35 | 35 | 10500 | 85 | 77 | 85 | 506 | 0.478 | 21.31 | 241.7 | 33.4 | 39
RV35 | 35 | 10500 | 90 | 77 | 85 | 504 | 0.577 | 25.65 | 290.9 | 33.3 | 39
RV35 | 35 | 10500 | 65 | 57 | 95 | 345.6 | 0.687 | 20.93 | 237.3 | 36.2 | 40
RV35 | 35 | 10500 | 70 | 57 | 95 | 346.1 | 0.836 | 25.51 | 289.3 | 36 | 40
RV35 | 35 | 10500 | 75 | 57 | 95 | 347.5 | 0.985 | 30.19 | 342.4 | 35.9 | 40
RV35 | 35 | 10500 | 80 | 57 | 95 | 365.7 | 0.995 | 32.09 | 363.9 | 36 | 40
RV35 | 35 | 10500 | 85 | 57 | 95 | 385.4 | 0.995 | 33.82 | 383.5 | 36 | 40
RV35 | 35 | 10500 | 90 | 57 | 95 | 405 | 0.995 | 35.55 | 403.1 | 36.1 | 40
RV35 | 35 | 10500 | 65 | 62 | 95 | 378.2 | 0.488 | 16.26 | 184.4 | 36.6 | 40
RV35 | 35 | 10500 | 70 | 62 | 95 | 378.7 | 0.627 | 20.93 | 237.4 | 36.4 | 40
RV35 | 35 | 10500 | 75 | 62 | 95 | 378.6 | 0.766 | 25.58 | 290.1 | 36.3 | 40
RV35 | 35 | 10500 | 80 | 62 | 95 | 378.7 | 0.906 | 30.25 | 343 | 36.1 | 40
RV35 | 35 | 10500 | 85 | 62 | 95 | 385.6 | 0.995 | 33.84 | 383.7 | 36 | 40
RV35 | 35 | 10500 | 90 | 62 | 95 | 405.3 | 0.995 | 35.56 | 403.3 | 36.1 | 40
RV35 | 35 | 10500 | 70 | 67 | 95 | 412.5 | 0.448 | 16.29 | 184.7 | 36.8 | 40
RV35 | 35 | 10500 | 75 | 67 | 95 | 412.6 | 0.577 | 21 | 238.1 | 36.6 | 40
RV35 | 35 | 10500 | 80 | 67 | 95 | 412.2 | 0.707 | 25.69 | 291.3 | 36.5 | 40
RV35 | 35 | 10500 | 85 | 67 | 95 | 412.1 | 0.826 | 30.02 | 340.4 | 36.3 | 40
RV35 | 35 | 10500 | 90 | 67 | 95 | 411.8 | 0.955 | 34.69 | 393.4 | 36.2 | 40
RV35 | 35 | 10500 | 75 | 72 | 95 | 449.1 | 0.408 | 16.16 | 183.2 | 37 | 40
RV35 | 35 | 10500 | 80 | 72 | 95 | 448.9 | 0.528 | 20.88 | 236.8 | 36.8 | 40
RV35 | 35 | 10500 | 85 | 72 | 95 | 448 | 0.647 | 25.56 | 289.8 | 36.7 | 40
RV35 | 35 | 10500 | 90 | 72 | 95 | 446.9 | 0.756 | 29.81 | 338 | 36.5 | 40
RV35 | 35 | 10500 | 80 | 77 | 95 | 486.4 | 0.378 | 16.22 | 183.9 | 37.2 | 40
RV35 | 35 | 10500 | 85 | 77 | 95 | 486 | 0.478 | 20.47 | 232.1 | 37 | 40
RV35 | 35 | 10500 | 90 | 77 | 95 | 484.4 | 0.587 | 25.08 | 284.4 | 36.9 | 40
RV35 | 35 | 10500 | 65 | 57 | 105 | 329 | 0.697 | 20.21 | 229.2 | 39.7 | 40
RV35 | 35 | 10500 | 70 | 57 | 105 | 329.7 | 0.856 | 24.89 | 282.2 | 39.5 | 40
RV35 | 35 | 10500 | 75 | 57 | 105 | 332.4 | 0.995 | 29.17 | 330.8 | 39.5 | 40
RV35 | 35 | 10500 | 80 | 57 | 105 | 351.7 | 0.995 | 30.86 | 350 | 39.6 | 40
RV35 | 35 | 10500 | 85 | 57 | 105 | 371.2 | 0.995 | 32.57 | 369.4 | 39.7 | 40
RV35 | 35 | 10500 | 90 | 57 | 105 | 390.5 | 0.995 | 34.27 | 388.6 | 39.7 | 40
RV35 | 35 | 10500 | 65 | 62 | 105 | 360.2 | 0.488 | 15.49 | 175.6 | 40.2 | 40
RV35 | 35 | 10500 | 70 | 62 | 105 | 360.8 | 0.637 | 20.26 | 229.8 | 40 | 40
RV35 | 35 | 10500 | 75 | 62 | 105 | 360.9 | 0.786 | 25.03 | 283.8 | 39.9 | 40
RV35 | 35 | 10500 | 80 | 62 | 105 | 361.1 | 0.926 | 29.47 | 334.2 | 39.7 | 40
RV35 | 35 | 10500 | 85 | 62 | 105 | 371.4 | 0.995 | 32.59 | 369.6 | 39.7 | 40
RV35 | 35 | 10500 | 90 | 62 | 105 | 390.7 | 0.995 | 34.29 | 388.8 | 39.7 | 40
RV35 | 35 | 10500 | 70 | 67 | 105 | 393 | 0.448 | 15.52 | 176 | 40.5 | 40
RV35 | 35 | 10500 | 75 | 67 | 105 | 393.4 | 0.587 | 20.37 | 231 | 40.3 | 40
RV35 | 35 | 10500 | 80 | 67 | 105 | 393.2 | 0.716 | 24.84 | 281.7 | 40.1 | 40
RV35 | 35 | 10500 | 85 | 67 | 105 | 393.4 | 0.846 | 29.35 | 332.8 | 40 | 40
RV35 | 35 | 10500 | 90 | 67 | 105 | 394.4 | 0.975 | 33.92 | 384.6 | 39.8 | 40
RV35 | 35 | 10500 | 75 | 72 | 105 | 428.4 | 0.408 | 15.41 | 174.8 | 40.8 | 40
RV35 | 35 | 10500 | 80 | 72 | 105 | 428.4 | 0.537 | 20.3 | 230.2 | 40.5 | 40
RV35 | 35 | 10500 | 85 | 72 | 105 | 427.8 | 0.657 | 24.78 | 281 | 40.4 | 40
RV35 | 35 | 10500 | 90 | 72 | 105 | 427 | 0.776 | 29.22 | 331.4 | 40.2 | 40
RV35 | 35 | 10500 | 80 | 77 | 105 | 464.6 | 0.378 | 15.49 | 175.7 | 41 | 40
RV35 | 35 | 10500 | 85 | 77 | 105 | 464.4 | 0.488 | 19.97 | 226.5 | 40.8 | 40
RV35 | 35 | 10500 | 90 | 77 | 105 | 463.1 | 0.597 | 24.38 | 276.5 | 40.6 | 40
RV35 | 35 | 10500 | 65 | 57 | 115 | 310.5 | 0.707 | 19.35 | 219.4 | 43.6 | 40
RV35 | 35 | 10500 | 70 | 57 | 115 | 311.2 | 0.876 | 24.03 | 272.5 | 43.4 | 40
RV35 | 35 | 10500 | 75 | 57 | 115 | 317.2 | 0.995 | 27.83 | 315.6 | 43.4 | 40
RV35 | 35 | 10500 | 80 | 57 | 115 | 336 | 0.995 | 29.49 | 334.4 | 43.6 | 40
RV35 | 35 | 10500 | 85 | 57 | 115 | 355.1 | 0.995 | 31.16 | 353.4 | 43.7 | 40
RV35 | 35 | 10500 | 90 | 57 | 115 | 374.1 | 0.995 | 32.83 | 372.3 | 43.9 | 40
RV35 | 35 | 10500 | 65 | 62 | 115 | 340.2 | 0.498 | 14.93 | 169.3 | 44.4 | 40
RV35 | 35 | 10500 | 70 | 62 | 115 | 341 | 0.647 | 19.45 | 220.6 | 44 | 40
RV35 | 35 | 10500 | 75 | 62 | 115 | 341.3 | 0.796 | 23.96 | 271.7 | 43.9 | 40
RV35 | 35 | 10500 | 80 | 62 | 115 | 341.4 | 0.955 | 28.77 | 326.2 | 43.7 | 40
RV35 | 35 | 10500 | 85 | 62 | 115 | 355.3 | 0.995 | 31.18 | 353.6 | 43.7 | 40
RV35 | 35 | 10500 | 90 | 62 | 115 | 374.3 | 0.995 | 32.85 | 372.5 | 43.9 | 40
RV35 | 35 | 10500 | 70 | 67 | 115 | 371.3 | 0.448 | 14.66 | 166.3 | 44.6 | 40
RV35 | 35 | 10500 | 75 | 67 | 115 | 372.1 | 0.597 | 19.59 | 222.2 | 44.4 | 40
RV35 | 35 | 10500 | 80 | 67 | 115 | 371.9 | 0.736 | 24.15 | 273.9 | 44.2 | 40
RV35 | 35 | 10500 | 85 | 67 | 115 | 372.4 | 0.876 | 28.76 | 326.1 | 44 | 40
RV35 | 35 | 10500 | 90 | 67 | 115 | 374.6 | 0.995 | 32.87 | 372.8 | 43.9 | 40
RV35 | 35 | 10500 | 75 | 72 | 115 | 405.1 | 0.418 | 14.93 | 169.3 | 45 | 40
RV35 | 35 | 10500 | 80 | 72 | 115 | 405.5 | 0.537 | 19.22 | 217.9 | 44.7 | 40
RV35 | 35 | 10500 | 85 | 72 | 115 | 405.1 | 0.667 | 23.82 | 270.1 | 44.5 | 40
RV35 | 35 | 10500 | 90 | 72 | 115 | 404.5 | 0.796 | 28.4 | 322.1 | 44.3 | 40
RV35 | 35 | 10500 | 80 | 77 | 115 | 440 | 0.378 | 14.67 | 166.4 | 45.3 | 40
RV35 | 35 | 10500 | 85 | 77 | 115 | 440 | 0.497 | 19.3 | 218.9 | 45.1 | 40
RV35 | 35 | 10500 | 90 | 77 | 115 | 438.1 | 0.617 | 23.84 | 270.3 | 44.8 | 40
RV35 | 35 | 10500 | 65 | 57 | 125 | 291.3 | 0.726 | 18.66 | 211.6 | 8.3 | 41
RV35 | 35 | 10500 | 70 | 57 | 125 | 291.9 | 0.905 | 23.31 | 264.3 | 8.3 | 41
RV35 | 35 | 10500 | 75 | 57 | 125 | 301 | 0.995 | 26.42 | 299.6 | 8.3 | 41
RV35 | 35 | 10500 | 80 | 57 | 125 | 319.3 | 0.995 | 28.02 | 317.8 | 8.3 | 41
RV35 | 35 | 10500 | 85 | 57 | 125 | 338 | 0.995 | 29.66 | 336.3 | 8.3 | 41
RV35 | 35 | 10500 | 90 | 57 | 125 | 356.6 | 0.995 | 31.3 | 354.9 | 8.3 | 41
RV35 | 35 | 10500 | 65 | 62 | 125 | 319.2 | 0.497 | 14 | 158.8 | 8.3 | 41
RV35 | 35 | 10500 | 70 | 62 | 125 | 320.2 | 0.657 | 18.54 | 210.3 | 8.3 | 41
RV35 | 35 | 10500 | 75 | 62 | 125 | 320.6 | 0.826 | 23.35 | 264.8 | 8.3 | 41
RV35 | 35 | 10500 | 80 | 62 | 125 | 321.4 | 0.975 | 27.65 | 313.5 | 8.3 | 41
RV35 | 35 | 10500 | 85 | 62 | 125 | 338.2 | 0.995 | 29.67 | 336.5 | 8.3 | 41
RV35 | 35 | 10500 | 90 | 62 | 125 | 356.7 | 0.995 | 31.31 | 355 | 8.3 | 41
RV35 | 35 | 10500 | 70 | 67 | 125 | 348.9 | 0.458 | 14.08 | 159.7 | 8.3 | 41
RV35 | 35 | 10500 | 75 | 67 | 125 | 349.8 | 0.607 | 18.72 | 212.3 | 8.3 | 41
RV35 | 35 | 10500 | 80 | 67 | 125 | 349.9 | 0.756 | 23.33 | 264.6 | 8.3 | 41
RV35 | 35 | 10500 | 85 | 67 | 125 | 349.5 | 0.906 | 27.91 | 316.5 | 8.3 | 41
RV35 | 35 | 10500 | 90 | 67 | 125 | 357 | 0.995 | 31.32 | 355.2 | 8.3 | 41
RV35 | 35 | 10500 | 75 | 72 | 125 | 380.9 | 0.418 | 14.04 | 159.2 | 8.3 | 41
RV35 | 35 | 10500 | 80 | 72 | 125 | 383.5 | 0.547 | 18.51 | 209.9 | 8.3 | 41
RV35 | 35 | 10500 | 85 | 72 | 125 | 381 | 0.687 | 23.07 | 261.6 | 8.3 | 41
RV35 | 35 | 10500 | 90 | 72 | 125 | 380.8 | 0.826 | 27.73 | 314.5 | 8.3 | 41
RV35 | 35 | 10500 | 80 | 77 | 125 | 414 | 0.378 | 13.8 | 156.5 | 8.3 | 41
RV35 | 35 | 10500 | 85 | 77 | 125 | 414.5 | 0.508 | 18.55 | 210.4 | 8.3 | 41
RV35 | 35 | 10500 | 90 | 77 | 125 | 413.7 | 0.627 | 22.87 | 259.3 | 8.3 | 41
RV35 | 35 | 12250 | 65 | 57 | 75 | 388.3 | 0.697 | 20.45 | 270.5 | 31.1 | 39
RV35 | 35 | 12250 | 70 | 57 | 75 | 388.9 | 0.856 | 25.15 | 332.8 | 30.9 | 39
RV35 | 35 | 12250 | 75 | 57 | 75 | 390.9 | 0.995 | 29.4 | 389 | 30.8 | 39
RV35 | 35 | 12250 | 80 | 57 | 75 | 412.4 | 0.995 | 31.02 | 410.4 | 30.8 | 39
RV35 | 35 | 12250 | 85 | 57 | 75 | 433.7 | 0.995 | 32.62 | 431.6 | 30.8 | 39
RV35 | 35 | 12250 | 90 | 57 | 75 | 454.5 | 0.995 | 34.19 | 452.3 | 30.8 | 39
RV35 | 35 | 12250 | 65 | 62 | 75 | 423.3 | 0.488 | 15.6 | 206.4 | 31.3 | 39
RV35 | 35 | 12250 | 70 | 62 | 75 | 423.6 | 0.637 | 20.39 | 269.8 | 31.1 | 39
RV35 | 35 | 12250 | 75 | 62 | 75 | 423.3 | 0.786 | 25.15 | 332.8 | 31 | 39
RV35 | 35 | 12250 | 80 | 62 | 75 | 423.7 | 0.926 | 29.64 | 392.2 | 30.9 | 39
RV35 | 35 | 12250 | 85 | 62 | 75 | 433.9 | 0.995 | 32.64 | 431.8 | 30.8 | 39
RV35 | 35 | 12250 | 90 | 62 | 75 | 454.6 | 0.995 | 34.2 | 452.4 | 30.8 | 39
RV35 | 35 | 12250 | 70 | 67 | 75 | 460.9 | 0.448 | 15.6 | 206.4 | 31.4 | 39
RV35 | 35 | 12250 | 75 | 67 | 75 | 460.6 | 0.587 | 20.44 | 270.4 | 31.2 | 39
RV35 | 35 | 12250 | 80 | 67 | 75 | 459.7 | 0.717 | 24.9 | 329.4 | 31.1 | 39
RV35 | 35 | 12250 | 85 | 67 | 75 | 459 | 0.846 | 29.34 | 388.2 | 31 | 39
RV35 | 35 | 12250 | 90 | 67 | 75 | 458.4 | 0.975 | 33.79 | 447.1 | 30.9 | 39
RV35 | 35 | 12250 | 75 | 72 | 75 | 499.4 | 0.408 | 15.4 | 203.8 | 31.5 | 39
RV35 | 35 | 12250 | 80 | 72 | 75 | 498.6 | 0.537 | 20.25 | 267.9 | 31.3 | 39
RV35 | 35 | 12250 | 85 | 72 | 75 | 497.2 | 0.657 | 24.69 | 326.6 | 31.2 | 39
RV35 | 35 | 12250 | 90 | 72 | 75 | 495 | 0.776 | 29.05 | 384.3 | 31.1 | 39
RV35 | 35 | 12250 | 80 | 77 | 75 | 538 | 0.378 | 15.37 | 203.4 | 31.6 | 39
RV35 | 35 | 12250 | 85 | 77 | 75 | 536.5 | 0.488 | 19.77 | 261.6 | 31.5 | 39
RV35 | 35 | 12250 | 90 | 77 | 75 | 534.3 | 0.607 | 24.52 | 324.4 | 31.4 | 39
RV35 | 35 | 12250 | 65 | 57 | 85 | 372.5 | 0.707 | 19.89 | 263.2 | 34.2 | 39
RV35 | 35 | 12250 | 70 | 57 | 85 | 372.1 | 0.866 | 24.35 | 322.2 | 34 | 39
RV35 | 35 | 12250 | 75 | 57 | 85 | 378 | 0.995 | 28.44 | 376.2 | 33.9 | 39
RV35 | 35 | 12250 | 80 | 57 | 85 | 399.3 | 0.995 | 30.04 | 397.4 | 33.9 | 39
RV35 | 35 | 12250 | 85 | 57 | 85 | 420.6 | 0.995 | 31.64 | 418.6 | 33.9 | 39
RV35 | 35 | 12250 | 90 | 57 | 85 | 441.8 | 0.995 | 33.24 | 439.7 | 33.9 | 39
RV35 | 35 | 12250 | 65 | 62 | 85 | 406.2 | 0.498 | 15.28 | 202.1 | 34.5 | 39
RV35 | 35 | 12250 | 70 | 62 | 85 | 406.8 | 0.647 | 19.89 | 263.1 | 34.3 | 39
RV35 | 35 | 12250 | 75 | 62 | 85 | 407.1 | 0.796 | 24.5 | 324.1 | 34.2 | 39
RV35 | 35 | 12250 | 80 | 62 | 85 | 407.4 | 0.945 | 29.11 | 385.1 | 34 | 39
RV35 | 35 | 12250 | 85 | 62 | 85 | 420.8 | 0.995 | 31.65 | 418.7 | 33.9 | 39
RV35 | 35 | 12250 | 90 | 62 | 85 | 441.7 | 0.995 | 33.23 | 439.6 | 34 | 39
RV35 | 35 | 12250 | 70 | 67 | 85 | 442.9 | 0.448 | 14.99 | 198.3 | 34.6 | 39
RV35 | 35 | 12250 | 75 | 67 | 85 | 443.1 | 0.587 | 19.67 | 260.2 | 34.4 | 39
RV35 | 35 | 12250 | 80 | 67 | 85 | 442.4 | 0.726 | 24.29 | 321.4 | 34.3 | 39
RV35 | 35 | 12250 | 85 | 67 | 85 | 442.2 | 0.866 | 28.93 | 382.8 | 34.2 | 39
RV35 | 35 | 12250 | 90 | 67 | 85 | 443.4 | 0.985 | 33.02 | 436.8 | 34 | 39
RV35 | 35 | 12250 | 75 | 72 | 85 | 480.9 | 0.408 | 14.83 | 196.2 | 34.8 | 39
RV35 | 35 | 12250 | 80 | 72 | 85 | 480.5 | 0.537 | 19.52 | 258.2 | 34.6 | 39
RV35 | 35 | 12250 | 85 | 72 | 85 | 479.4 | 0.667 | 24.16 | 319.6 | 34.4 | 39
RV35 | 35 | 12250 | 90 | 72 | 85 | 478.1 | 0.796 | 28.77 | 380.6 | 34.3 | 39
RV35 | 35 | 12250 | 80 | 77 | 85 | 519.1 | 0.378 | 14.84 | 196.3 | 34.9 | 39
RV35 | 35 | 12250 | 85 | 77 | 85 | 518 | 0.497 | 19.48 | 257.7 | 34.7 | 39
RV35 | 35 | 12250 | 90 | 77 | 85 | 515.9 | 0.607 | 23.67 | 313.2 | 34.6 | 39
RV35 | 35 | 12250 | 65 | 57 | 95 | 355.5 | 0.716 | 19.25 | 254.7 | 37.5 | 40
RV35 | 35 | 12250 | 70 | 57 | 95 | 356.3 | 0.886 | 23.85 | 315.6 | 37.4 | 40
RV35 | 35 | 12250 | 75 | 57 | 95 | 363.7 | 0.995 | 27.36 | 362 | 37.3 | 40
RV35 | 35 | 12250 | 80 | 57 | 95 | 384.9 | 0.995 | 28.95 | 383 | 37.3 | 40
RV35 | 35 | 12250 | 85 | 57 | 95 | 406.1 | 0.995 | 30.54 | 404.1 | 37.4 | 40
RV35 | 35 | 12250 | 90 | 57 | 95 | 427 | 0.995 | 32.12 | 424.9 | 37.4 | 40
RV35 | 35 | 12250 | 65 | 62 | 95 | 387.7 | 0.498 | 14.58 | 192.9 | 37.9 | 40
RV35 | 35 | 12250 | 70 | 62 | 95 | 388.6 | 0.657 | 19.29 | 255.2 | 37.8 | 40
RV35 | 35 | 12250 | 75 | 62 | 95 | 389.1 | 0.806 | 23.71 | 313.7 | 37.6 | 40
RV35 | 35 | 12250 | 80 | 62 | 95 | 389.6 | 0.965 | 28.43 | 376.1 | 37.4 | 40
RV35 | 35 | 12250 | 85 | 62 | 95 | 406.2 | 0.995 | 30.56 | 404.3 | 37.4 | 40
RV35 | 35 | 12250 | 90 | 62 | 95 | 427.2 | 0.995 | 32.13 | 425.1 | 37.4 | 40
RV35 | 35 | 12250 | 70 | 67 | 95 | 423.3 | 0.458 | 14.65 | 193.8 | 38.2 | 40
RV35 | 35 | 12250 | 75 | 67 | 95 | 423.6 | 0.597 | 19.12 | 253 | 38 | 40
RV35 | 35 | 12250 | 80 | 67 | 95 | 423.3 | 0.737 | 23.57 | 311.8 | 37.8 | 40
RV35 | 35 | 12250 | 85 | 67 | 95 | 423.2 | 0.886 | 28.33 | 374.8 | 37.6 | 40
RV35 | 35 | 12250 | 90 | 67 | 95 | 427.4 | 0.995 | 32.15 | 425.3 | 37.5 | 40
RV35 | 35 | 12250 | 75 | 72 | 95 | 460.2 | 0.418 | 14.54 | 192.3 | 38.4 | 40
RV35 | 35 | 12250 | 80 | 72 | 95 | 460 | 0.547 | 19.03 | 251.8 | 38.2 | 40
RV35 | 35 | 12250 | 85 | 72 | 95 | 459.2 | 0.677 | 23.49 | 310.8 | 38 | 40
RV35 | 35 | 12250 | 90 | 72 | 95 | 458.5 | 0.806 | 27.94 | 369.6 | 37.9 | 40
RV35 | 35 | 12250 | 80 | 77 | 95 | 497.3 | 0.378 | 14.22 | 188.1 | 38.6 | 40
RV35 | 35 | 12250 | 85 | 77 | 95 | 496.8 | 0.498 | 18.68 | 247.2 | 38.4 | 40
RV35 | 35 | 12250 | 90 | 77 | 95 | 495.4 | 0.627 | 23.48 | 310.6 | 38.2 | 40
RV35 | 35 | 12250 | 65 | 57 | 105 | 338 | 0.727 | 18.56 | 245.6 | 41.1 | 40
RV35 | 35 | 12250 | 70 | 57 | 105 | 338.7 | 0.906 | 23.18 | 306.7 | 40.9 | 40
RV35 | 35 | 12250 | 75 | 57 | 105 | 349.1 | 0.995 | 26.26 | 347.4 | 40.9 | 40
RV35 | 35 | 12250 | 80 | 57 | 105 | 369.7 | 0.995 | 27.81 | 367.9 | 41 | 40
RV35 | 35 | 12250 | 85 | 57 | 105 | 390.6 | 0.995 | 29.38 | 388.7 | 41.1 | 40
RV35 | 35 | 12250 | 90 | 57 | 105 | 411.2 | 0.995 | 30.94 | 409.3 | 41.1 | 40
RV35 | 35 | 12250 | 65 | 62 | 105 | 368.6 | 0.498 | 13.86 | 183.4 | 41.6 | 40
RV35 | 35 | 12250 | 70 | 62 | 105 | 369.6 | 0.667 | 18.63 | 246.5 | 41.4 | 40
RV35 | 35 | 12250 | 75 | 62 | 105 | 370.3 | 0.826 | 23.11 | 305.8 | 41.2 | 40
RV35 | 35 | 12250 | 80 | 62 | 105 | 371.9 | 0.975 | 27.41 | 362.7 | 41 | 40
RV35 | 35 | 12250 | 85 | 62 | 105 | 390.6 | 0.995 | 29.38 | 388.7 | 41.1 | 40
RV35 | 35 | 12250 | 90 | 62 | 105 | 411.6 | 0.995 | 30.96 | 409.6 | 41.2 | 40
RV35 | 35 | 12250 | 70 | 67 | 105 | 402.8 | 0.458 | 13.94 | 184.4 | 41.9 | 40
RV35 | 35 | 12250 | 75 | 67 | 105 | 403.4 | 0.607 | 18.51 | 244.9 | 41.7 | 40
RV35 | 35 | 12250 | 80 | 67 | 105 | 403.5 | 0.756 | 23.06 | 305.1 | 41.5 | 40
RV35 | 35 | 12250 | 85 | 67 | 105 | 403.5 | 0.906 | 27.63 | 365.5 | 41.3 | 40
RV35 | 35 | 12250 | 90 | 67 | 105 | 411.7 | 0.995 | 30.98 | 409.8 | 41.2 | 40
RV35 | 35 | 12250 | 75 | 72 | 105 | 438.2 | 0.418 | 13.85 | 183.2 | 42.2 | 40
RV35 | 35 | 12250 | 80 | 72 | 105 | 438.6 | 0.557 | 18.47 | 244.4 | 41.9 | 40
RV35 | 35 | 12250 | 85 | 72 | 105 | 437.9 | 0.697 | 23.06 | 305.1 | 41.8 | 40
RV35 | 35 | 12250 | 90 | 72 | 105 | 437.5 | 0.826 | 27.32 | 361.4 | 41.6 | 40
RV35 | 35 | 12250 | 80 | 77 | 105 | 474.2 | 0.378 | 13.55 | 179.3 | 42.5 | 40
RV35 | 35 | 12250 | 85 | 77 | 105 | 473.9 | 0.507 | 18.18 | 240.5 | 42.2 | 40
RV35 | 35 | 12250 | 90 | 77 | 105 | 472.9 | 0.637 | 22.77 | 301.2 | 42 | 40
RV35 | 35 | 12250 | 65 | 57 | 115 | 318.4 | 0.736 | 17.72 | 234.5 | 45.1 | 41
RV35 | 35 | 12250 | 70 | 57 | 115 | 319.2 | 0.925 | 22.33 | 295.4 | 44.8 | 41
RV35 | 35 | 12250 | 75 | 57 | 115 | 332.4 | 0.995 | 25 | 330.8 | 44.9 | 41
RV35 | 35 | 12250 | 80 | 57 | 115 | 352.6 | 0.995 | 26.52 | 350.9 | 45.1 | 41
RV35 | 35 | 12250 | 85 | 57 | 115 | 373 | 0.995 | 28.06 | 371.2 | 45.2 | 41
RV35 | 35 | 12250 | 90 | 57 | 115 | 393.3 | 0.995 | 29.58 | 391.4 | 45.3 | 41
RV35 | 35 | 12250 | 65 | 62 | 115 | 347.3 | 0.498 | 13.06 | 172.8 | 45.7 | 41
RV35 | 35 | 12250 | 70 | 62 | 115 | 348.4 | 0.677 | 17.82 | 235.8 | 45.4 | 41
RV35 | 35 | 12250 | 75 | 62 | 115 | 349.4 | 0.846 | 22.34 | 295.6 | 45.2 | 41
RV35 | 35 | 12250 | 80 | 62 | 115 | 352.8 | 0.995 | 26.54 | 351.1 | 45.1 | 41
RV35 | 35 | 12250 | 85 | 62 | 115 | 373.2 | 0.995 | 28.07 | 371.4 | 45.2 | 41
RV35 | 35 | 12250 | 90 | 62 | 115 | 393.6 | 0.995 | 29.61 | 391.7 | 45.3 | 41
RV35 | 35 | 12250 | 70 | 67 | 115 | 380 | 0.458 | 13.14 | 173.9 | 46 | 41
RV35 | 35 | 12250 | 75 | 67 | 115 | 380.9 | 0.617 | 17.76 | 235 | 45.8 | 41
RV35 | 35 | 12250 | 80 | 67 | 115 | 381.1 | 0.776 | 22.36 | 295.8 | 45.5 | 41
RV35 | 35 | 12250 | 85 | 67 | 115 | 381.2 | 0.935 | 26.95 | 356.6 | 45.4 | 41
RV35 | 35 | 12250 | 90 | 67 | 115 | 394 | 0.995 | 29.64 | 392.1 | 45.3 | 41
RV35 | 35 | 12250 | 75 | 72 | 115 | 413.9 | 0.418 | 13.08 | 173 | 46.4 | 41
RV35 | 35 | 12250 | 80 | 72 | 115 | 414.4 | 0.567 | 17.77 | 235.1 | 46.1 | 41
RV35 | 35 | 12250 | 85 | 72 | 115 | 414.1 | 0.707 | 22.12 | 292.6 | 45.9 | 41
RV35 | 35 | 12250 | 90 | 72 | 115 | 414 | 0.856 | 26.78 | 354.3 | 45.7 | 41
RV35 | 35 | 12250 | 80 | 77 | 115 | 448.1 | 0.388 | 13.14 | 173.9 | 46.8 | 41
RV35 | 35 | 12250 | 85 | 77 | 115 | 448.3 | 0.518 | 17.54 | 232 | 46.4 | 41
RV35 | 35 | 12250 | 90 | 77 | 115 | 447.7 | 0.657 | 22.23 | 294.1 | 46.2 | 41
RV35 | 35 | 12250 | 65 | 57 | 125 | 297.9 | 0.756 | 17.03 | 225.3 | 9.5 | 41
RV35 | 35 | 12250 | 70 | 57 | 125 | 298.6 | 0.955 | 21.56 | 285.3 | 9.5 | 41
RV35 | 35 | 12250 | 75 | 57 | 125 | 314.9 | 0.995 | 23.68 | 313.3 | 9.5 | 41
RV35 | 35 | 12250 | 80 | 57 | 125 | 334.6 | 0.995 | 25.17 | 333 | 9.5 | 41
RV35 | 35 | 12250 | 85 | 57 | 125 | 354.4 | 0.995 | 26.66 | 352.7 | 9.5 | 41
RV35 | 35 | 12250 | 90 | 57 | 125 | 374.4 | 0.995 | 28.16 | 372.6 | 9.5 | 41
RV35 | 35 | 12250 | 65 | 62 | 125 | 325 | 0.507 | 12.46 | 164.9 | 9.5 | 41
RV35 | 35 | 12250 | 70 | 62 | 125 | 326.6 | 0.686 | 16.95 | 224.2 | 9.5 | 41
RV35 | 35 | 12250 | 75 | 62 | 125 | 327.5 | 0.876 | 21.68 | 286.8 | 9.5 | 41
RV35 | 35 | 12250 | 80 | 62 | 125 | 334.8 | 0.995 | 25.19 | 333.2 | 9.5 | 41
RV35 | 35 | 12250 | 85 | 62 | 125 | 354.6 | 0.995 | 26.67 | 352.9 | 9.5 | 41
RV35 | 35 | 12250 | 90 | 62 | 125 | 375.1 | 0.995 | 28.22 | 373.3 | 9.5 | 41
RV35 | 35 | 12250 | 70 | 67 | 125 | 356.2 | 0.458 | 12.33 | 163.1 | 9.5 | 41
RV35 | 35 | 12250 | 75 | 67 | 125 | 357.3 | 0.627 | 16.93 | 224 | 9.5 | 41
RV35 | 35 | 12250 | 80 | 67 | 125 | 357.6 | 0.796 | 21.52 | 284.7 | 9.5 | 41
RV35 | 35 | 12250 | 85 | 67 | 125 | 358.3 | 0.965 | 26.15 | 345.9 | 9.5 | 41
RV35 | 35 | 12250 | 90 | 67 | 125 | 375.3 | 0.995 | 28.23 | 373.5 | 9.5 | 41
RV35 | 35 | 12250 | 75 | 72 | 125 | 388.7 | 0.418 | 12.28 | 162.5 | 9.5 | 41
RV35 | 35 | 12250 | 80 | 72 | 125 | 389.3 | 0.577 | 16.98 | 224.7 | 9.5 | 41
RV35 | 35 | 12250 | 85 | 72 | 125 | 389.2 | 0.736 | 21.66 | 286.6 | 9.5 | 41
RV35 | 35 | 12250 | 90 | 72 | 125 | 389.1 | 0.886 | 26.05 | 344.7 | 9.5 | 41
RV35 | 35 | 12250 | 80 | 77 | 125 | 420.7 | 0.388 | 12.34 | 163.3 | 9.5 | 41
RV35 | 35 | 12250 | 85 | 77 | 125 | 421.5 | 0.527 | 16.8 | 222.3 | 9.5 | 41
RV35 | 35 | 12250 | 90 | 77 | 125 | 421.3 | 0.677 | 21.55 | 285.1 | 9.5 | 41
RV35 | 35 | 14000 | 65 | 57 | 75 | 397.5 | 0.716 | 18.84 | 284.8 | 33.4 | 39
RV35 | 35 | 14000 | 70 | 57 | 75 | 398.4 | 0.896 | 23.6 | 356.8 | 33.3 | 39
RV35 | 35 | 14000 | 75 | 57 | 75 | 407.6 | 0.995 | 26.83 | 405.6 | 33.1 | 39
RV35 | 35 | 14000 | 80 | 57 | 75 | 430.2 | 0.995 | 28.31 | 428.1 | 33.1 | 39
RV35 | 35 | 14000 | 85 | 57 | 75 | 452.6 | 0.995 | 29.79 | 450.4 | 33.1 | 39
RV35 | 35 | 14000 | 90 | 57 | 75 | 474.7 | 0.995 | 31.24 | 472.4 | 33.2 | 39
RV35 | 35 | 14000 | 65 | 62 | 75 | 432.5 | 0.498 | 14.23 | 215.2 | 33.6 | 39
RV35 | 35 | 14000 | 70 | 62 | 75 | 433 | 0.657 | 18.81 | 284.4 | 33.5 | 39
RV35 | 35 | 14000 | 75 | 62 | 75 | 433.1 | 0.816 | 23.38 | 353.5 | 33.3 | 39
RV35 | 35 | 14000 | 80 | 62 | 75 | 433.7 | 0.975 | 27.98 | 423 | 33.2 | 39
RV35 | 35 | 14000 | 85 | 62 | 75 | 452.9 | 0.995 | 29.81 | 450.7 | 33.2 | 39
RV35 | 35 | 14000 | 90 | 62 | 75 | 474.6 | 0.995 | 31.24 | 472.3 | 33.2 | 39
RV35 | 35 | 14000 | 70 | 67 | 75 | 470.4 | 0.458 | 14.24 | 215.3 | 33.7 | 39
RV35 | 35 | 14000 | 75 | 67 | 75 | 470.4 | 0.607 | 18.88 | 285.5 | 33.6 | 39
RV35 | 35 | 14000 | 80 | 67 | 75 | 469.8 | 0.746 | 23.19 | 350.7 | 33.4 | 39
RV35 | 35 | 14000 | 85 | 67 | 75 | 468.8 | 0.896 | 27.77 | 419.9 | 33.3 | 39
RV35 | 35 | 14000 | 90 | 67 | 75 | 474.9 | 0.995 | 31.26 | 472.6 | 33.2 | 39
RV35 | 35 | 14000 | 75 | 72 | 75 | 509.5 | 0.418 | 14.09 | 213 | 33.8 | 39
RV35 | 35 | 14000 | 80 | 72 | 75 | 508.4 | 0.547 | 18.4 | 278.2 | 33.6 | 39
RV35 | 35 | 14000 | 85 | 72 | 75 | 506.8 | 0.687 | 23.02 | 348 | 33.6 | 39
RV35 | 35 | 14000 | 90 | 72 | 75 | 505 | 0.826 | 27.59 | 417.1 | 33.5 | 39
RV35 | 35 | 14000 | 80 | 77 | 75 | 548.4 | 0.378 | 13.72 | 207.4 | 33.9 | 39
RV35 | 35 | 14000 | 85 | 77 | 75 | 546.9 | 0.508 | 18.36 | 277.6 | 33.8 | 39
RV35 | 35 | 14000 | 90 | 77 | 75 | 545 | 0.637 | 22.96 | 347.1 | 33.8 | 39
RV35 | 35 | 14000 | 65 | 57 | 85 | 381.1 | 0.727 | 18.31 | 276.9 | 36.5 | 39
RV35 | 35 | 14000 | 70 | 57 | 85 | 382 | 0.906 | 22.88 | 346 | 36.3 | 39
RV35 | 35 | 14000 | 75 | 57 | 85 | 393.9 | 0.995 | 25.93 | 392 | 36.3 | 39
RV35 | 35 | 14000 | 80 | 57 | 85 | 416.6 | 0.995 | 27.42 | 414.6 | 36.3 | 39
RV35 | 35 | 14000 | 85 | 57 | 85 | 439 | 0.995 | 28.9 | 436.9 | 36.3 | 39
RV35 | 35 | 14000 | 90 | 57 | 85 | 460.9 | 0.995 | 30.34 | 458.7 | 36.3 | 39
RV35 | 35 | 14000 | 65 | 62 | 85 | 414.6 | 0.498 | 13.64 | 206.3 | 36.8 | 39
RV35 | 35 | 14000 | 70 | 62 | 85 | 415.7 | 0.667 | 18.33 | 277.2 | 36.7 | 39
RV35 | 35 | 14000 | 75 | 62 | 85 | 416.1 | 0.836 | 23 | 347.8 | 36.5 | 39
RV35 | 35 | 14000 | 80 | 62 | 85 | 418.1 | 0.985 | 27.24 | 411.9 | 36.3 | 39
RV35 | 35 | 14000 | 85 | 62 | 85 | 439.1 | 0.995 | 28.9 | 437 | 36.3 | 39
RV35 | 35 | 14000 | 90 | 62 | 85 | 461.2 | 0.995 | 30.35 | 458.9 | 36.3 | 39
RV35 | 35 | 14000 | 70 | 67 | 85 | 451.9 | 0.458 | 13.68 | 206.9 | 37 | 39
RV35 | 35 | 14000 | 75 | 67 | 85 | 452.2 | 0.607 | 18.15 | 274.5 | 36.8 | 39
RV35 | 35 | 14000 | 80 | 67 | 85 | 451.9 | 0.766 | 22.9 | 346.3 | 36.6 | 39
RV35 | 35 | 14000 | 85 | 67 | 85 | 451.5 | 0.916 | 27.34 | 413.4 | 36.5 | 39
RV35 | 35 | 14000 | 90 | 67 | 85 | 461.4 | 0.995 | 30.36 | 459.1 | 36.4 | 39
RV35 | 35 | 14000 | 75 | 72 | 85 | 490.2 | 0.418 | 13.55 | 204.9 | 37.1 | 39
RV35 | 35 | 14000 | 80 | 72 | 85 | 489.6 | 0.557 | 18.05 | 272.9 | 36.9 | 39
RV35 | 35 | 14000 | 85 | 72 | 85 | 488.2 | 0.697 | 22.49 | 340.1 | 36.8 | 39
RV35 | 35 | 14000 | 90 | 72 | 85 | 487.2 | 0.846 | 27.26 | 412.1 | 36.6 | 39
RV35 | 35 | 14000 | 80 | 77 | 85 | 528.8 | 0.378 | 13.23 | 200 | 37.3 | 39
RV35 | 35 | 14000 | 85 | 77 | 85 | 527.8 | 0.517 | 18.06 | 273.1 | 37.1 | 39
RV35 | 35 | 14000 | 90 | 77 | 85 | 525.9 | 0.647 | 22.5 | 340.2 | 37 | 39
RV35 | 35 | 14000 | 65 | 57 | 95 | 363.5 | 0.736 | 17.71 | 267.7 | 39.9 | 40
RV35 | 35 | 14000 | 70 | 57 | 95 | 364.5 | 0.926 | 22.31 | 337.4 | 39.7 | 40
RV35 | 35 | 14000 | 75 | 57 | 95 | 379 | 0.995 | 24.94 | 377.1 | 39.7 | 40
RV35 | 35 | 14000 | 80 | 57 | 95 | 401.3 | 0.995 | 26.41 | 399.3 | 39.7 | 40
RV35 | 35 | 14000 | 85 | 57 | 95 | 423.5 | 0.995 | 27.88 | 421.5 | 39.8 | 40
RV35 | 35 | 14000 | 90 | 57 | 95 | 445.3 | 0.995 | 29.31 | 443.2 | 39.8 | 40
RV35 | 35 | 14000 | 65 | 62 | 95 | 395.5 | 0.498 | 13.02 | 196.8 | 40.3 | 40
RV35 | 35 | 14000 | 70 | 62 | 95 | 396.7 | 0.677 | 17.76 | 268.5 | 40.1 | 40
RV35 | 35 | 14000 | 75 | 62 | 95 | 397.2 | 0.846 | 22.22 | 336 | 39.9 | 40
RV35 | 35 | 14000 | 80 | 62 | 95 | 401.4 | 0.995 | 26.42 | 399.5 | 39.8 | 40
RV35 | 35 | 14000 | 85 | 62 | 95 | 423.7 | 0.995 | 27.88 | 421.6 | 39.8 | 40
RV35 | 35 | 14000 | 90 | 62 | 95 | 445.7 | 0.995 | 29.33 | 443.5 | 39.9 | 40
RV35 | 35 | 14000 | 70 | 67 | 95 | 431.2 | 0.458 | 13.06 | 197.4 | 40.6 | 40
RV35 | 35 | 14000 | 75 | 67 | 95 | 431.9 | 0.617 | 17.63 | 266.5 | 40.3 | 40
RV35 | 35 | 14000 | 80 | 67 | 95 | 432 | 0.776 | 22.18 | 335.3 | 40.2 | 40
RV35 | 35 | 14000 | 85 | 67 | 95 | 432.1 | 0.935 | 26.73 | 404.2 | 40 | 40
RV35 | 35 | 14000 | 90 | 67 | 95 | 445.7 | 0.995 | 29.34 | 443.6 | 39.9 | 40
RV35 | 35 | 14000 | 75 | 72 | 95 | 468.4 | 0.418 | 12.95 | 195.8 | 40.8 | 40
RV35 | 35 | 14000 | 80 | 72 | 95 | 468.4 | 0.567 | 17.57 | 265.7 | 40.5 | 40
RV35 | 35 | 14000 | 85 | 72 | 95 | 467.6 | 0.717 | 22.16 | 335.1 | 40.4 | 40
RV35 | 35 | 14000 | 90 | 72 | 95 | 466.9 | 0.856 | 26.43 | 399.6 | 40.2 | 40
RV35 | 35 | 14000 | 80 | 77 | 95 | 506.4 | 0.388 | 13 | 196.5 | 41 | 40
RV35 | 35 | 14000 | 85 | 77 | 95 | 505.9 | 0.517 | 17.31 | 261.8 | 40.7 | 40
RV35 | 35 | 14000 | 90 | 77 | 95 | 504.4 | 0.657 | 21.91 | 331.3 | 40.6 | 40
RV35 | 35 | 14000 | 65 | 57 | 105 | 345.2 | 0.756 | 17.27 | 261.1 | 43.5 | 40
RV35 | 35 | 14000 | 70 | 57 | 105 | 346.2 | 0.945 | 21.65 | 327.3 | 43.3 | 40
RV35 | 35 | 14000 | 75 | 57 | 105 | 363.2 | 0.995 | 23.9 | 361.4 | 43.3 | 40
RV35 | 35 | 14000 | 80 | 57 | 105 | 385.1 | 0.995 | 25.34 | 383.2 | 43.4 | 40
RV35 | 35 | 14000 | 85 | 57 | 105 | 407.1 | 0.995 | 26.79 | 405.1 | 43.5 | 40
RV35 | 35 | 14000 | 90 | 57 | 105 | 428.8 | 0.995 | 28.22 | 426.7 | 43.6 | 40
RV35 | 35 | 14000 | 65 | 62 | 105 | 375.6 | 0.507 | 12.61 | 190.6 | 44 | 40
RV35 | 35 | 14000 | 70 | 62 | 105 | 377.1 | 0.687 | 17.12 | 258.9 | 43.8 | 40
RV35 | 35 | 14000 | 75 | 62 | 105 | 377.8 | 0.866 | 21.63 | 327.1 | 43.6 | 40
RV35 | 35 | 14000 | 80 | 62 | 105 | 385.2 | 0.995 | 25.35 | 383.3 | 43.4 | 40
RV35 | 35 | 14000 | 85 | 62 | 105 | 407.2 | 0.995 | 26.81 | 405.3 | 43.5 | 40
RV35 | 35 | 14000 | 90 | 62 | 105 | 428.9 | 0.995 | 28.23 | 426.9 | 43.6 | 40
RV35 | 35 | 14000 | 70 | 67 | 105 | 409.7 | 0.458 | 12.41 | 187.6 | 44.3 | 40
RV35 | 35 | 14000 | 75 | 67 | 105 | 410.9 | 0.627 | 17.04 | 257.6 | 44 | 40
RV35 | 35 | 14000 | 80 | 67 | 105 | 411.2 | 0.796 | 21.65 | 327.4 | 43.8 | 40
RV35 | 35 | 14000 | 85 | 67 | 105 | 411.7 | 0.956 | 26.02 | 393.4 | 43.6 | 40
RV35 | 35 | 14000 | 90 | 67 | 105 | 429.1 | 0.995 | 28.25 | 427.1 | 43.6 | 40
RV35 | 35 | 14000 | 75 | 72 | 105 | 445.7 | 0.418 | 12.32 | 186.3 | 44.6 | 40
RV35 | 35 | 14000 | 80 | 72 | 105 | 446 | 0.577 | 17.02 | 257.4 | 44.3 | 40
RV35 | 35 | 14000 | 85 | 72 | 105 | 445.8 | 0.726 | 21.42 | 323.8 | 44.1 | 40
RV35 | 35 | 14000 | 90 | 72 | 105 | 445 | 0.886 | 26.06 | 394.1 | 43.9 | 40
RV35 | 35 | 14000 | 80 | 77 | 105 | 482.5 | 0.388 | 12.39 | 187.3 | 44.9 | 40
RV35 | 35 | 14000 | 85 | 77 | 105 | 482.7 | 0.527 | 16.84 | 254.6 | 44.6 | 40
RV35 | 35 | 14000 | 90 | 77 | 105 | 481.3 | 0.667 | 21.22 | 320.9 | 44.4 | 40
RV35 | 35 | 14000 | 65 | 57 | 115 | 325 | 0.766 | 16.47 | 249.1 | 47.5 | 41
RV35 | 35 | 14000 | 70 | 57 | 115 | 326.3 | 0.975 | 21.04 | 318.2 | 47.2 | 41
RV35 | 35 | 14000 | 75 | 57 | 115 | 345.5 | 0.995 | 22.74 | 343.8 | 47.4 | 41
RV35 | 35 | 14000 | 80 | 57 | 115 | 367 | 0.995 | 24.15 | 365.2 | 47.5 | 41
RV35 | 35 | 14000 | 85 | 57 | 115 | 388.8 | 0.995 | 25.59 | 386.9 | 47.7 | 41
RV35 | 35 | 14000 | 90 | 57 | 115 | 409.8 | 0.995 | 26.98 | 407.9 | 47.8 | 41
RV35 | 35 | 14000 | 65 | 62 | 115 | 353.8 | 0.508 | 11.88 | 179.6 | 48.3 | 41
RV35 | 35 | 14000 | 70 | 62 | 115 | 355.3 | 0.706 | 16.6 | 251 | 47.8 | 41
RV35 | 35 | 14000 | 75 | 62 | 115 | 356.2 | 0.896 | 21.1 | 319 | 47.6 | 41
RV35 | 35 | 14000 | 80 | 62 | 115 | 367.2 | 0.995 | 24.17 | 365.4 | 47.5 | 41
RV35 | 35 | 14000 | 85 | 62 | 115 | 388.6 | 0.995 | 25.58 | 386.8 | 47.7 | 41
RV35 | 35 | 14000 | 90 | 62 | 115 | 410 | 0.995 | 26.99 | 408.1 | 47.8 | 41
RV35 | 35 | 14000 | 70 | 67 | 115 | 387.1 | 0.468 | 11.98 | 181.1 | 48.5 | 41
RV35 | 35 | 14000 | 75 | 67 | 115 | 387.4 | 0.647 | 16.57 | 250.6 | 48.2 | 41
RV35 | 35 | 14000 | 80 | 67 | 115 | 388 | 0.816 | 20.94 | 316.6 | 47.9 | 41
RV35 | 35 | 14000 | 85 | 67 | 115 | 390.3 | 0.985 | 25.43 | 384.5 | 47.7 | 41
RV35 | 35 | 14000 | 90 | 67 | 115 | 410.1 | 0.995 | 27 | 408.2 | 47.8 | 41
RV35 | 35 | 14000 | 75 | 72 | 115 | 420.3 | 0.428 | 11.89 | 179.8 | 48.9 | 41
RV35 | 35 | 14000 | 80 | 72 | 115 | 421.2 | 0.587 | 16.36 | 247.3 | 48.5 | 41
RV35 | 35 | 14000 | 85 | 72 | 115 | 421 | 0.746 | 20.78 | 314.2 | 48.2 | 41
RV35 | 35 | 14000 | 90 | 72 | 115 | 420.7 | 0.916 | 25.48 | 385.2 | 48 | 41
RV35 | 35 | 14000 | 80 | 77 | 115 | 455.8 | 0.388 | 11.7 | 176.9 | 49.2 | 41
RV35 | 35 | 14000 | 85 | 77 | 115 | 456.4 | 0.537 | 16.22 | 245.3 | 48.8 | 41
RV35 | 35 | 14000 | 90 | 77 | 115 | 455.7 | 0.687 | 20.69 | 312.9 | 48.6 | 41
RV35 | 35 | 14000 | 65 | 57 | 125 | 303.8 | 0.786 | 15.8 | 238.9 | 11.8 | 41
RV35 | 35 | 14000 | 70 | 57 | 125 | 306.5 | 0.995 | 20.17 | 305 | 11.8 | 41
RV35 | 35 | 14000 | 75 | 57 | 125 | 326.8 | 0.995 | 21.51 | 325.3 | 11.8 | 41
RV35 | 35 | 14000 | 80 | 57 | 125 | 347.7 | 0.995 | 22.89 | 346.1 | 11.8 | 41
RV35 | 35 | 14000 | 85 | 57 | 125 | 368.7 | 0.995 | 24.27 | 366.9 | 11.8 | 41
RV35 | 35 | 14000 | 90 | 57 | 125 | 389.5 | 0.995 | 25.64 | 387.7 | 11.8 | 41
RV35 | 35 | 14000 | 65 | 62 | 125 | 330.8 | 0.518 | 11.32 | 171.2 | 11.8 | 41
RV35 | 35 | 14000 | 70 | 62 | 125 | 332.8 | 0.717 | 15.77 | 238.5 | 11.8 | 41
RV35 | 35 | 14000 | 75 | 62 | 125 | 333.5 | 0.926 | 20.42 | 308.7 | 11.8 | 41
RV35 | 35 | 14000 | 80 | 62 | 125 | 347.9 | 0.995 | 22.9 | 346.2 | 11.8 | 41
RV35 | 35 | 14000 | 85 | 62 | 125 | 368.9 | 0.995 | 24.28 | 367.1 | 11.8 | 41
RV35 | 35 | 14000 | 90 | 62 | 125 | 389.7 | 0.995 | 25.65 | 387.8 | 11.8 | 41
RV35 | 35 | 14000 | 70 | 67 | 125 | 362 | 0.468 | 11.2 | 169.3 | 11.8 | 41
RV35 | 35 | 14000 | 75 | 67 | 125 | 363.4 | 0.657 | 15.79 | 238.7 | 11.8 | 41
RV35 | 35 | 14000 | 80 | 67 | 125 | 363.9 | 0.846 | 20.36 | 307.8 | 11.8 | 41
RV35 | 35 | 14000 | 85 | 67 | 125 | 369.1 | 0.995 | 24.29 | 367.3 | 11.8 | 41
RV35 | 35 | 14000 | 90 | 67 | 125 | 389.9 | 0.995 | 25.66 | 388 | 11.8 | 41
RV35 | 35 | 14000 | 75 | 72 | 125 | 396.1 | 0.428 | 11.21 | 169.5 | 11.8 | 41
RV35 | 35 | 14000 | 80 | 72 | 125 | 395 | 0.607 | 15.86 | 239.8 | 11.8 | 41
RV35 | 35 | 14000 | 85 | 72 | 125 | 395.1 | 0.776 | 20.28 | 306.7 | 11.8 | 41
RV35 | 35 | 14000 | 90 | 72 | 125 | 395.4 | 0.945 | 24.72 | 373.8 | 11.8 | 41
RV35 | 35 | 14000 | 80 | 77 | 125 | 427.6 | 0.398 | 11.26 | 170.2 | 11.8 | 41
RV35 | 35 | 14000 | 85 | 77 | 125 | 428.7 | 0.557 | 15.8 | 238.9 | 11.8 | 41
RV35 | 35 | 14000 | 90 | 77 | 125 | 428.2 | 0.716 | 20.29 | 306.8 | 11.8 | 41
RV35 | 35 | 15750 | 65 | 57 | 75 | 404.4 | 0.746 | 17.74 | 301.8 | 36.4 | 39
RV35 | 35 | 15750 | 70 | 57 | 75 | 405.9 | 0.926 | 22.09 | 375.7 | 36.2 | 39
RV35 | 35 | 15750 | 75 | 57 | 75 | 421.8 | 0.995 | 24.68 | 419.8 | 36.1 | 39
RV35 | 35 | 15750 | 80 | 57 | 75 | 445.5 | 0.995 | 26.07 | 443.4 | 36.1 | 39
RV35 | 35 | 15750 | 85 | 57 | 75 | 468.9 | 0.995 | 27.43 | 466.6 | 36.1 | 39
RV35 | 35 | 15750 | 90 | 57 | 75 | 491.5 | 0.995 | 28.75 | 489.1 | 36.2 | 39
RV35 | 35 | 15750 | 65 | 62 | 75 | 440.2 | 0.507 | 13.13 | 223.4 | 36.6 | 39
RV35 | 35 | 15750 | 70 | 62 | 75 | 441 | 0.677 | 17.54 | 298.4 | 36.4 | 39
RV35 | 35 | 15750 | 75 | 62 | 75 | 441.1 | 0.856 | 22.19 | 377.5 | 36.3 | 39
RV35 | 35 | 15750 | 80 | 62 | 75 | 445.8 | 0.995 | 26.08 | 443.6 | 36.1 | 39
RV35 | 35 | 15750 | 85 | 62 | 75 | 469 | 0.995 | 27.44 | 466.7 | 36.1 | 39
RV35 | 35 | 15750 | 90 | 62 | 75 | 491.7 | 0.995 | 28.77 | 489.3 | 36.2 | 39
RV35 | 35 | 15750 | 70 | 67 | 75 | 478.5 | 0.458 | 12.87 | 219 | 36.7 | 39
RV35 | 35 | 15750 | 75 | 67 | 75 | 478.5 | 0.627 | 17.64 | 300 | 36.5 | 39
RV35 | 35 | 15750 | 80 | 67 | 75 | 478 | 0.786 | 22.09 | 375.8 | 36.4 | 39
RV35 | 35 | 15750 | 85 | 67 | 75 | 476.9 | 0.945 | 26.51 | 450.9 | 36.2 | 39
RV35 | 35 | 15750 | 90 | 67 | 75 | 492 | 0.995 | 28.79 | 489.7 | 36.2 | 39
RV35 | 35 | 15750 | 75 | 72 | 75 | 517.5 | 0.418 | 12.72 | 216.3 | 36.8 | 39
RV35 | 35 | 15750 | 80 | 72 | 75 | 516.5 | 0.567 | 17.23 | 293 | 36.6 | 39
RV35 | 35 | 15750 | 85 | 72 | 75 | 515 | 0.717 | 21.69 | 369 | 36.5 | 39
RV35 | 35 | 15750 | 90 | 72 | 75 | 512.9 | 0.876 | 26.41 | 449.2 | 36.4 | 39
RV35 | 35 | 15750 | 80 | 77 | 75 | 556.6 | 0.388 | 12.7 | 216 | 36.9 | 39
RV35 | 35 | 15750 | 85 | 77 | 75 | 555 | 0.527 | 17.21 | 292.7 | 36.8 | 39
RV35 | 35 | 15750 | 90 | 77 | 75 | 553.1 | 0.667 | 21.68 | 368.8 | 36.7 | 39
RV35 | 35 | 15750 | 65 | 57 | 85 | 388.3 | 0.756 | 17.27 | 293.7 | 14.7 | 39
RV35 | 35 | 15750 | 70 | 57 | 85 | 389.9 | 0.945 | 21.67 | 368.6 | 14.7 | 39
RV35 | 35 | 15750 | 75 | 57 | 85 | 408.3 | 0.995 | 23.89 | 406.3 | 14.7 | 39
RV35 | 35 | 15750 | 80 | 57 | 85 | 432.1 | 0.995 | 25.28 | 430 | 14.7 | 39
RV35 | 35 | 15750 | 85 | 57 | 85 | 455.3 | 0.995 | 26.64 | 453.1 | 14.7 | 39
RV35 | 35 | 15750 | 90 | 57 | 85 | 478.3 | 0.995 | 27.98 | 476 | 14.7 | 39
RV35 | 35 | 15750 | 65 | 62 | 85 | 422.8 | 0.508 | 12.62 | 214.6 | 14.7 | 39
RV35 | 35 | 15750 | 70 | 62 | 85 | 423.9 | 0.687 | 17.11 | 291.1 | 14.7 | 39
RV35 | 35 | 15750 | 75 | 62 | 85 | 424.3 | 0.876 | 21.85 | 371.6 | 14.7 | 39
RV35 | 35 | 15750 | 80 | 62 | 85 | 432.2 | 0.995 | 25.29 | 430.1 | 14.7 | 39
RV35 | 35 | 15750 | 85 | 62 | 85 | 455.6 | 0.995 | 26.65 | 453.4 | 14.7 | 39
RV35 | 35 | 15750 | 90 | 62 | 85 | 478.5 | 0.995 | 28 | 476.2 | 14.7 | 39
RV35 | 35 | 15750 | 70 | 67 | 85 | 460.2 | 0.458 | 12.38 | 210.6 | 14.7 | 39
RV35 | 35 | 15750 | 75 | 67 | 85 | 460.6 | 0.627 | 16.98 | 288.8 | 14.7 | 39
RV35 | 35 | 15750 | 80 | 67 | 85 | 460.5 | 0.796 | 21.55 | 366.6 | 14.7 | 39
RV35 | 35 | 15750 | 85 | 67 | 85 | 460.4 | 0.965 | 26.13 | 444.4 | 14.7 | 39
RV35 | 35 | 15750 | 90 | 67 | 85 | 478.6 | 0.995 | 28 | 476.3 | 14.7 | 39
RV35 | 35 | 15750 | 75 | 72 | 85 | 498.5 | 0.428 | 12.54 | 213.3 | 14.7 | 39
RV35 | 35 | 15750 | 80 | 72 | 85 | 498.1 | 0.577 | 16.9 | 287.5 | 14.7 | 39
RV35 | 35 | 15750 | 85 | 72 | 85 | 497.2 | 0.736 | 21.52 | 366.1 | 14.7 | 39
RV35 | 35 | 15750 | 90 | 72 | 85 | 495.6 | 0.886 | 25.81 | 439 | 14.7 | 39
RV35 | 35 | 15750 | 80 | 77 | 85 | 537.3 | 0.388 | 12.26 | 208.5 | 14.7 | 39
RV35 | 35 | 15750 | 85 | 77 | 85 | 536.4 | 0.527 | 16.63 | 282.9 | 14.7 | 39
RV35 | 35 | 15750 | 90 | 77 | 85 | 534.1 | 0.677 | 21.25 | 361.4 | 14.7 | 39
RV35 | 35 | 15750 | 65 | 57 | 95 | 371.1 | 0.766 | 16.72 | 284.4 | 42.9 | 40
RV35 | 35 | 15750 | 70 | 57 | 95 | 373.1 | 0.965 | 21.17 | 360.1 | 42.7 | 40
RV35 | 35 | 15750 | 75 | 57 | 95 | 393.4 | 0.995 | 23.02 | 391.5 | 42.7 | 40
RV35 | 35 | 15750 | 80 | 57 | 95 | 416.8 | 0.995 | 24.38 | 414.7 | 42.8 | 40
RV35 | 35 | 15750 | 85 | 57 | 95 | 440 | 0.995 | 25.74 | 437.9 | 42.8 | 40
RV35 | 35 | 15750 | 90 | 57 | 95 | 462.9 | 0.995 | 27.08 | 460.6 | 42.9 | 40
RV35 | 35 | 15750 | 65 | 62 | 95 | 403.9 | 0.508 | 12.05 | 205 | 43.4 | 40
RV35 | 35 | 15750 | 70 | 62 | 95 | 405.2 | 0.697 | 16.6 | 282.3 | 43.1 | 40
RV35 | 35 | 15750 | 75 | 62 | 95 | 405.9 | 0.896 | 21.37 | 363.5 | 42.9 | 40
RV35 | 35 | 15750 | 80 | 62 | 95 | 417 | 0.995 | 24.4 | 415 | 42.8 | 40
RV35 | 35 | 15750 | 85 | 62 | 95 | 440.1 | 0.995 | 25.75 | 438 | 42.8 | 40
RV35 | 35 | 15750 | 90 | 62 | 95 | 463.1 | 0.995 | 27.1 | 460.9 | 42.9 | 40
RV35 | 35 | 15750 | 70 | 67 | 95 | 440 | 0.468 | 12.1 | 205.8 | 43.6 | 40
RV35 | 35 | 15750 | 75 | 67 | 95 | 441 | 0.637 | 16.51 | 280.9 | 43.3 | 40
RV35 | 35 | 15750 | 80 | 67 | 95 | 441.4 | 0.816 | 21.18 | 360.2 | 43.1 | 40
RV35 | 35 | 15750 | 85 | 67 | 95 | 442.2 | 0.975 | 25.36 | 431.3 | 42.9 | 40
RV35 | 35 | 15750 | 90 | 67 | 95 | 463.3 | 0.995 | 27.11 | 461.1 | 42.9 | 40
RV35 | 35 | 15750 | 75 | 72 | 95 | 477.1 | 0.428 | 12 | 204.1 | 43.8 | 40
RV35 | 35 | 15750 | 80 | 72 | 95 | 477 | 0.587 | 16.47 | 280.1 | 43.5 | 40
RV35 | 35 | 15750 | 85 | 72 | 95 | 476.6 | 0.746 | 20.91 | 355.7 | 43.3 | 40
RV35 | 35 | 15750 | 90 | 72 | 95 | 475.8 | 0.906 | 25.33 | 430.9 | 43.1 | 40
RV35 | 35 | 15750 | 80 | 77 | 95 | 514.9 | 0.388 | 11.75 | 199.9 | 44 | 40
RV35 | 35 | 15750 | 85 | 77 | 95 | 514.6 | 0.538 | 16.26 | 276.6 | 43.7 | 40
RV35 | 35 | 15750 | 90 | 77 | 95 | 512.8 | 0.687 | 20.7 | 352.1 | 43.5 | 40
RV35 | 35 | 15750 | 65 | 57 | 105 | 353.4 | 0.776 | 16.13 | 274.3 | 46.4 | 40
RV35 | 35 | 15750 | 70 | 57 | 105 | 355.8 | 0.995 | 20.82 | 354.1 | 46.3 | 40
RV35 | 35 | 15750 | 75 | 57 | 105 | 377.8 | 0.995 | 22.1 | 376 | 46.4 | 40
RV35 | 35 | 15750 | 80 | 57 | 105 | 400.7 | 0.995 | 23.44 | 398.7 | 46.5 | 40
RV35 | 35 | 15750 | 85 | 57 | 105 | 423.5 | 0.995 | 24.78 | 421.5 | 46.6 | 40
RV35 | 35 | 15750 | 90 | 57 | 105 | 446 | 0.995 | 26.1 | 443.9 | 46.6 | 40
RV35 | 35 | 15750 | 65 | 62 | 105 | 384.5 | 0.518 | 11.7 | 199 | 47 | 40
RV35 | 35 | 15750 | 70 | 62 | 105 | 385.8 | 0.716 | 16.25 | 276.4 | 46.8 | 40
RV35 | 35 | 15750 | 75 | 62 | 105 | 387 | 0.916 | 20.83 | 354.3 | 46.5 | 40
RV35 | 35 | 15750 | 80 | 62 | 105 | 400.9 | 0.995 | 23.45 | 398.9 | 46.5 | 40
RV35 | 35 | 15750 | 85 | 62 | 105 | 423.7 | 0.995 | 24.79 | 421.7 | 46.6 | 40
RV35 | 35 | 15750 | 90 | 62 | 105 | 446.4 | 0.995 | 26.11 | 444.2 | 46.6 | 40
RV35 | 35 | 15750 | 70 | 67 | 105 | 418.8 | 0.468 | 11.52 | 195.9 | 47.4 | 40
RV35 | 35 | 15750 | 75 | 67 | 105 | 420.2 | 0.657 | 16.23 | 276 | 47.1 | 40
RV35 | 35 | 15750 | 80 | 67 | 105 | 420.3 | 0.836 | 20.66 | 351.4 | 46.8 | 40
RV35 | 35 | 15750 | 85 | 67 | 105 | 423.8 | 0.995 | 24.8 | 421.8 | 46.6 | 40
RV35 | 35 | 15750 | 90 | 67 | 105 | 446.4 | 0.995 | 26.11 | 444.2 | 46.6 | 40
RV35 | 35 | 15750 | 75 | 72 | 105 | 454.7 | 0.428 | 11.44 | 194.6 | 47.7 | 40
RV35 | 35 | 15750 | 80 | 72 | 105 | 455.1 | 0.597 | 15.97 | 271.7 | 47.3 | 40
RV35 | 35 | 15750 | 85 | 72 | 105 | 454.7 | 0.766 | 20.49 | 348.5 | 47.1 | 40
RV35 | 35 | 15750 | 90 | 72 | 105 | 454.5 | 0.935 | 24.99 | 425.1 | 46.8 | 40
RV35 | 35 | 15750 | 80 | 77 | 105 | 490.8 | 0.398 | 11.49 | 195.4 | 47.9 | 40
RV35 | 35 | 15750 | 85 | 77 | 105 | 491.3 | 0.547 | 15.81 | 268.9 | 47.6 | 40
RV35 | 35 | 15750 | 90 | 77 | 105 | 490.2 | 0.706 | 20.36 | 346.3 | 47.3 | 40
RV35 | 35 | 15750 | 65 | 57 | 115 | 333.5 | 0.796 | 15.61 | 265.5 | 50.5 | 41
RV35 | 35 | 15750 | 70 | 57 | 115 | 338.3 | 0.995 | 19.79 | 336.7 | 50.3 | 41
RV35 | 35 | 15750 | 75 | 57 | 115 | 360.1 | 0.995 | 21.07 | 358.4 | 50.4 | 41
RV35 | 35 | 15750 | 80 | 57 | 115 | 382.4 | 0.995 | 22.37 | 380.5 | 50.6 | 41
RV35 | 35 | 15750 | 85 | 57 | 115 | 404.7 | 0.995 | 23.67 | 402.7 | 50.7 | 41
RV35 | 35 | 15750 | 90 | 57 | 115 | 426.8 | 0.995 | 24.97 | 424.8 | 50.8 | 41
RV35 | 35 | 15750 | 65 | 62 | 115 | 362.8 | 0.517 | 11.03 | 187.7 | 51.3 | 41
RV35 | 35 | 15750 | 70 | 62 | 115 | 364.4 | 0.727 | 15.57 | 264.8 | 50.8 | 41
RV35 | 35 | 15750 | 75 | 62 | 115 | 365.5 | 0.946 | 20.32 | 345.6 | 50.6 | 41
RV35 | 35 | 15750 | 80 | 62 | 115 | 382.5 | 0.995 | 22.38 | 380.7 | 50.6 | 41
RV35 | 35 | 15750 | 85 | 62 | 115 | 405.1 | 0.995 | 23.7 | 403.2 | 50.7 | 41
RV35 | 35 | 15750 | 90 | 62 | 115 | 427 | 0.995 | 24.99 | 425 | 50.8 | 41
RV35 | 35 | 15750 | 70 | 67 | 115 | 395.4 | 0.478 | 11.11 | 188.9 | 51.6 | 41
RV35 | 35 | 15750 | 75 | 67 | 115 | 397.2 | 0.667 | 15.57 | 264.8 | 51.2 | 41
RV35 | 35 | 15750 | 80 | 67 | 115 | 397.3 | 0.866 | 20.22 | 344 | 50.9 | 41
RV35 | 35 | 15750 | 85 | 67 | 115 | 405.1 | 0.995 | 23.7 | 403.1 | 50.7 | 41
RV35 | 35 | 15750 | 90 | 67 | 115 | 427.3 | 0.995 | 25 | 425.2 | 50.8 | 41
RV35 | 35 | 15750 | 75 | 72 | 115 | 429.2 | 0.438 | 11.05 | 188 | 51.9 | 41
RV35 | 35 | 15750 | 80 | 72 | 115 | 430.5 | 0.617 | 15.61 | 265.6 | 51.5 | 41
RV35 | 35 | 15750 | 85 | 72 | 115 | 430.4 | 0.796 | 20.14 | 342.6 | 51.3 | 41
RV35 | 35 | 15750 | 90 | 72 | 115 | 430.4 | 0.965 | 24.42 | 415.4 | 50.9 | 41
RV35 | 35 | 15750 | 80 | 77 | 115 | 464.3 | 0.398 | 10.86 | 184.8 | 52.3 | 41
RV35 | 35 | 15750 | 85 | 77 | 115 | 465.2 | 0.567 | 15.51 | 263.9 | 51.8 | 41
RV35 | 35 | 15750 | 90 | 77 | 115 | 463.8 | 0.726 | 19.81 | 336.9 | 51.5 | 41
RV35 | 35 | 15750 | 65 | 57 | 125 | 312.7 | 0.826 | 15.19 | 258.3 | 14.7 | 41
RV35 | 35 | 15750 | 70 | 57 | 125 | 320.4 | 0.995 | 18.74 | 318.8 | 14.7 | 41
RV35 | 35 | 15750 | 75 | 57 | 125 | 341.5 | 0.995 | 19.98 | 339.9 | 14.7 | 41
RV35 | 35 | 15750 | 80 | 57 | 125 | 363 | 0.995 | 21.23 | 361.2 | 14.7 | 41
RV35 | 35 | 15750 | 85 | 57 | 125 | 384.7 | 0.995 | 22.5 | 382.8 | 14.7 | 41
RV35 | 35 | 15750 | 90 | 57 | 125 | 406.3 | 0.995 | 23.77 | 404.3 | 14.7 | 41
RV35 | 35 | 15750 | 65 | 62 | 125 | 339.7 | 0.528 | 10.53 | 179.2 | 14.7 | 41
RV35 | 35 | 15750 | 70 | 62 | 125 | 342.1 | 0.756 | 15.21 | 258.7 | 14.7 | 41
RV35 | 35 | 15750 | 75 | 62 | 125 | 343.5 | 0.975 | 19.69 | 335 | 14.7 | 41
RV35 | 35 | 15750 | 80 | 62 | 125 | 363.2 | 0.995 | 21.25 | 361.4 | 14.7 | 41
RV35 | 35 | 15750 | 85 | 62 | 125 | 384.8 | 0.995 | 22.52 | 383 | 14.7 | 41
RV35 | 35 | 15750 | 90 | 62 | 125 | 406.5 | 0.995 | 23.78 | 404.5 | 14.7 | 41
RV35 | 35 | 15750 | 70 | 67 | 125 | 371.5 | 0.478 | 10.44 | 177.5 | 14.7 | 41
RV35 | 35 | 15750 | 75 | 67 | 125 | 373.1 | 0.687 | 15.06 | 256.2 | 14.7 | 41
RV35 | 35 | 15750 | 80 | 67 | 125 | 373.4 | 0.896 | 19.66 | 334.5 | 14.7 | 41
RV35 | 35 | 15750 | 85 | 67 | 125 | 385 | 0.995 | 22.52 | 383.1 | 14.7 | 41
RV35 | 35 | 15750 | 90 | 67 | 125 | 406.6 | 0.995 | 23.79 | 404.6 | 14.7 | 41
RV35 | 35 | 15750 | 75 | 72 | 125 | 403.6 | 0.438 | 10.39 | 176.7 | 14.7 | 41
RV35 | 35 | 15750 | 80 | 72 | 125 | 404.5 | 0.627 | 14.91 | 253.6 | 14.7 | 41
RV35 | 35 | 15750 | 85 | 72 | 125 | 404.7 | 0.816 | 19.41 | 330.2 | 14.7 | 41
RV35 | 35 | 15750 | 90 | 72 | 125 | 407 | 0.995 | 23.81 | 405 | 14.7 | 41
RV35 | 35 | 15750 | 80 | 77 | 125 | 436.6 | 0.398 | 10.22 | 173.8 | 14.7 | 41
RV35 | 35 | 15750 | 85 | 77 | 125 | 437.6 | 0.577 | 14.85 | 252.6 | 14.7 | 41
RV35 | 35 | 15750 | 90 | 77 | 125 | 437 | 0.756 | 19.43 | 330.5 | 14.7 | 41
RV40 | 40 | 10000 | 65 | 57 | 75 | 380.1 | 0.678 | 23.87 | 257.8 | 27.2 | 42
RV40 | 40 | 10000 | 70 | 57 | 75 | 378 | 0.82 | 28.69 | 309.9 | 27 | 42
RV40 | 40 | 10000 | 75 | 57 | 75 | 375.8 | 0.952 | 33.11 | 357.6 | 26.8 | 42
RV40 | 40 | 10000 | 80 | 57 | 75 | 385.5 | 1 | 35.69 | 385.5 | 26.6 | 42
RV40 | 40 | 10000 | 85 | 57 | 75 | 403.7 | 1 | 37.38 | 403.7 | 26.4 | 42
RV40 | 40 | 10000 | 90 | 57 | 75 | 421.8 | 1 | 39.06 | 421.8 | 26.4 | 42
RV40 | 40 | 10000 | 65 | 62 | 75 | 418.4 | 0.496 | 19.22 | 207.6 | 27.4 | 42
RV40 | 40 | 10000 | 70 | 62 | 75 | 416.5 | 0.618 | 23.81 | 257.2 | 27.1 | 42
RV40 | 40 | 10000 | 75 | 62 | 75 | 414.3 | 0.749 | 28.74 | 310.4 | 26.9 | 42
RV40 | 40 | 10000 | 80 | 62 | 75 | 412.1 | 0.871 | 33.22 | 358.8 | 26.7 | 42
RV40 | 40 | 10000 | 85 | 62 | 75 | 410.2 | 0.992 | 37.69 | 407 | 26.4 | 42
RV40 | 40 | 10000 | 90 | 62 | 75 | 425 | 1 | 39.35 | 425 | 26.4 | 42
RV40 | 40 | 10000 | 70 | 67 | 75 | 458.5 | 0.456 | 19.34 | 208.9 | 27.2 | 42
RV40 | 40 | 10000 | 75 | 67 | 75 | 456.2 | 0.567 | 23.94 | 258.6 | 26.9 | 42
RV40 | 40 | 10000 | 80 | 67 | 75 | 453.5 | 0.678 | 28.48 | 307.6 | 26.7 | 42
RV40 | 40 | 10000 | 85 | 67 | 75 | 450.4 | 0.8 | 33.35 | 360.2 | 26.6 | 42
RV40 | 40 | 10000 | 90 | 67 | 75 | 448.1 | 0.911 | 37.81 | 408.3 | 26.6 | 42
RV40 | 40 | 10000 | 75 | 72 | 75 | 501.2 | 0.415 | 19.26 | 208 | 27 | 42
RV40 | 40 | 10000 | 80 | 72 | 75 | 498.3 | 0.516 | 23.82 | 257.3 | 26.8 | 42
RV40 | 40 | 10000 | 85 | 72 | 75 | 495.3 | 0.628 | 28.79 | 310.9 | 26.8 | 42
RV40 | 40 | 10000 | 90 | 72 | 75 | 492 | 0.729 | 33.2 | 358.6 | 26.7 | 42
RV40 | 40 | 10000 | 80 | 77 | 75 | 548.2 | 0.374 | 19.01 | 205.3 | 27 | 42
RV40 | 40 | 10000 | 85 | 77 | 75 | 544.6 | 0.476 | 23.99 | 259.1 | 27 | 42
RV40 | 40 | 10000 | 90 | 77 | 75 | 541 | 0.567 | 28.4 | 306.7 | 26.9 | 42
RV40 | 40 | 10000 | 65 | 57 | 85 | 364.2 | 0.688 | 23.21 | 250.7 | 30.9 | 42
RV40 | 40 | 10000 | 70 | 57 | 85 | 362.1 | 0.83 | 27.83 | 300.6 | 30.6 | 42
RV40 | 40 | 10000 | 75 | 57 | 85 | 360.3 | 0.972 | 32.43 | 350.2 | 30.3 | 42
RV40 | 40 | 10000 | 80 | 57 | 85 | 372.6 | 1 | 34.5 | 372.6 | 30.1 | 42
RV40 | 40 | 10000 | 85 | 57 | 85 | 390.6 | 1 | 36.17 | 390.6 | 30 | 42
RV40 | 40 | 10000 | 90 | 57 | 85 | 408.5 | 1 | 37.82 | 408.5 | 29.8 | 42
RV40 | 40 | 10000 | 65 | 62 | 85 | 401 | 0.496 | 18.42 | 198.9 | 31.2 | 42
RV40 | 40 | 10000 | 70 | 62 | 85 | 399.3 | 0.628 | 23.2 | 250.6 | 30.6 | 42
RV40 | 40 | 10000 | 75 | 62 | 85 | 397.4 | 0.759 | 27.94 | 301.8 | 30.5 | 42
RV40 | 40 | 10000 | 80 | 62 | 85 | 395.6 | 0.881 | 32.26 | 348.4 | 30.3 | 42
RV40 | 40 | 10000 | 85 | 62 | 85 | 395.2 | 1 | 36.59 | 395.2 | 30 | 42
RV40 | 40 | 10000 | 90 | 62 | 85 | 411.6 | 1 | 38.11 | 411.6 | 29.9 | 42
RV40 | 40 | 10000 | 70 | 67 | 85 | 439.9 | 0.456 | 18.56 | 200.4 | 31 | 42
RV40 | 40 | 10000 | 75 | 67 | 85 | 437.9 | 0.577 | 23.4 | 252.7 | 30.7 | 42
RV40 | 40 | 10000 | 80 | 67 | 85 | 435.5 | 0.688 | 27.76 | 299.8 | 30.4 | 42
RV40 | 40 | 10000 | 85 | 67 | 85 | 432.6 | 0.81 | 32.44 | 350.4 | 30.2 | 42
RV40 | 40 | 10000 | 90 | 67 | 85 | 430.4 | 0.931 | 37.12 | 400.9 | 30 | 42
RV40 | 40 | 10000 | 75 | 72 | 85 | 481.4 | 0.415 | 18.5 | 199.8 | 30.9 | 42
RV40 | 40 | 10000 | 80 | 72 | 85 | 479 | 0.527 | 23.35 | 252.2 | 30.6 | 42
RV40 | 40 | 10000 | 85 | 72 | 85 | 476.2 | 0.628 | 27.68 | 298.9 | 30.3 | 42
RV40 | 40 | 10000 | 90 | 72 | 85 | 472.8 | 0.739 | 32.35 | 349.4 | 30.1 | 42
RV40 | 40 | 10000 | 80 | 77 | 85 | 526.7 | 0.375 | 18.27 | 197.3 | 30.7 | 42
RV40 | 40 | 10000 | 85 | 77 | 85 | 523.3 | 0.476 | 23.06 | 249 | 30.4 | 42
RV40 | 40 | 10000 | 90 | 77 | 85 | 519.9 | 0.577 | 27.78 | 300 | 30.2 | 42
RV40 | 40 | 10000 | 65 | 57 | 95 | 346.9 | 0.688 | 22.11 | 238.8 | 35.3 | 42
RV40 | 40 | 10000 | 70 | 57 | 95 | 345.1 | 0.84 | 26.85 | 290 | 34.8 | 42
RV40 | 40 | 10000 | 75 | 57 | 95 | 343.7 | 0.992 | 31.57 | 341 | 34.3 | 42
RV40 | 40 | 10000 | 80 | 57 | 95 | 358.7 | 1 | 33.21 | 358.7 | 34.2 | 42
RV40 | 40 | 10000 | 85 | 57 | 95 | 376.5 | 1 | 34.86 | 376.5 | 34 | 42
RV40 | 40 | 10000 | 90 | 57 | 95 | 394.1 | 1 | 36.49 | 394.1 | 33.9 | 42
RV40 | 40 | 10000 | 65 | 62 | 95 | 382 | 0.496 | 17.55 | 189.5 | 35.8 | 42
RV40 | 40 | 10000 | 70 | 62 | 95 | 381 | 0.638 | 22.5 | 243 | 35.1 | 42
RV40 | 40 | 10000 | 75 | 62 | 95 | 379.2 | 0.769 | 27.01 | 291.7 | 34.8 | 42
RV40 | 40 | 10000 | 80 | 62 | 95 | 377.3 | 0.901 | 31.47 | 339.9 | 34.4 | 42
RV40 | 40 | 10000 | 85 | 62 | 95 | 379.3 | 1 | 35.12 | 379.3 | 34 | 42
RV40 | 40 | 10000 | 90 | 62 | 95 | 397.2 | 1 | 36.78 | 397.2 | 33.9 | 42
RV40 | 40 | 10000 | 70 | 67 | 95 | 419.6 | 0.456 | 17.7 | 191.2 | 35.5 | 42
RV40 | 40 | 10000 | 75 | 67 | 95 | 418.2 | 0.577 | 22.34 | 241.3 | 35 | 42
RV40 | 40 | 10000 | 80 | 67 | 95 | 415.9 | 0.698 | 26.9 | 290.5 | 34.6 | 42
RV40 | 40 | 10000 | 85 | 67 | 95 | 413.6 | 0.82 | 31.41 | 339.2 | 34.3 | 42
RV40 | 40 | 10000 | 90 | 67 | 95 | 411.4 | 0.952 | 36.25 | 391.5 | 34 | 42
RV40 | 40 | 10000 | 75 | 72 | 95 | 459.7 | 0.415 | 17.67 | 190.8 | 35.3 | 42
RV40 | 40 | 10000 | 80 | 72 | 95 | 457.8 | 0.526 | 22.31 | 241 | 34.9 | 42
RV40 | 40 | 10000 | 85 | 72 | 95 | 455.2 | 0.638 | 26.88 | 290.3 | 34.5 | 42
RV40 | 40 | 10000 | 90 | 72 | 95 | 452 | 0.749 | 31.35 | 338.6 | 34.3 | 42
RV40 | 40 | 10000 | 80 | 77 | 95 | 503.3 | 0.385 | 17.93 | 193.6 | 35.1 | 42
RV40 | 40 | 10000 | 85 | 77 | 95 | 500.2 | 0.486 | 22.51 | 243.1 | 34.7 | 42
RV40 | 40 | 10000 | 90 | 77 | 95 | 497.1 | 0.587 | 27.03 | 291.9 | 34.4 | 42
RV40 | 40 | 10000 | 65 | 57 | 105 | 328.5 | 0.698 | 21.24 | 229.4 | 40.2 | 43
RV40 | 40 | 10000 | 70 | 57 | 105 | 327.4 | 0.86 | 26.08 | 281.7 | 39.5 | 43
RV40 | 40 | 10000 | 75 | 57 | 105 | 327.3 | 1 | 30.31 | 327.3 | 39 | 43
RV40 | 40 | 10000 | 80 | 57 | 105 | 343.7 | 1 | 31.82 | 343.7 | 38.8 | 43
RV40 | 40 | 10000 | 85 | 57 | 105 | 361.5 | 1 | 33.47 | 361.5 | 38.5 | 43
RV40 | 40 | 10000 | 90 | 57 | 105 | 379.1 | 1 | 35.1 | 379.1 | 38.3 | 43
RV40 | 40 | 10000 | 65 | 62 | 105 | 362.3 | 0.496 | 16.64 | 179.7 | 41.1 | 43
RV40 | 40 | 10000 | 70 | 62 | 105 | 361.5 | 0.638 | 21.35 | 230.6 | 40 | 43
RV40 | 40 | 10000 | 75 | 62 | 105 | 359.8 | 0.78 | 25.97 | 280.5 | 39.5 | 43
RV40 | 40 | 10000 | 80 | 62 | 105 | 358.5 | 0.921 | 30.58 | 330.3 | 39 | 43
RV40 | 40 | 10000 | 85 | 62 | 105 | 364.3 | 1 | 33.73 | 364.3 | 38.5 | 43
RV40 | 40 | 10000 | 90 | 62 | 105 | 381.9 | 1 | 35.36 | 381.9 | 38.3 | 43
RV40 | 40 | 10000 | 70 | 67 | 105 | 398.3 | 0.456 | 16.81 | 181.5 | 40.6 | 43
RV40 | 40 | 10000 | 75 | 67 | 105 | 397.3 | 0.587 | 21.6 | 233.3 | 39.9 | 43
RV40 | 40 | 10000 | 80 | 67 | 105 | 395.5 | 0.719 | 26.32 | 284.3 | 39.3 | 43
RV40 | 40 | 10000 | 85 | 67 | 105 | 393.6 | 0.84 | 30.62 | 330.7 | 38.9 | 43
RV40 | 40 | 10000 | 90 | 67 | 105 | 391.4 | 0.972 | 35.22 | 380.4 | 38.5 | 43
RV40 | 40 | 10000 | 75 | 72 | 105 | 436.7 | 0.415 | 16.79 | 181.3 | 40.4 | 43
RV40 | 40 | 10000 | 80 | 72 | 105 | 435.2 | 0.537 | 21.62 | 233.5 | 39.7 | 43
RV40 | 40 | 10000 | 85 | 72 | 105 | 433.2 | 0.648 | 25.99 | 280.7 | 39.2 | 43
RV40 | 40 | 10000 | 90 | 72 | 105 | 430.3 | 0.769 | 30.66 | 331.1 | 38.8 | 43
RV40 | 40 | 10000 | 80 | 77 | 105 | 478.6 | 0.385 | 17.05 | 184.1 | 40.1 | 43
RV40 | 40 | 10000 | 85 | 77 | 105 | 476.1 | 0.486 | 21.42 | 231.3 | 39.5 | 43
RV40 | 40 | 10000 | 90 | 77 | 105 | 473.5 | 0.597 | 26.19 | 282.8 | 39.1 | 43
RV40 | 40 | 10000 | 65 | 57 | 115 | 307.5 | 0.719 | 20.46 | 221 | 46.4 | 43
RV40 | 40 | 10000 | 70 | 57 | 115 | 306.9 | 0.881 | 25.03 | 270.3 | 45.5 | 43
RV40 | 40 | 10000 | 75 | 57 | 115 | 309.9 | 1 | 28.69 | 309.9 | 44.8 | 43
RV40 | 40 | 10000 | 80 | 57 | 115 | 327.1 | 1 | 30.29 | 327.1 | 44.4 | 43
RV40 | 40 | 10000 | 85 | 57 | 115 | 344.5 | 1 | 31.9 | 344.5 | 44 | 43
RV40 | 40 | 10000 | 90 | 57 | 115 | 361.9 | 1 | 33.51 | 361.9 | 43.7 | 43
RV40 | 40 | 10000 | 65 | 62 | 115 | 339.2 | 0.506 | 15.9 | 171.7 | 47.6 | 43
RV40 | 40 | 10000 | 70 | 62 | 115 | 339.4 | 0.658 | 20.69 | 223.4 | 46.2 | 43
RV40 | 40 | 10000 | 75 | 62 | 115 | 338.4 | 0.8 | 25.06 | 270.7 | 45.3 | 43
RV40 | 40 | 10000 | 80 | 62 | 115 | 337.5 | 0.952 | 29.74 | 321.2 | 44.6 | 43
RV40 | 40 | 10000 | 85 | 62 | 115 | 347.1 | 1 | 32.14 | 347.1 | 44 | 43
RV40 | 40 | 10000 | 90 | 62 | 115 | 364.8 | 1 | 33.78 | 364.8 | 43.7 | 43
RV40 | 40 | 10000 | 70 | 67 | 115 | 374 | 0.456 | 15.78 | 170.4 | 47.1 | 43
RV40 | 40 | 10000 | 75 | 67 | 115 | 373.5 | 0.597 | 20.66 | 223.1 | 45.9 | 43
RV40 | 40 | 10000 | 80 | 67 | 115 | 372.2 | 0.729 | 25.12 | 271.3 | 45.1 | 43
RV40 | 40 | 10000 | 85 | 67 | 115 | 370.5 | 0.871 | 29.87 | 322.6 | 44.3 | 43
RV40 | 40 | 10000 | 90 | 67 | 115 | 370.4 | 0.992 | 34.03 | 367.5 | 43.7 | 43
RV40 | 40 | 10000 | 75 | 72 | 115 | 410.9 | 0.415 | 15.79 | 170.5 | 46.6 | 43
RV40 | 40 | 10000 | 80 | 72 | 115 | 410 | 0.547 | 20.75 | 224.1 | 45.5 | 43
RV40 | 40 | 10000 | 85 | 72 | 115 | 408.7 | 0.668 | 25.29 | 273.1 | 45.1 | 43
RV40 | 40 | 10000 | 90 | 72 | 115 | 406.1 | 0.79 | 29.69 | 320.7 | 44.3 | 43
RV40 | 40 | 10000 | 80 | 77 | 115 | 450.9 | 0.385 | 16.06 | 173.5 | 46.2 | 43
RV40 | 40 | 10000 | 85 | 77 | 115 | 448.9 | 0.496 | 20.62 | 222.7 | 45.3 | 43
RV40 | 40 | 10000 | 90 | 77 | 115 | 447 | 0.607 | 25.14 | 271.5 | 44.6 | 43
RV40 | 40 | 10000 | 65 | 57 | 125 | 282.5 | 0.719 | 18.81 | 203.1 | 46 | 44
RV40 | 40 | 10000 | 70 | 57 | 125 | 281.4 | 0.891 | 23.21 | 250.7 | 45.7 | 44
RV40 | 40 | 10000 | 75 | 57 | 125 | 283.8 | 1 | 26.28 | 283.8 | 45.5 | 44
RV40 | 40 | 10000 | 80 | 57 | 125 | 299.4 | 1 | 27.72 | 299.4 | 45.7 | 44
RV40 | 40 | 10000 | 85 | 57 | 125 | 314.9 | 1 | 29.16 | 314.9 | 45.9 | 44
RV40 | 40 | 10000 | 90 | 57 | 125 | 330.4 | 1 | 30.59 | 330.4 | 46 | 44
RV40 | 40 | 10000 | 65 | 62 | 125 | 311.4 | 0.506 | 14.59 | 157.6 | 46.7 | 44
RV40 | 40 | 10000 | 70 | 62 | 125 | 310.6 | 0.658 | 18.93 | 204.4 | 46.3 | 44
RV40 | 40 | 10000 | 75 | 62 | 125 | 309.3 | 0.81 | 23.19 | 250.5 | 46 | 44
RV40 | 40 | 10000 | 80 | 62 | 125 | 306.9 | 0.962 | 27.33 | 295.2 | 45.8 | 44
RV40 | 40 | 10000 | 85 | 62 | 125 | 317.3 | 1 | 29.38 | 317.3 | 45.9 | 44
RV40 | 40 | 10000 | 90 | 62 | 125 | 333 | 1 | 30.83 | 333 | 46 | 44
RV40 | 40 | 10000 | 70 | 67 | 125 | 341.9 | 0.466 | 14.74 | 159.2 | 46.9 | 44
RV40 | 40 | 10000 | 75 | 67 | 125 | 340.4 | 0.597 | 18.82 | 203.3 | 46.6 | 44
RV40 | 40 | 10000 | 80 | 67 | 125 | 338.5 | 0.739 | 23.17 | 250.2 | 46.4 | 44
RV40 | 40 | 10000 | 85 | 67 | 125 | 336.8 | 0.881 | 27.47 | 296.7 | 46.2 | 44
RV40 | 40 | 10000 | 90 | 67 | 125 | 335.8 | 1 | 31.09 | 335.8 | 46 | 44
RV40 | 40 | 10000 | 75 | 72 | 125 | 374.4 | 0.425 | 14.74 | 159.2 | 47.2 | 44
RV40 | 40 | 10000 | 80 | 72 | 125 | 372.6 | 0.547 | 18.86 | 203.7 | 46.9 | 44
RV40 | 40 | 10000 | 85 | 72 | 125 | 370.8 | 0.678 | 23.29 | 251.5 | 46.7 | 44
RV40 | 40 | 10000 | 90 | 72 | 125 | 368.3 | 0.81 | 27.62 | 298.3 | 46.6 | 44
RV40 | 40 | 10000 | 80 | 77 | 125 | 408.9 | 0.385 | 14.56 | 157.3 | 47.5 | 44
RV40 | 40 | 10000 | 85 | 77 | 125 | 406.4 | 0.506 | 19.05 | 205.7 | 47.2 | 44
RV40 | 40 | 10000 | 90 | 77 | 125 | 404 | 0.618 | 23.1 | 249.5 | 47.1 | 44
RV40 | 40 | 12000 | 65 | 57 | 75 | 394.7 | 0.709 | 21.58 | 279.7 | 28.9 | 42
RV40 | 40 | 12000 | 70 | 57 | 75 | 393.2 | 0.861 | 26.11 | 338.4 | 28.6 | 42
RV40 | 40 | 12000 | 75 | 57 | 75 | 393.2 | 1 | 30.34 | 393.2 | 28.3 | 42
RV40 | 40 | 12000 | 80 | 57 | 75 | 412 | 1 | 31.79 | 412 | 28.2 | 42
RV40 | 40 | 12000 | 85 | 57 | 75 | 432.3 | 1 | 33.36 | 432.3 | 28.1 | 42
RV40 | 40 | 12000 | 90 | 57 | 75 | 452.3 | 1 | 34.9 | 452.3 | 28.1 | 42
RV40 | 40 | 12000 | 65 | 62 | 75 | 434.4 | 0.496 | 16.63 | 215.5 | 29 | 42
RV40 | 40 | 12000 | 70 | 62 | 75 | 432.8 | 0.648 | 21.64 | 280.4 | 28.7 | 42
RV40 | 40 | 12000 | 75 | 62 | 75 | 430.3 | 0.79 | 26.22 | 339.8 | 28.6 | 42
RV40 | 40 | 12000 | 80 | 62 | 75 | 428.7 | 0.931 | 30.81 | 399.3 | 28.3 | 42
RV40 | 40 | 12000 | 85 | 62 | 75 | 435.4 | 1 | 33.6 | 435.4 | 28.1 | 42
RV40 | 40 | 12000 | 90 | 62 | 75 | 455.7 | 1 | 35.16 | 455.7 | 28.1 | 42
RV40 | 40 | 12000 | 70 | 67 | 75 | 474.8 | 0.456 | 16.69 | 216.3 | 28.9 | 42
RV40 | 40 | 12000 | 75 | 67 | 75 | 472.8 | 0.587 | 21.42 | 277.6 | 28.6 | 42
RV40 | 40 | 12000 | 80 | 67 | 75 | 470.1 | 0.719 | 26.07 | 337.9 | 28.4 | 42
RV40 | 40 | 12000 | 85 | 67 | 75 | 467.6 | 0.85 | 30.68 | 397.6 | 28.3 | 42
RV40 | 40 | 12000 | 90 | 67 | 75 | 465.8 | 0.972 | 34.93 | 452.7 | 28.2 | 42
RV40 | 40 | 12000 | 75 | 72 | 75 | 518.7 | 0.415 | 16.61 | 215.3 | 28.7 | 42
RV40 | 40 | 12000 | 80 | 72 | 75 | 516.1 | 0.537 | 21.37 | 276.9 | 28.5 | 42
RV40 | 40 | 12000 | 85 | 72 | 75 | 513.1 | 0.658 | 26.05 | 337.6 | 28.5 | 42
RV40 | 40 | 12000 | 90 | 72 | 75 | 509.9 | 0.78 | 30.67 | 397.5 | 28.4 | 42
RV40 | 40 | 12000 | 80 | 77 | 75 | 566.3 | 0.385 | 16.81 | 217.8 | 28.7 | 42
RV40 | 40 | 12000 | 85 | 77 | 75 | 562.8 | 0.496 | 21.54 | 279.2 | 28.6 | 42
RV40 | 40 | 12000 | 90 | 77 | 75 | 559.2 | 0.597 | 25.77 | 334 | 28.6 | 42
RV40 | 40 | 12000 | 65 | 57 | 85 | 377.8 | 0.709 | 20.66 | 267.7 | 32.6 | 42
RV40 | 40 | 12000 | 70 | 57 | 85 | 376.5 | 0.871 | 25.29 | 327.8 | 32.3 | 42
RV40 | 40 | 12000 | 75 | 57 | 85 | 378.1 | 1 | 29.17 | 378.1 | 31.9 | 42
RV40 | 40 | 12000 | 80 | 57 | 85 | 397.9 | 1 | 30.7 | 397.9 | 31.8 | 42
RV40 | 40 | 12000 | 85 | 57 | 85 | 417.7 | 1 | 32.23 | 417.7 | 31.6 | 42
RV40 | 40 | 12000 | 90 | 57 | 85 | 437.8 | 1 | 33.78 | 437.8 | 31.4 | 42
RV40 | 40 | 12000 | 65 | 62 | 85 | 415.9 | 0.506 | 16.24 | 210.5 | 32.9 | 42
RV40 | 40 | 12000 | 70 | 62 | 85 | 414.5 | 0.648 | 20.72 | 268.5 | 32.5 | 42
RV40 | 40 | 12000 | 75 | 62 | 85 | 412.4 | 0.8 | 25.45 | 329.8 | 32.2 | 42
RV40 | 40 | 12000 | 80 | 62 | 85 | 411 | 0.952 | 30.18 | 391.1 | 31.9 | 42
RV40 | 40 | 12000 | 85 | 62 | 85 | 421 | 1 | 32.48 | 421 | 31.6 | 42
RV40 | 40 | 12000 | 90 | 62 | 85 | 441.1 | 1 | 34.04 | 441.1 | 31.4 | 42
RV40 | 40 | 12000 | 70 | 67 | 85 | 455 | 0.456 | 16 | 207.3 | 32.8 | 42
RV40 | 40 | 12000 | 75 | 67 | 85 | 453.2 | 0.597 | 20.89 | 270.7 | 32.4 | 42
RV40 | 40 | 12000 | 80 | 67 | 85 | 450.7 | 0.729 | 25.35 | 328.5 | 32.1 | 42
RV40 | 40 | 12000 | 85 | 67 | 85 | 448.7 | 0.871 | 30.14 | 390.6 | 31.8 | 42
RV40 | 40 | 12000 | 90 | 67 | 85 | 447.9 | 0.992 | 34.29 | 444.4 | 31.5 | 42
RV40 | 40 | 12000 | 75 | 72 | 85 | 497.4 | 0.415 | 15.93 | 206.5 | 32.6 | 42
RV40 | 40 | 12000 | 80 | 72 | 85 | 495.7 | 0.547 | 20.91 | 271 | 32.3 | 42
RV40 | 40 | 12000 | 85 | 72 | 85 | 492.6 | 0.668 | 25.39 | 329.1 | 32 | 42
RV40 | 40 | 12000 | 90 | 72 | 85 | 489.9 | 0.79 | 29.85 | 386.8 | 31.7 | 42
RV40 | 40 | 12000 | 80 | 77 | 85 | 543.3 | 0.385 | 16.13 | 209 | 32.4 | 42
RV40 | 40 | 12000 | 85 | 77 | 85 | 540 | 0.496 | 20.67 | 267.9 | 32 | 42
RV40 | 40 | 12000 | 90 | 77 | 85 | 536.9 | 0.607 | 25.16 | 326.1 | 31.9 | 42
RV40 | 40 | 12000 | 65 | 57 | 95 | 359.4 | 0.719 | 19.93 | 258.3 | 37 | 43
RV40 | 40 | 12000 | 70 | 57 | 95 | 358.3 | 0.891 | 24.63 | 319.2 | 36.5 | 43
RV40 | 40 | 12000 | 75 | 57 | 95 | 363 | 1 | 28.01 | 363 | 36.1 | 43
RV40 | 40 | 12000 | 80 | 57 | 95 | 382.6 | 1 | 29.52 | 382.6 | 35.9 | 43
RV40 | 40 | 12000 | 85 | 57 | 95 | 402.1 | 1 | 31.03 | 402.1 | 35.7 | 43
RV40 | 40 | 12000 | 90 | 57 | 95 | 422 | 1 | 32.56 | 422 | 35.5 | 43
RV40 | 40 | 12000 | 65 | 62 | 95 | 395.5 | 0.506 | 15.45 | 200.2 | 37.5 | 43
RV40 | 40 | 12000 | 70 | 62 | 95 | 394.7 | 0.658 | 20.04 | 259.7 | 36.8 | 43
RV40 | 40 | 12000 | 75 | 62 | 95 | 393.2 | 0.82 | 24.88 | 322.4 | 36.4 | 43
RV40 | 40 | 12000 | 80 | 62 | 95 | 391.7 | 0.972 | 29.38 | 380.7 | 35.9 | 43
RV40 | 40 | 12000 | 85 | 62 | 95 | 405.2 | 1 | 31.27 | 405.2 | 35.7 | 43
RV40 | 40 | 12000 | 90 | 62 | 95 | 425.3 | 1 | 32.82 | 425.3 | 35.5 | 43
RV40 | 40 | 12000 | 70 | 67 | 95 | 433.3 | 0.456 | 15.23 | 197.4 | 37.3 | 43
RV40 | 40 | 12000 | 75 | 67 | 95 | 432.1 | 0.607 | 20.25 | 262.5 | 36.7 | 43
RV40 | 40 | 12000 | 80 | 67 | 95 | 429.7 | 0.749 | 24.84 | 321.9 | 36.4 | 43
RV40 | 40 | 12000 | 85 | 67 | 95 | 428.3 | 0.881 | 29.1 | 377.2 | 35.9 | 43
RV40 | 40 | 12000 | 90 | 67 | 95 | 429 | 1 | 33.1 | 429 | 35.6 | 43
RV40 | 40 | 12000 | 75 | 72 | 95 | 474.3 | 0.425 | 15.56 | 201.7 | 37.1 | 43
RV40 | 40 | 12000 | 80 | 72 | 95 | 472.7 | 0.547 | 19.94 | 258.4 | 36.6 | 43
RV40 | 40 | 12000 | 85 | 72 | 95 | 470.1 | 0.678 | 24.61 | 318.9 | 36.2 | 43
RV40 | 40 | 12000 | 90 | 72 | 95 | 467.9 | 0.81 | 29.24 | 378.9 | 35.9 | 43
RV40 | 40 | 12000 | 80 | 77 | 95 | 518.3 | 0.385 | 15.39 | 199.4 | 36.9 | 43
RV40 | 40 | 12000 | 85 | 77 | 95 | 515.7 | 0.506 | 20.14 | 261 | 36.4 | 43
RV40 | 40 | 12000 | 90 | 77 | 95 | 512.6 | 0.618 | 24.43 | 316.6 | 36.1 | 43
RV40 | 40 | 12000 | 65 | 57 | 105 | 339.9 | 0.729 | 19.11 | 247.7 | 42.1 | 43
RV40 | 40 | 12000 | 70 | 57 | 105 | 339.2 | 0.911 | 23.85 | 309.1 | 41.2 | 43
RV40 | 40 | 12000 | 75 | 57 | 105 | 347.1 | 1 | 26.78 | 347.1 | 40.8 | 43
RV40 | 40 | 12000 | 80 | 57 | 105 | 366.5 | 1 | 28.28 | 366.5 | 40.5 | 43
RV40 | 40 | 12000 | 85 | 57 | 105 | 385.8 | 1 | 29.77 | 385.8 | 40.2 | 43
RV40 | 40 | 12000 | 90 | 57 | 105 | 405.5 | 1 | 31.29 | 405.5 | 40 | 43
RV40 | 40 | 12000 | 65 | 62 | 105 | 374.4 | 0.506 | 14.62 | 189.5 | 42.7 | 43
RV40 | 40 | 12000 | 70 | 62 | 105 | 373.9 | 0.668 | 19.27 | 249.8 | 41.8 | 43
RV40 | 40 | 12000 | 75 | 62 | 105 | 372.9 | 0.83 | 23.88 | 309.5 | 41.1 | 43
RV40 | 40 | 12000 | 80 | 62 | 105 | 372.2 | 0.992 | 28.5 | 369.3 | 40.4 | 43
RV40 | 40 | 12000 | 85 | 62 | 105 | 388.7 | 1 | 29.99 | 388.7 | 40.2 | 43
RV40 | 40 | 12000 | 90 | 62 | 105 | 408.4 | 1 | 31.51 | 408.4 | 40 | 43
RV40 | 40 | 12000 | 70 | 67 | 105 | 410.7 | 0.466 | 14.76 | 191.3 | 42.5 | 43
RV40 | 40 | 12000 | 75 | 67 | 105 | 409.9 | 0.607 | 19.21 | 249 | 41.6 | 43
RV40 | 40 | 12000 | 80 | 67 | 105 | 408.1 | 0.759 | 23.91 | 309.9 | 41.1 | 43
RV40 | 40 | 12000 | 85 | 67 | 105 | 406.7 | 0.911 | 28.6 | 370.6 | 40.5 | 43
RV40 | 40 | 12000 | 90 | 67 | 105 | 411.7 | 1 | 31.77 | 411.7 | 40 | 43
RV40 | 40 | 12000 | 75 | 72 | 105 | 449.6 | 0.425 | 14.75 | 191.2 | 42.6 | 43
RV40 | 40 | 12000 | 80 | 72 | 105 | 448.8 | 0.557 | 19.28 | 249.9 | 41.4 | 43
RV40 | 40 | 12000 | 85 | 72 | 105 | 446.5 | 0.699 | 24.07 | 311.9 | 41 | 43
RV40 | 40 | 12000 | 90 | 72 | 105 | 444.6 | 0.83 | 28.48 | 369.1 | 40.4 | 43
RV40 | 40 | 12000 | 80 | 77 | 105 | 491.9 | 0.385 | 14.6 | 189.2 | 42 | 43
RV40 | 40 | 12000 | 85 | 77 | 105 | 490 | 0.506 | 19.14 | 248 | 41.2 | 43
RV40 | 40 | 12000 | 90 | 77 | 105 | 487.5 | 0.638 | 23.99 | 310.9 | 40.7 | 43
RV40 | 40 | 12000 | 65 | 57 | 115 | 317.6 | 0.749 | 18.36 | 238 | 48.4 | 43
RV40 | 40 | 12000 | 70 | 57 | 115 | 317.4 | 0.942 | 23.06 | 298.9 | 47 | 43
RV40 | 40 | 12000 | 75 | 57 | 115 | 329 | 1 | 25.39 | 329 | 46.5 | 43
RV40 | 40 | 12000 | 80 | 57 | 115 | 348.2 | 1 | 26.87 | 348.2 | 46.1 | 43
RV40 | 40 | 12000 | 85 | 57 | 115 | 367.3 | 1 | 28.34 | 367.3 | 45.8 | 43
RV40 | 40 | 12000 | 90 | 57 | 115 | 386.4 | 1 | 29.81 | 386.4 | 45.3 | 43
RV40 | 40 | 12000 | 65 | 62 | 115 | 349.7 | 0.506 | 13.66 | 177 | 49.5 | 43
RV40 | 40 | 12000 | 70 | 62 | 115 | 350.3 | 0.688 | 18.6 | 241.1 | 48 | 43
RV40 | 40 | 12000 | 75 | 62 | 115 | 349.9 | 0.861 | 23.23 | 301.1 | 46.9 | 43
RV40 | 40 | 12000 | 80 | 62 | 115 | 350.9 | 1 | 27.08 | 350.9 | 46.1 | 43
RV40 | 40 | 12000 | 85 | 62 | 115 | 370.1 | 1 | 28.56 | 370.1 | 45.7 | 43
RV40 | 40 | 12000 | 90 | 62 | 115 | 389.5 | 1 | 30.05 | 389.5 | 45.4 | 43
RV40 | 40 | 12000 | 70 | 67 | 115 | 384.6 | 0.466 | 13.82 | 179.1 | 49.1 | 43
RV40 | 40 | 12000 | 75 | 67 | 115 | 384.7 | 0.628 | 18.63 | 241.5 | 47.7 | 43
RV40 | 40 | 12000 | 80 | 67 | 115 | 383.9 | 0.779 | 23.09 | 299.2 | 46.6 | 43
RV40 | 40 | 12000 | 85 | 67 | 115 | 382.8 | 0.941 | 27.81 | 360.4 | 45.9 | 43
RV40 | 40 | 12000 | 90 | 67 | 115 | 392.5 | 1 | 30.29 | 392.5 | 45.4 | 43
RV40 | 40 | 12000 | 75 | 72 | 115 | 422.2 | 0.425 | 13.85 | 179.5 | 48.6 | 43
RV40 | 40 | 12000 | 80 | 72 | 115 | 421.9 | 0.567 | 18.46 | 239.2 | 47.3 | 43
RV40 | 40 | 12000 | 85 | 72 | 115 | 420.1 | 0.719 | 23.3 | 302 | 46.6 | 43
RV40 | 40 | 12000 | 90 | 72 | 115 | 418.9 | 0.861 | 27.82 | 360.5 | 45.9 | 43
RV40 | 40 | 12000 | 80 | 77 | 115 | 462.4 | 0.385 | 13.73 | 177.9 | 48.3 | 43
RV40 | 40 | 12000 | 85 | 77 | 115 | 461.5 | 0.516 | 18.39 | 238.3 | 47.1 | 43
RV40 | 40 | 12000 | 90 | 77 | 115 | 459.3 | 0.648 | 22.96 | 297.6 | 46.3 | 43
RV40 | 40 | 12000 | 65 | 57 | 125 | 291.3 | 0.749 | 16.84 | 218.2 | 47.8 | 44
RV40 | 40 | 12000 | 70 | 57 | 125 | 289.8 | 0.942 | 21.06 | 272.9 | 47.4 | 44
RV40 | 40 | 12000 | 75 | 57 | 125 | 300.5 | 1 | 23.19 | 300.5 | 47.4 | 44
RV40 | 40 | 12000 | 80 | 57 | 125 | 317.4 | 1 | 24.49 | 317.4 | 47.6 | 44
RV40 | 40 | 12000 | 85 | 57 | 125 | 334.3 | 1 | 25.79 | 334.3 | 47.7 | 44
RV40 | 40 | 12000 | 90 | 57 | 125 | 351.1 | 1 | 27.09 | 351.1 | 47.9 | 44
RV40 | 40 | 12000 | 65 | 62 | 125 | 320.4 | 0.516 | 12.76 | 165.4 | 48.5 | 44
RV40 | 40 | 12000 | 70 | 62 | 125 | 319.4 | 0.688 | 16.97 | 219.9 | 48.1 | 44
RV40 | 40 | 12000 | 75 | 62 | 125 | 318.5 | 0.861 | 21.15 | 274.1 | 47.8 | 44
RV40 | 40 | 12000 | 80 | 62 | 125 | 319.7 | 1 | 24.67 | 319.7 | 47.6 | 44
RV40 | 40 | 12000 | 85 | 62 | 125 | 336.8 | 1 | 25.99 | 336.8 | 47.8 | 44
RV40 | 40 | 12000 | 90 | 62 | 125 | 353.8 | 1 | 27.3 | 353.8 | 47.9 | 44
RV40 | 40 | 12000 | 70 | 67 | 125 | 351.4 | 0.466 | 12.62 | 163.6 | 48.9 | 44
RV40 | 40 | 12000 | 75 | 67 | 125 | 350.7 | 0.628 | 16.98 | 220.1 | 48.4 | 44
RV40 | 40 | 12000 | 80 | 67 | 125 | 349 | 0.79 | 21.27 | 275.6 | 48.1 | 44
RV40 | 40 | 12000 | 85 | 67 | 125 | 347 | 0.952 | 25.48 | 330.2 | 47.9 | 44
RV40 | 40 | 12000 | 90 | 67 | 125 | 356.6 | 1 | 27.52 | 356.6 | 47.9 | 44
RV40 | 40 | 12000 | 75 | 72 | 125 | 384.2 | 0.425 | 12.6 | 163.3 | 49.1 | 44
RV40 | 40 | 12000 | 80 | 72 | 125 | 382.9 | 0.577 | 17.05 | 221 | 48.7 | 44
RV40 | 40 | 12000 | 85 | 72 | 125 | 380.8 | 0.729 | 21.41 | 277.5 | 48.5 | 44
RV40 | 40 | 12000 | 90 | 72 | 125 | 379.1 | 0.87 | 25.46 | 330 | 48.3 | 44
RV40 | 40 | 12000 | 80 | 77 | 125 | 419.6 | 0.395 | 12.79 | 165.7 | 49.4 | 44
RV40 | 40 | 12000 | 85 | 77 | 125 | 417.6 | 0.526 | 16.96 | 219.8 | 49 | 44
RV40 | 40 | 12000 | 90 | 77 | 125 | 415.1 | 0.658 | 21.07 | 273.1 | 48.8 | 44
RV40 | 40 | 14000 | 65 | 57 | 75 | 406.3 | 0.729 | 19.59 | 296.2 | 31.1 | 42
RV40 | 40 | 14000 | 70 | 57 | 75 | 405.1 | 0.901 | 24.14 | 365 | 30.8 | 42
RV40 | 40 | 14000 | 75 | 57 | 75 | 412.1 | 1 | 27.26 | 412.1 | 30.6 | 42
RV40 | 40 | 14000 | 80 | 57 | 75 | 433.9 | 1 | 28.7 | 433.9 | 30.4 | 42
RV40 | 40 | 14000 | 85 | 57 | 75 | 455.7 | 1 | 30.14 | 455.7 | 30.4 | 42
RV40 | 40 | 14000 | 90 | 57 | 75 | 477.8 | 1 | 31.6 | 477.8 | 30.4 | 42
RV40 | 40 | 14000 | 65 | 62 | 75 | 445.6 | 0.506 | 14.92 | 225.6 | 31.3 | 42
RV40 | 40 | 14000 | 70 | 62 | 75 | 444.2 | 0.668 | 19.63 | 296.8 | 31 | 42
RV40 | 40 | 14000 | 75 | 62 | 75 | 442.3 | 0.83 | 24.28 | 367.1 | 30.8 | 42
RV40 | 40 | 14000 | 80 | 62 | 75 | 441.2 | 0.982 | 28.66 | 433.3 | 30.4 | 42
RV40 | 40 | 14000 | 85 | 62 | 75 | 458.9 | 1 | 30.35 | 458.9 | 30.4 | 42
RV40 | 40 | 14000 | 90 | 62 | 75 | 481.2 | 1 | 31.83 | 481.2 | 30.4 | 42
RV40 | 40 | 14000 | 70 | 67 | 75 | 487 | 0.466 | 15 | 226.8 | 31.2 | 42
RV40 | 40 | 14000 | 75 | 67 | 75 | 485.2 | 0.607 | 19.49 | 294.7 | 30.9 | 42
RV40 | 40 | 14000 | 80 | 67 | 75 | 482.6 | 0.759 | 24.23 | 366.4 | 30.6 | 42
RV40 | 40 | 14000 | 85 | 67 | 75 | 480.7 | 0.901 | 28.64 | 433.1 | 30.5 | 42
RV40 | 40 | 14000 | 90 | 67 | 75 | 484.9 | 1 | 32.07 | 484.9 | 30.5 | 42
RV40 | 40 | 14000 | 75 | 72 | 75 | 531.5 | 0.425 | 14.95 | 226 | 30.9 | 42
RV40 | 40 | 14000 | 80 | 72 | 75 | 529.2 | 0.557 | 19.49 | 294.7 | 30.8 | 42
RV40 | 40 | 14000 | 85 | 72 | 75 | 526.3 | 0.698 | 24.31 | 367.6 | 30.7 | 42
RV40 | 40 | 14000 | 90 | 72 | 75 | 523.9 | 0.83 | 28.76 | 434.9 | 30.7 | 42
RV40 | 40 | 14000 | 80 | 77 | 75 | 579.2 | 0.385 | 14.74 | 222.8 | 31 | 42
RV40 | 40 | 14000 | 85 | 77 | 75 | 576.2 | 0.506 | 19.29 | 291.7 | 30.9 | 42
RV40 | 40 | 14000 | 90 | 77 | 75 | 573 | 0.638 | 24.17 | 365.4 | 30.8 | 42
RV40 | 40 | 14000 | 65 | 57 | 85 | 388.5 | 0.739 | 18.99 | 287.1 | 35 | 42
RV40 | 40 | 14000 | 70 | 57 | 85 | 387.2 | 0.921 | 23.59 | 356.7 | 34.5 | 42
RV40 | 40 | 14000 | 75 | 57 | 85 | 397.3 | 1 | 26.28 | 397.3 | 34.2 | 42
RV40 | 40 | 14000 | 80 | 57 | 85 | 418.7 | 1 | 27.69 | 418.7 | 34 | 42
RV40 | 40 | 14000 | 85 | 57 | 85 | 440.2 | 1 | 29.11 | 440.2 | 33.8 | 42
RV40 | 40 | 14000 | 90 | 57 | 85 | 462.1 | 1 | 30.56 | 462.1 | 33.6 | 42
RV40 | 40 | 14000 | 65 | 62 | 85 | 425.9 | 0.506 | 14.26 | 215.6 | 35.3 | 42
RV40 | 40 | 14000 | 70 | 62 | 85 | 424.9 | 0.678 | 19.06 | 288.2 | 34.8 | 42
RV40 | 40 | 14000 | 75 | 62 | 85 | 423.4 | 0.84 | 23.53 | 355.8 | 34.4 | 42
RV40 | 40 | 14000 | 80 | 62 | 85 | 423.8 | 1 | 28.03 | 423.8 | 34.1 | 42
RV40 | 40 | 14000 | 85 | 62 | 85 | 443.4 | 1 | 29.33 | 443.4 | 33.9 | 42
RV40 | 40 | 14000 | 90 | 62 | 85 | 465.4 | 1 | 30.78 | 465.4 | 33.7 | 42
RV40 | 40 | 14000 | 70 | 67 | 85 | 466.2 | 0.466 | 14.36 | 217.1 | 35 | 42
RV40 | 40 | 14000 | 75 | 67 | 85 | 464.8 | 0.617 | 18.98 | 287 | 34.7 | 42
RV40 | 40 | 14000 | 80 | 67 | 85 | 462.6 | 0.769 | 23.54 | 355.9 | 34.4 | 42
RV40 | 40 | 14000 | 85 | 67 | 85 | 461 | 0.921 | 28.09 | 424.7 | 34 | 42
RV40 | 40 | 14000 | 90 | 67 | 85 | 468.8 | 1 | 31.01 | 468.8 | 33.7 | 42
RV40 | 40 | 14000 | 75 | 72 | 85 | 509.3 | 0.425 | 14.32 | 216.5 | 34.9 | 42
RV40 | 40 | 14000 | 80 | 72 | 85 | 507.6 | 0.567 | 19.03 | 287.8 | 34.5 | 42
RV40 | 40 | 14000 | 85 | 72 | 85 | 504.6 | 0.709 | 23.65 | 357.6 | 34.2 | 42
RV40 | 40 | 14000 | 90 | 72 | 85 | 502.7 | 0.84 | 27.94 | 422.4 | 33.9 | 42
RV40 | 40 | 14000 | 80 | 77 | 85 | 555 | 0.385 | 14.12 | 213.5 | 34.7 | 42
RV40 | 40 | 14000 | 85 | 77 | 85 | 552.5 | 0.516 | 18.87 | 285.3 | 34.3 | 42
RV40 | 40 | 14000 | 90 | 77 | 85 | 549.4 | 0.648 | 23.54 | 356 | 34.2 | 42
RV40 | 40 | 14000 | 65 | 57 | 95 | 369 | 0.749 | 18.28 | 276.4 | 39.4 | 43
RV40 | 40 | 14000 | 70 | 57 | 95 | 368.1 | 0.942 | 22.92 | 346.6 | 38.7 | 43
RV40 | 40 | 14000 | 75 | 57 | 95 | 381 | 1 | 25.2 | 381 | 38.4 | 43
RV40 | 40 | 14000 | 80 | 57 | 95 | 402.2 | 1 | 26.6 | 402.2 | 38.2 | 43
RV40 | 40 | 14000 | 85 | 57 | 95 | 423.6 | 1 | 28.02 | 423.6 | 38 | 43
RV40 | 40 | 14000 | 90 | 57 | 95 | 445 | 1 | 29.43 | 445 | 37.8 | 43
RV40 | 40 | 14000 | 65 | 62 | 95 | 404.7 | 0.506 | 13.54 | 204.8 | 39.9 | 43
RV40 | 40 | 14000 | 70 | 62 | 95 | 404.2 | 0.688 | 18.4 | 278.2 | 39.2 | 43
RV40 | 40 | 14000 | 75 | 62 | 95 | 403.1 | 0.86 | 22.94 | 346.8 | 38.7 | 43
RV40 | 40 | 14000 | 80 | 62 | 95 | 405.1 | 1 | 26.79 | 405.1 | 38.2 | 43
RV40 | 40 | 14000 | 85 | 62 | 95 | 426.7 | 1 | 28.22 | 426.7 | 38 | 43
RV40 | 40 | 14000 | 90 | 62 | 95 | 448.3 | 1 | 29.65 | 448.3 | 37.8 | 43
RV40 | 40 | 14000 | 70 | 67 | 95 | 443.4 | 0.466 | 13.66 | 206.5 | 39.7 | 43
RV40 | 40 | 14000 | 75 | 67 | 95 | 442.7 | 0.628 | 18.37 | 277.8 | 39.1 | 43
RV40 | 40 | 14000 | 80 | 67 | 95 | 441.1 | 0.79 | 23.04 | 348.3 | 38.6 | 43
RV40 | 40 | 14000 | 85 | 67 | 95 | 439.5 | 0.942 | 27.37 | 413.8 | 38.1 | 43
RV40 | 40 | 14000 | 90 | 67 | 95 | 451.6 | 1 | 29.87 | 451.6 | 37.8 | 43
RV40 | 40 | 14000 | 75 | 72 | 95 | 484.6 | 0.425 | 13.63 | 206.1 | 39.6 | 43
RV40 | 40 | 14000 | 80 | 72 | 95 | 483.6 | 0.577 | 18.46 | 279.1 | 38.9 | 43
RV40 | 40 | 14000 | 85 | 72 | 95 | 481.1 | 0.719 | 22.87 | 345.8 | 38.5 | 43
RV40 | 40 | 14000 | 90 | 72 | 95 | 479.2 | 0.871 | 27.59 | 417.2 | 38.1 | 43
RV40 | 40 | 14000 | 80 | 77 | 95 | 529.1 | 0.395 | 13.82 | 208.9 | 39.3 | 43
RV40 | 40 | 14000 | 85 | 77 | 95 | 526.8 | 0.526 | 18.34 | 277.3 | 38.8 | 43
RV40 | 40 | 14000 | 90 | 77 | 95 | 524.1 | 0.658 | 22.81 | 344.9 | 38.4 | 43
RV40 | 40 | 14000 | 65 | 57 | 105 | 348.5 | 0.77 | 17.74 | 268.2 | 44.4 | 43
RV40 | 40 | 14000 | 70 | 57 | 105 | 348.3 | 0.972 | 22.39 | 338.5 | 43.3 | 43
RV40 | 40 | 14000 | 75 | 57 | 105 | 364.1 | 1 | 24.08 | 364.1 | 43.1 | 43
RV40 | 40 | 14000 | 80 | 57 | 105 | 384.9 | 1 | 25.46 | 384.9 | 42.8 | 43
RV40 | 40 | 14000 | 85 | 57 | 105 | 406 | 1 | 26.85 | 406 | 42.5 | 43
RV40 | 40 | 14000 | 90 | 57 | 105 | 427.1 | 1 | 28.25 | 427.1 | 42.3 | 43
RV40 | 40 | 14000 | 65 | 62 | 105 | 382.2 | 0.516 | 13.05 | 197.3 | 45.3 | 43
RV40 | 40 | 14000 | 70 | 62 | 105 | 382.3 | 0.699 | 17.67 | 267.1 | 44.1 | 43
RV40 | 40 | 14000 | 75 | 62 | 105 | 381.7 | 0.881 | 22.24 | 336.2 | 43.5 | 43
RV40 | 40 | 14000 | 80 | 62 | 105 | 387.7 | 1 | 25.64 | 387.7 | 42.8 | 43
RV40 | 40 | 14000 | 85 | 62 | 105 | 409 | 1 | 27.05 | 409 | 42.6 | 43
RV40 | 40 | 14000 | 90 | 62 | 105 | 430.1 | 1 | 28.45 | 430.1 | 42.3 | 43
RV40 | 40 | 14000 | 70 | 67 | 105 | 419.5 | 0.466 | 12.92 | 195.4 | 45 | 43
RV40 | 40 | 14000 | 75 | 67 | 105 | 419.4 | 0.638 | 17.69 | 267.5 | 44 | 43
RV40 | 40 | 14000 | 80 | 67 | 105 | 418.2 | 0.81 | 22.4 | 338.7 | 43.3 | 43
RV40 | 40 | 14000 | 85 | 67 | 105 | 417.7 | 0.972 | 26.85 | 405.9 | 42.6 | 43
RV40 | 40 | 14000 | 90 | 67 | 105 | 433.6 | 1 | 28.68 | 433.6 | 42.3 | 43
RV40 | 40 | 14000 | 75 | 72 | 105 | 459 | 0.425 | 12.91 | 195.2 | 44.8 | 43
RV40 | 40 | 14000 | 80 | 72 | 105 | 458.9 | 0.587 | 17.82 | 269.5 | 43.9 | 43
RV40 | 40 | 14000 | 85 | 72 | 105 | 456.8 | 0.739 | 22.33 | 337.6 | 43.1 | 43
RV40 | 40 | 14000 | 90 | 72 | 105 | 455.2 | 0.891 | 26.83 | 405.6 | 42.6 | 43
RV40 | 40 | 14000 | 80 | 77 | 105 | 501.5 | 0.395 | 13.1 | 198 | 44.6 | 43
RV40 | 40 | 14000 | 85 | 77 | 105 | 500.4 | 0.537 | 17.76 | 268.5 | 43.6 | 43
RV40 | 40 | 14000 | 90 | 77 | 105 | 498 | 0.678 | 22.34 | 337.8 | 43.1 | 43
RV40 | 40 | 14000 | 65 | 57 | 115 | 325.4 | 0.779 | 16.77 | 253.6 | 50.8 | 44
RV40 | 40 | 14000 | 70 | 57 | 115 | 326.1 | 0.992 | 21.4 | 323.6 | 49.3 | 44
RV40 | 40 | 14000 | 75 | 57 | 115 | 344.6 | 1 | 22.79 | 344.6 | 49 | 44
RV40 | 40 | 14000 | 80 | 57 | 115 | 365.3 | 1 | 24.16 | 365.3 | 48.4 | 44
RV40 | 40 | 14000 | 85 | 57 | 115 | 385.9 | 1 | 25.52 | 385.9 | 48.1 | 44
RV40 | 40 | 14000 | 90 | 57 | 115 | 406.8 | 1 | 26.9 | 406.8 | 47.7 | 44
RV40 | 40 | 14000 | 65 | 62 | 115 | 356.5 | 0.516 | 12.18 | 184.1 | 52.3 | 44
RV40 | 40 | 14000 | 70 | 62 | 115 | 357.6 | 0.719 | 17 | 257 | 50.5 | 44
RV40 | 40 | 14000 | 75 | 62 | 115 | 358.1 | 0.911 | 21.58 | 326.3 | 49.1 | 44
RV40 | 40 | 14000 | 80 | 62 | 115 | 367.9 | 1 | 24.33 | 367.9 | 48.5 | 44
RV40 | 40 | 14000 | 85 | 62 | 115 | 388.7 | 1 | 25.71 | 388.7 | 48.1 | 44
RV40 | 40 | 14000 | 90 | 62 | 115 | 409.7 | 1 | 27.1 | 409.7 | 47.7 | 44
RV40 | 40 | 14000 | 70 | 67 | 115 | 392.1 | 0.476 | 12.34 | 186.6 | 51.7 | 44
RV40 | 40 | 14000 | 75 | 67 | 115 | 393.2 | 0.658 | 17.11 | 258.7 | 50.1 | 44
RV40 | 40 | 14000 | 80 | 67 | 115 | 392.9 | 0.83 | 21.57 | 326.1 | 49 | 44
RV40 | 40 | 14000 | 85 | 67 | 115 | 393.8 | 0.992 | 25.84 | 390.7 | 48 | 44
RV40 | 40 | 14000 | 90 | 67 | 115 | 412.9 | 1 | 27.31 | 412.9 | 47.7 | 44
RV40 | 40 | 14000 | 75 | 72 | 115 | 430.1 | 0.435 | 12.38 | 187.2 | 51.3 | 44
RV40 | 40 | 14000 | 80 | 72 | 115 | 430.6 | 0.597 | 17.01 | 257.2 | 49.7 | 44
RV40 | 40 | 14000 | 85 | 72 | 115 | 429.6 | 0.759 | 21.57 | 326.2 | 48.8 | 44
RV40 | 40 | 14000 | 90 | 72 | 115 | 428.9 | 0.921 | 26.13 | 395.1 | 47.9 | 44
RV40 | 40 | 14000 | 80 | 77 | 115 | 470.8 | 0.395 | 12.29 | 185.9 | 51.1 | 44
RV40 | 40 | 14000 | 85 | 77 | 115 | 470.7 | 0.547 | 17.02 | 257.3 | 49.5 | 44
RV40 | 40 | 14000 | 90 | 77 | 115 | 468.8 | 0.699 | 21.66 | 327.5 | 48.7 | 44
RV40 | 40 | 14000 | 65 | 57 | 125 | 297.3 | 0.789 | 15.52 | 234.7 | 50.2 | 44
RV40 | 40 | 14000 | 70 | 57 | 125 | 296.9 | 1 | 19.64 | 296.9 | 49.7 | 44
RV40 | 40 | 14000 | 75 | 57 | 125 | 313.8 | 1 | 20.75 | 313.8 | 49.8 | 44
RV40 | 40 | 14000 | 80 | 57 | 125 | 332 | 1 | 21.96 | 332 | 50 | 44
RV40 | 40 | 14000 | 85 | 57 | 125 | 350.2 | 1 | 23.16 | 350.2 | 50.2 | 44
RV40 | 40 | 14000 | 90 | 57 | 125 | 368.3 | 1 | 24.36 | 368.3 | 50.3 | 44
RV40 | 40 | 14000 | 65 | 62 | 125 | 326.9 | 0.516 | 11.16 | 168.8 | 51 | 44
RV40 | 40 | 14000 | 70 | 62 | 125 | 327 | 0.719 | 15.54 | 235 | 50.5 | 44
RV40 | 40 | 14000 | 75 | 62 | 125 | 325.9 | 0.921 | 19.85 | 300.2 | 50.1 | 44
RV40 | 40 | 14000 | 80 | 62 | 125 | 334.4 | 1 | 22.12 | 334.4 | 50 | 44
RV40 | 40 | 14000 | 85 | 62 | 125 | 352.7 | 1 | 23.33 | 352.7 | 50.2 | 44
RV40 | 40 | 14000 | 90 | 62 | 125 | 370.9 | 1 | 24.53 | 370.9 | 50.3 | 44
RV40 | 40 | 14000 | 70 | 67 | 125 | 358.5 | 0.476 | 11.28 | 170.6 | 51.4 | 44
RV40 | 40 | 14000 | 75 | 67 | 125 | 358.2 | 0.658 | 15.59 | 235.7 | 50.7 | 44
RV40 | 40 | 14000 | 80 | 67 | 125 | 357 | 0.84 | 19.84 | 300 | 50.5 | 44
RV40 | 40 | 14000 | 85 | 67 | 125 | 356 | 1 | 23.54 | 356 | 50.2 | 44
RV40 | 40 | 14000 | 90 | 67 | 125 | 373.8 | 1 | 24.72 | 373.8 | 50.3 | 44
RV40 | 40 | 14000 | 75 | 72 | 125 | 391.6 | 0.435 | 11.28 | 170.5 | 51.6 | 44
RV40 | 40 | 14000 | 80 | 72 | 125 | 391 | 0.597 | 15.44 | 233.5 | 51.1 | 44
RV40 | 40 | 14000 | 85 | 72 | 125 | 388.9 | 0.769 | 19.79 | 299.2 | 50.8 | 44
RV40 | 40 | 14000 | 90 | 72 | 125 | 387.1 | 0.931 | 23.84 | 360.5 | 50.6 | 44
RV40 | 40 | 14000 | 80 | 77 | 125 | 426.7 | 0.395 | 11.14 | 168.5 | 51.8 | 44
RV40 | 40 | 14000 | 85 | 77 | 125 | 425.3 | 0.547 | 15.38 | 232.5 | 51.4 | 44
RV40 | 40 | 14000 | 90 | 77 | 125 | 423.1 | 0.709 | 19.83 | 299.9 | 51.1 | 44
RV40 | 40 | 16000 | 65 | 57 | 75 | 414.6 | 0.759 | 18.22 | 314.8 | 34.1 | 42
RV40 | 40 | 16000 | 70 | 57 | 75 | 413.9 | 0.952 | 22.8 | 393.9 | 33.8 | 42
RV40 | 40 | 16000 | 75 | 57 | 75 | 429.1 | 1 | 24.83 | 429.1 | 33.6 | 42
RV40 | 40 | 16000 | 80 | 57 | 75 | 452.2 | 1 | 26.17 | 452.2 | 33.4 | 42
RV40 | 40 | 16000 | 85 | 57 | 75 | 475.6 | 1 | 27.52 | 475.6 | 33.4 | 42
RV40 | 40 | 16000 | 90 | 57 | 75 | 499.4 | 1 | 28.9 | 499.4 | 33.4 | 42
RV40 | 40 | 16000 | 65 | 62 | 75 | 454.5 | 0.516 | 13.58 | 234.7 | 34.3 | 42
RV40 | 40 | 16000 | 70 | 62 | 75 | 453.4 | 0.688 | 18.06 | 312.1 | 34 | 42
RV40 | 40 | 16000 | 75 | 62 | 75 | 451.6 | 0.871 | 22.75 | 393.2 | 33.7 | 42
RV40 | 40 | 16000 | 80 | 62 | 75 | 455.4 | 1 | 26.35 | 455.4 | 33.4 | 42
RV40 | 40 | 16000 | 85 | 62 | 75 | 479 | 1 | 27.72 | 479 | 33.4 | 42
RV40 | 40 | 16000 | 90 | 62 | 75 | 502.9 | 1 | 29.1 | 502.9 | 33.4 | 42
RV40 | 40 | 16000 | 70 | 67 | 75 | 496.2 | 0.466 | 13.37 | 231.1 | 34.2 | 42
RV40 | 40 | 16000 | 75 | 67 | 75 | 494.9 | 0.638 | 18.27 | 315.7 | 33.8 | 42
RV40 | 40 | 16000 | 80 | 67 | 75 | 492.9 | 0.8 | 22.81 | 394.2 | 33.6 | 42
RV40 | 40 | 16000 | 85 | 67 | 75 | 491 | 0.962 | 27.33 | 472.2 | 33.5 | 42
RV40 | 40 | 16000 | 90 | 67 | 75 | 506.6 | 1 | 29.32 | 506.6 | 33.5 | 42
RV40 | 40 | 16000 | 75 | 72 | 75 | 540.9 | 0.425 | 13.31 | 230 | 34 | 42
RV40 | 40 | 16000 | 80 | 72 | 75 | 539.1 | 0.577 | 18 | 311.1 | 33.8 | 42
RV40 | 40 | 16000 | 85 | 72 | 75 | 536.2 | 0.729 | 22.62 | 390.9 | 33.7 | 42
RV40 | 40 | 16000 | 90 | 72 | 75 | 534.4 | 0.881 | 27.24 | 470.7 | 33.6 | 42
RV40 | 40 | 16000 | 80 | 77 | 75 | 589 | 0.395 | 13.46 | 232.6 | 34 | 42
RV40 | 40 | 16000 | 85 | 77 | 75 | 586.6 | 0.526 | 17.87 | 308.8 | 33.9 | 42
RV40 | 40 | 16000 | 90 | 77 | 75 | 583.1 | 0.668 | 22.55 | 389.6 | 33.8 | 42
RV40 | 40 | 16000 | 65 | 57 | 85 | 395.9 | 0.769 | 17.63 | 304.6 | 37.9 | 42
RV40 | 40 | 16000 | 70 | 57 | 85 | 395.8 | 0.972 | 22.26 | 384.6 | 37.4 | 42
RV40 | 40 | 16000 | 75 | 57 | 85 | 413.3 | 1 | 23.92 | 413.3 | 37.2 | 42
RV40 | 40 | 16000 | 80 | 57 | 85 | 436.2 | 1 | 25.24 | 436.2 | 37 | 42
RV40 | 40 | 16000 | 85 | 57 | 85 | 459.3 | 1 | 26.58 | 459.3 | 36.8 | 42
RV40 | 40 | 16000 | 90 | 57 | 85 | 482.7 | 1 | 27.93 | 482.7 | 36.7 | 42
RV40 | 40 | 16000 | 65 | 62 | 85 | 434.1 | 0.516 | 12.97 | 224.1 | 38.4 | 42
RV40 | 40 | 16000 | 70 | 62 | 85 | 433.4 | 0.699 | 17.52 | 302.8 | 37.8 | 42
RV40 | 40 | 16000 | 75 | 62 | 85 | 432.2 | 0.891 | 22.28 | 385 | 37.4 | 42
RV40 | 40 | 16000 | 80 | 62 | 85 | 439.3 | 1 | 25.42 | 439.3 | 37.1 | 42
RV40 | 40 | 16000 | 85 | 62 | 85 | 462.5 | 1 | 26.77 | 462.5 | 36.8 | 42
RV40 | 40 | 16000 | 90 | 62 | 85 | 486.3 | 1 | 28.14 | 486.3 | 36.7 | 42
RV40 | 40 | 16000 | 70 | 67 | 85 | 474.5 | 0.476 | 13.07 | 225.8 | 38.2 | 42
RV40 | 40 | 16000 | 75 | 67 | 85 | 473.8 | 0.648 | 17.77 | 307 | 37.7 | 42
RV40 | 40 | 16000 | 80 | 67 | 85 | 471.9 | 0.81 | 22.12 | 382.2 | 37.3 | 42
RV40 | 40 | 16000 | 85 | 67 | 85 | 471.3 | 0.982 | 26.78 | 462.8 | 36.9 | 42
RV40 | 40 | 16000 | 90 | 67 | 85 | 489.8 | 1 | 28.34 | 489.8 | 36.7 | 42
RV40 | 40 | 16000 | 75 | 72 | 85 | 517.7 | 0.435 | 13.04 | 225.4 | 38 | 42
RV40 | 40 | 16000 | 80 | 72 | 85 | 516.5 | 0.587 | 17.55 | 303.3 | 37.5 | 42
RV40 | 40 | 16000 | 85 | 72 | 85 | 514.2 | 0.749 | 22.29 | 385.2 | 37.2 | 42
RV40 | 40 | 16000 | 90 | 72 | 85 | 512.3 | 0.901 | 26.71 | 461.6 | 36.9 | 42
RV40 | 40 | 16000 | 80 | 77 | 85 | 564.2 | 0.395 | 12.89 | 222.7 | 37.8 | 42
RV40 | 40 | 16000 | 85 | 77 | 85 | 561.9 | 0.537 | 17.45 | 301.5 | 37.3 | 42
RV40 | 40 | 16000 | 90 | 77 | 85 | 558.8 | 0.678 | 21.93 | 379 | 37.2 | 42
RV40 | 40 | 16000 | 65 | 57 | 95 | 376 | 0.78 | 16.96 | 293.1 | 42.3 | 43
RV40 | 40 | 16000 | 70 | 57 | 95 | 376.4 | 0.992 | 21.61 | 373.4 | 41.6 | 43
RV40 | 40 | 16000 | 75 | 57 | 95 | 396.2 | 1 | 22.93 | 396.2 | 41.4 | 43
RV40 | 40 | 16000 | 80 | 57 | 95 | 418.8 | 1 | 24.24 | 418.8 | 41.2 | 43
RV40 | 40 | 16000 | 85 | 57 | 95 | 441.6 | 1 | 25.56 | 441.6 | 40.9 | 43
RV40 | 40 | 16000 | 90 | 57 | 95 | 464.4 | 1 | 26.88 | 464.4 | 40.8 | 43
RV40 | 40 | 16000 | 65 | 62 | 95 | 412 | 0.516 | 12.31 | 212.7 | 43.1 | 43
RV40 | 40 | 16000 | 70 | 62 | 95 | 411.7 | 0.719 | 17.12 | 295.9 | 42.3 | 43
RV40 | 40 | 16000 | 75 | 62 | 95 | 411.3 | 0.911 | 21.68 | 374.7 | 41.6 | 43
RV40 | 40 | 16000 | 80 | 62 | 95 | 421.8 | 1 | 24.41 | 421.8 | 41.2 | 43
RV40 | 40 | 16000 | 85 | 62 | 95 | 444.9 | 1 | 25.75 | 444.9 | 41 | 43
RV40 | 40 | 16000 | 90 | 62 | 95 | 467.7 | 1 | 27.07 | 467.7 | 40.8 | 43
RV40 | 40 | 16000 | 70 | 67 | 95 | 451.1 | 0.476 | 12.42 | 214.7 | 42.9 | 43
RV40 | 40 | 16000 | 75 | 67 | 95 | 450.8 | 0.658 | 17.16 | 296.6 | 42.1 | 43
RV40 | 40 | 16000 | 80 | 67 | 95 | 449.7 | 0.83 | 21.6 | 373.3 | 41.5 | 43
RV40 | 40 | 16000 | 85 | 67 | 95 | 450.4 | 0.992 | 25.86 | 446.8 | 41 | 43
RV40 | 40 | 16000 | 90 | 67 | 95 | 471.1 | 1 | 27.26 | 471.1 | 40.8 | 43
RV40 | 40 | 16000 | 75 | 72 | 95 | 492.4 | 0.435 | 12.4 | 214.3 | 42.7 | 43
RV40 | 40 | 16000 | 80 | 72 | 95 | 491.6 | 0.597 | 16.99 | 293.6 | 41.9 | 43
RV40 | 40 | 16000 | 85 | 72 | 95 | 490 | 0.759 | 21.53 | 372.1 | 41.5 | 43
RV40 | 40 | 16000 | 90 | 72 | 95 | 489 | 0.921 | 26.07 | 450.5 | 41 | 43
RV40 | 40 | 16000 | 80 | 77 | 95 | 537.1 | 0.395 | 12.27 | 212.1 | 42.5 | 43
RV40 | 40 | 16000 | 85 | 77 | 95 | 535.7 | 0.547 | 16.94 | 292.8 | 41.8 | 43
RV40 | 40 | 16000 | 90 | 77 | 95 | 533 | 0.698 | 21.55 | 372.3 | 41.4 | 43
RV40 | 40 | 16000 | 65 | 57 | 105 | 355.1 | 0.8 | 16.44 | 284 | 47.4 | 43
RV40 | 40 | 16000 | 70 | 57 | 105 | 356.4 | 1 | 20.62 | 356.4 | 46.4 | 43
RV40 | 40 | 16000 | 75 | 57 | 105 | 378.1 | 1 | 21.88 | 378.1 | 46.2 | 43
RV40 | 40 | 16000 | 80 | 57 | 105 | 400.4 | 1 | 23.17 | 400.4 | 45.8 | 43
RV40 | 40 | 16000 | 85 | 57 | 105 | 422.9 | 1 | 24.47 | 422.9 | 45.6 | 43
RV40 | 40 | 16000 | 90 | 57 | 105 | 445.5 | 1 | 25.78 | 445.5 | 45.3 | 43
RV40 | 40 | 16000 | 65 | 62 | 105 | 388.6 | 0.527 | 11.84 | 204.6 | 48.9 | 43
RV40 | 40 | 16000 | 70 | 62 | 105 | 389.3 | 0.729 | 16.42 | 283.8 | 47.3 | 43
RV40 | 40 | 16000 | 75 | 62 | 105 | 389.6 | 0.931 | 21 | 362.9 | 46.3 | 43
RV40 | 40 | 16000 | 80 | 62 | 105 | 403.3 | 1 | 23.34 | 403.3 | 45.9 | 43
RV40 | 40 | 16000 | 85 | 62 | 105 | 426 | 1 | 24.65 | 426 | 45.6 | 43
RV40 | 40 | 16000 | 90 | 62 | 105 | 448.7 | 1 | 25.97 | 448.7 | 45.3 | 43
RV40 | 40 | 16000 | 70 | 67 | 105 | 426.1 | 0.476 | 11.74 | 202.8 | 48.3 | 43
RV40 | 40 | 16000 | 75 | 67 | 105 | 426.9 | 0.668 | 16.51 | 285.3 | 47.2 | 43
RV40 | 40 | 16000 | 80 | 67 | 105 | 426 | 0.85 | 20.97 | 362.3 | 46 | 43
RV40 | 40 | 16000 | 85 | 67 | 105 | 429 | 1 | 24.83 | 429 | 45.6 | 43
RV40 | 40 | 16000 | 90 | 67 | 105 | 451.9 | 1 | 26.15 | 451.9 | 45.3 | 43
RV40 | 40 | 16000 | 75 | 72 | 105 | 465.9 | 0.435 | 11.74 | 202.8 | 47.9 | 43
RV40 | 40 | 16000 | 80 | 72 | 105 | 465.9 | 0.607 | 16.38 | 283 | 46.9 | 43
RV40 | 40 | 16000 | 85 | 72 | 105 | 464.9 | 0.78 | 20.97 | 362.4 | 46.2 | 43
RV40 | 40 | 16000 | 90 | 72 | 105 | 464 | 0.952 | 25.56 | 441.6 | 45.6 | 43
RV40 | 40 | 16000 | 80 | 77 | 105 | 508.7 | 0.405 | 11.92 | 206 | 47.7 | 43
RV40 | 40 | 16000 | 85 | 77 | 105 | 508.3 | 0.557 | 16.38 | 283 | 46.7 | 43
RV40 | 40 | 16000 | 90 | 77 | 105 | 506.4 | 0.719 | 21.06 | 364 | 46.1 | 43
RV40 | 40 | 16000 | 65 | 57 | 115 | 331.4 | 0.82 | 15.73 | 271.8 | 53.8 | 44
RV40 | 40 | 16000 | 70 | 57 | 115 | 336.1 | 1 | 19.45 | 336.1 | 52.5 | 44
RV40 | 40 | 16000 | 75 | 57 | 115 | 358 | 1 | 20.72 | 358 | 51.9 | 44
RV40 | 40 | 16000 | 80 | 57 | 115 | 379.7 | 1 | 21.97 | 379.7 | 51.5 | 44
RV40 | 40 | 16000 | 85 | 57 | 115 | 401.6 | 1 | 23.24 | 401.6 | 51.2 | 44
RV40 | 40 | 16000 | 90 | 57 | 115 | 424 | 1 | 24.54 | 424 | 50.6 | 44
RV40 | 40 | 16000 | 65 | 62 | 115 | 361.5 | 0.526 | 11.01 | 190.3 | 56 | 44
RV40 | 40 | 16000 | 70 | 62 | 115 | 364.4 | 0.749 | 15.8 | 273 | 53.4 | 44
RV40 | 40 | 16000 | 75 | 62 | 115 | 364.8 | 0.972 | 20.52 | 354.5 | 52.3 | 44
RV40 | 40 | 16000 | 80 | 62 | 115 | 382.3 | 1 | 22.12 | 382.3 | 51.6 | 44
RV40 | 40 | 16000 | 85 | 62 | 115 | 404.5 | 1 | 23.41 | 404.5 | 51.1 | 44
RV40 | 40 | 16000 | 90 | 62 | 115 | 426.9 | 1 | 24.7 | 426.9 | 50.7 | 44
RV40 | 40 | 16000 | 70 | 67 | 115 | 397.8 | 0.486 | 11.19 | 193.3 | 55.3 | 44
RV40 | 40 | 16000 | 75 | 67 | 115 | 399.8 | 0.688 | 15.93 | 275.2 | 53.2 | 44
RV40 | 40 | 16000 | 80 | 67 | 115 | 399.5 | 0.881 | 20.36 | 351.9 | 52 | 44
RV40 | 40 | 16000 | 85 | 67 | 115 | 407.4 | 1 | 23.58 | 407.4 | 51.2 | 44
RV40 | 40 | 16000 | 90 | 67 | 115 | 430.1 | 1 | 24.89 | 430.1 | 50.7 | 44
RV40 | 40 | 16000 | 75 | 72 | 115 | 435.5 | 0.445 | 11.23 | 194 | 54.8 | 44
RV40 | 40 | 16000 | 80 | 72 | 115 | 437.2 | 0.628 | 15.88 | 274.4 | 52.9 | 44
RV40 | 40 | 16000 | 85 | 72 | 115 | 436.9 | 0.81 | 20.48 | 353.9 | 51.9 | 44
RV40 | 40 | 16000 | 90 | 72 | 115 | 437 | 0.982 | 24.83 | 429.1 | 50.7 | 44
RV40 | 40 | 16000 | 80 | 77 | 115 | 476.7 | 0.405 | 11.17 | 193.1 | 54.2 | 44
RV40 | 40 | 16000 | 85 | 77 | 115 | 477.5 | 0.577 | 15.95 | 275.6 | 52.6 | 44
RV40 | 40 | 16000 | 90 | 77 | 115 | 476.8 | 0.739 | 20.39 | 352.4 | 51.6 | 44
RV40 | 40 | 16000 | 65 | 57 | 125 | 303.3 | 0.82 | 14.39 | 248.7 | 53.3 | 44
RV40 | 40 | 16000 | 70 | 57 | 125 | 306.3 | 1 | 17.73 | 306.3 | 52.8 | 44
RV40 | 40 | 16000 | 75 | 57 | 125 | 325.3 | 1 | 18.83 | 325.3 | 53 | 44
RV40 | 40 | 16000 | 80 | 57 | 125 | 344.2 | 1 | 19.92 | 344.2 | 53.2 | 44
RV40 | 40 | 16000 | 85 | 57 | 125 | 363.6 | 1 | 21.04 | 363.6 | 53.3 | 44
RV40 | 40 | 16000 | 90 | 57 | 125 | 382.5 | 1 | 22.14 | 382.5 | 53.5 | 44
RV40 | 40 | 16000 | 65 | 62 | 125 | 332.5 | 0.526 | 10.13 | 175 | 54.2 | 44
RV40 | 40 | 16000 | 70 | 62 | 125 | 333 | 0.749 | 14.43 | 249.4 | 53.5 | 44
RV40 | 40 | 16000 | 75 | 62 | 125 | 331.6 | 0.972 | 18.65 | 322.3 | 53.1 | 44
RV40 | 40 | 16000 | 80 | 62 | 125 | 346.7 | 1 | 20.06 | 346.7 | 53.2 | 44
RV40 | 40 | 16000 | 85 | 62 | 125 | 366.2 | 1 | 21.19 | 366.2 | 53.3 | 44
RV40 | 40 | 16000 | 90 | 62 | 125 | 385.3 | 1 | 22.3 | 385.3 | 53.5 | 44
RV40 | 40 | 16000 | 70 | 67 | 125 | 363.4 | 0.486 | 10.22 | 176.6 | 54.6 | 44
RV40 | 40 | 16000 | 75 | 67 | 125 | 363.7 | 0.688 | 14.49 | 250.4 | 53.8 | 44
RV40 | 40 | 16000 | 80 | 67 | 125 | 362.5 | 0.891 | 18.69 | 322.9 | 53.5 | 44
RV40 | 40 | 16000 | 85 | 67 | 125 | 368.9 | 1 | 21.35 | 368.9 | 53.3 | 44
RV40 | 40 | 16000 | 90 | 67 | 125 | 388.1 | 1 | 22.46 | 388.1 | 53.5 | 44
RV40 | 40 | 16000 | 75 | 72 | 125 | 396.9 | 0.445 | 10.23 | 176.8 | 54.7 | 44
RV40 | 40 | 16000 | 80 | 72 | 125 | 396.7 | 0.628 | 14.41 | 249 | 54.1 | 44
RV40 | 40 | 16000 | 85 | 72 | 125 | 394.7 | 0.81 | 18.5 | 319.7 | 53.8 | 44
RV40 | 40 | 16000 | 90 | 72 | 125 | 393.6 | 0.992 | 22.6 | 390.5 | 53.5 | 44
RV40 | 40 | 16000 | 80 | 77 | 125 | 433.7 | 0.405 | 10.16 | 175.6 | 55.2 | 44
RV40 | 40 | 16000 | 85 | 77 | 125 | 431.7 | 0.577 | 14.42 | 249.1 | 54.4 | 44
RV40 | 40 | 16000 | 90 | 77 | 125 | 429.5 | 0.749 | 18.62 | 321.8 | 54.1 | 44
RV40 | 40 | 18000 | 65 | 57 | 75 | 421.4 | 0.78 | 16.9 | 328.5 | 37.9 | 42
RV40 | 40 | 18000 | 70 | 57 | 75 | 421.7 | 0.992 | 21.52 | 418.3 | 37.5 | 42
RV40 | 40 | 18000 | 75 | 57 | 75 | 443.5 | 1 | 22.81 | 443.5 | 37.4 | 42
RV40 | 40 | 18000 | 80 | 57 | 75 | 468.2 | 1 | 24.08 | 468.2 | 37.2 | 42
RV40 | 40 | 18000 | 85 | 57 | 75 | 493 | 1 | 25.36 | 493 | 37.2 | 42
RV40 | 40 | 18000 | 90 | 57 | 75 | 518.2 | 1 | 26.66 | 518.2 | 37.2 | 42
RV40 | 40 | 18000 | 65 | 62 | 75 | 461.2 | 0.516 | 12.25 | 238.1 | 38.3 | 42
RV40 | 40 | 18000 | 70 | 62 | 75 | 460.7 | 0.719 | 17.03 | 331.1 | 37.8 | 42
RV40 | 40 | 18000 | 75 | 62 | 75 | 459.6 | 0.911 | 21.54 | 418.8 | 37.5 | 42
RV40 | 40 | 18000 | 80 | 62 | 75 | 471.2 | 1 | 24.24 | 471.2 | 37.2 | 42
RV40 | 40 | 18000 | 85 | 62 | 75 | 496.3 | 1 | 25.53 | 496.3 | 37.2 | 42
RV40 | 40 | 18000 | 90 | 62 | 75 | 521.8 | 1 | 26.84 | 521.8 | 37.3 | 42
RV40 | 40 | 18000 | 70 | 67 | 75 | 503.2 | 0.476 | 12.31 | 239.4 | 38.2 | 42
RV40 | 40 | 18000 | 75 | 67 | 75 | 502.4 | 0.658 | 17.01 | 330.6 | 37.7 | 42
RV40 | 40 | 18000 | 80 | 67 | 75 | 500.9 | 0.84 | 21.65 | 420.9 | 37.4 | 42
RV40 | 40 | 18000 | 85 | 67 | 75 | 501.8 | 1 | 25.81 | 501.8 | 37.3 | 42
RV40 | 40 | 18000 | 90 | 67 | 75 | 525.3 | 1 | 27.02 | 525.3 | 37.3 | 42
RV40 | 40 | 18000 | 75 | 72 | 75 | 548.3 | 0.435 | 12.28 | 238.7 | 37.8 | 42
RV40 | 40 | 18000 | 80 | 72 | 75 | 547 | 0.597 | 16.81 | 326.7 | 37.6 | 42
RV40 | 40 | 18000 | 85 | 72 | 75 | 545.3 | 0.769 | 21.58 | 419.6 | 37.5 | 42
RV40 | 40 | 18000 | 90 | 72 | 75 | 544.1 | 0.931 | 26.06 | 506.7 | 37.4 | 42
RV40 | 40 | 18000 | 80 | 77 | 75 | 596.5 | 0.395 | 12.11 | 235.5 | 37.8 | 42
RV40 | 40 | 18000 | 85 | 77 | 75 | 594.5 | 0.547 | 16.72 | 325 | 37.7 | 42
RV40 | 40 | 18000 | 90 | 77 | 75 | 591.6 | 0.699 | 21.26 | 413.3 | 37.6 | 42
RV40 | 40 | 18000 | 65 | 57 | 85 | 402.5 | 0.8 | 16.56 | 321.9 | 41.8 | 42
RV40 | 40 | 18000 | 70 | 57 | 85 | 403.7 | 1 | 20.77 | 403.7 | 41.2 | 42
RV40 | 40 | 18000 | 75 | 57 | 85 | 427 | 1 | 21.97 | 427 | 41 | 42
RV40 | 40 | 18000 | 80 | 57 | 85 | 451 | 1 | 23.2 | 451 | 40.8 | 42
RV40 | 40 | 18000 | 85 | 57 | 85 | 475.8 | 1 | 24.48 | 475.8 | 40.6 | 42
RV40 | 40 | 18000 | 90 | 57 | 85 | 500.5 | 1 | 25.75 | 500.5 | 40.5 | 42
RV40 | 40 | 18000 | 65 | 62 | 85 | 440.2 | 0.526 | 11.92 | 231.7 | 42.3 | 42
RV40 | 40 | 18000 | 70 | 62 | 85 | 440.1 | 0.729 | 16.5 | 320.8 | 41.7 | 42
RV40 | 40 | 18000 | 75 | 62 | 85 | 439.8 | 0.931 | 21.07 | 409.6 | 41.2 | 42
RV40 | 40 | 18000 | 80 | 62 | 85 | 454.2 | 1 | 23.36 | 454.2 | 40.9 | 42
RV40 | 40 | 18000 | 85 | 62 | 85 | 479.1 | 1 | 24.65 | 479.1 | 40.6 | 42
RV40 | 40 | 18000 | 90 | 62 | 85 | 503.9 | 1 | 25.92 | 503.9 | 40.6 | 42
RV40 | 40 | 18000 | 70 | 67 | 85 | 481 | 0.476 | 11.77 | 228.9 | 42.1 | 42
RV40 | 40 | 18000 | 75 | 67 | 85 | 480.6 | 0.668 | 16.52 | 321.1 | 41.5 | 42
RV40 | 40 | 18000 | 80 | 67 | 85 | 479.1 | 0.851 | 20.96 | 407.5 | 41.1 | 42
RV40 | 40 | 18000 | 85 | 67 | 85 | 482.5 | 1 | 24.82 | 482.5 | 40.7 | 42
RV40 | 40 | 18000 | 90 | 67 | 85 | 507.5 | 1 | 26.11 | 507.5 | 40.6 | 42
RV40 | 40 | 18000 | 75 | 72 | 85 | 524.7 | 0.435 | 11.75 | 228.4 | 41.9 | 42
RV40 | 40 | 18000 | 80 | 72 | 85 | 523.8 | 0.607 | 16.37 | 318.2 | 41.4 | 42
RV40 | 40 | 18000 | 85 | 72 | 85 | 522.4 | 0.779 | 20.95 | 407.2 | 41 | 42
RV40 | 40 | 18000 | 90 | 72 | 85 | 521.1 | 0.952 | 25.51 | 495.9 | 40.7 | 42
RV40 | 40 | 18000 | 80 | 77 | 85 | 571.1 | 0.405 | 11.9 | 231.3 | 41.7 | 42
RV40 | 40 | 18000 | 85 | 77 | 85 | 569.3 | 0.557 | 16.31 | 317 | 41.2 | 42
RV40 | 40 | 18000 | 90 | 77 | 85 | 566.7 | 0.719 | 20.96 | 407.4 | 41 | 42
RV40 | 40 | 18000 | 65 | 57 | 95 | 381.8 | 0.81 | 15.91 | 309.2 | 46.2 | 43
RV40 | 40 | 18000 | 70 | 57 | 95 | 385.5 | 1 | 19.83 | 385.5 | 45.5 | 43
RV40 | 40 | 18000 | 75 | 57 | 95 | 409 | 1 | 21.04 | 409 | 45.3 | 43
RV40 | 40 | 18000 | 80 | 57 | 95 | 433.1 | 1 | 22.28 | 433.1 | 45 | 43
RV40 | 40 | 18000 | 85 | 57 | 95 | 457.1 | 1 | 23.51 | 457.1 | 44.8 | 43
RV40 | 40 | 18000 | 90 | 57 | 95 | 481.3 | 1 | 24.76 | 481.3 | 44.6 | 43
RV40 | 40 | 18000 | 65 | 62 | 95 | 417.5 | 0.526 | 11.31 | 219.8 | 47.1 | 43
RV40 | 40 | 18000 | 70 | 62 | 95 | 418 | 0.749 | 16.11 | 313.1 | 46.1 | 43
RV40 | 40 | 18000 | 75 | 62 | 95 | 418.1 | 0.962 | 20.68 | 402.1 | 45.4 | 43
RV40 | 40 | 18000 | 80 | 62 | 95 | 436 | 1 | 22.43 | 436 | 45.1 | 43
RV40 | 40 | 18000 | 85 | 62 | 95 | 460.2 | 1 | 23.67 | 460.2 | 44.8 | 43
RV40 | 40 | 18000 | 90 | 62 | 95 | 484.7 | 1 | 24.93 | 484.7 | 44.6 | 43
RV40 | 40 | 18000 | 70 | 67 | 95 | 456.2 | 0.486 | 11.4 | 221.7 | 47.2 | 43
RV40 | 40 | 18000 | 75 | 67 | 95 | 456.8 | 0.678 | 15.94 | 309.8 | 46 | 43
RV40 | 40 | 18000 | 80 | 67 | 95 | 456.4 | 0.881 | 20.68 | 402 | 45.3 | 43
RV40 | 40 | 18000 | 85 | 67 | 95 | 463.4 | 1 | 23.84 | 463.4 | 44.9 | 43
RV40 | 40 | 18000 | 90 | 67 | 95 | 488.1 | 1 | 25.11 | 488.1 | 44.6 | 43
RV40 | 40 | 18000 | 75 | 72 | 95 | 498.2 | 0.445 | 11.41 | 221.9 | 46.7 | 43
RV40 | 40 | 18000 | 80 | 72 | 95 | 498.5 | 0.628 | 16.1 | 312.9 | 45.8 | 43
RV40 | 40 | 18000 | 85 | 72 | 95 | 497.5 | 0.8 | 20.47 | 397.9 | 45.3 | 43
RV40 | 40 | 18000 | 90 | 72 | 95 | 497.6 | 0.972 | 24.88 | 483.6 | 44.7 | 43
RV40 | 40 | 18000 | 80 | 77 | 95 | 543.4 | 0.405 | 11.32 | 220 | 46.4 | 43
RV40 | 40 | 18000 | 85 | 77 | 95 | 542.8 | 0.567 | 15.83 | 307.7 | 45.7 | 43
RV40 | 40 | 18000 | 90 | 77 | 95 | 540.7 | 0.739 | 20.56 | 399.6 | 45.2 | 43
RV40 | 40 | 18000 | 65 | 57 | 105 | 360.2 | 0.83 | 15.38 | 299 | 51.3 | 43
RV40 | 40 | 18000 | 70 | 57 | 105 | 367.1 | 1 | 18.88 | 367.1 | 50.4 | 43
RV40 | 40 | 18000 | 75 | 57 | 105 | 390.2 | 1 | 20.07 | 390.2 | 50.1 | 43
RV40 | 40 | 18000 | 80 | 57 | 105 | 413.7 | 1 | 21.28 | 413.7 | 49.7 | 43
RV40 | 40 | 18000 | 85 | 57 | 105 | 437.3 | 1 | 22.49 | 437.3 | 49.4 | 43
RV40 | 40 | 18000 | 90 | 57 | 105 | 461.2 | 1 | 23.72 | 461.2 | 49.1 | 43
RV40 | 40 | 18000 | 65 | 62 | 105 | 393 | 0.537 | 10.85 | 210.9 | 53.1 | 43
RV40 | 40 | 18000 | 70 | 62 | 105 | 395.3 | 0.759 | 15.44 | 300.1 | 51.2 | 43
RV40 | 40 | 18000 | 75 | 62 | 105 | 396.6 | 0.982 | 20.03 | 389.4 | 50.1 | 43
RV40 | 40 | 18000 | 80 | 62 | 105 | 416.4 | 1 | 21.42 | 416.4 | 49.7 | 43
RV40 | 40 | 18000 | 85 | 62 | 105 | 440.3 | 1 | 22.65 | 440.3 | 49.4 | 43
RV40 | 40 | 18000 | 90 | 62 | 105 | 464.3 | 1 | 23.88 | 464.3 | 49.1 | 43
RV40 | 40 | 18000 | 70 | 67 | 105 | 431.2 | 0.486 | 10.78 | 209.5 | 52.3 | 43
RV40 | 40 | 18000 | 75 | 67 | 105 | 432.2 | 0.699 | 15.53 | 301.9 | 51 | 43
RV40 | 40 | 18000 | 80 | 67 | 105 | 432.5 | 0.901 | 20.05 | 389.7 | 50 | 43
RV40 | 40 | 18000 | 85 | 67 | 105 | 443.5 | 1 | 22.81 | 443.5 | 49.5 | 43
RV40 | 40 | 18000 | 90 | 67 | 105 | 467.8 | 1 | 24.06 | 467.8 | 49.2 | 43
RV40 | 40 | 18000 | 75 | 72 | 105 | 471.2 | 0.445 | 10.8 | 209.9 | 52.1 | 43
RV40 | 40 | 18000 | 80 | 72 | 105 | 472.2 | 0.638 | 15.49 | 301.2 | 50.7 | 43
RV40 | 40 | 18000 | 85 | 72 | 105 | 471.6 | 0.83 | 20.14 | 391.5 | 50 | 43
RV40 | 40 | 18000 | 90 | 72 | 105 | 473.4 | 0.992 | 24.16 | 469.7 | 49.2 | 43
RV40 | 40 | 18000 | 80 | 77 | 105 | 514.1 | 0.405 | 10.71 | 208.2 | 51.8 | 43
RV40 | 40 | 18000 | 85 | 77 | 105 | 514.6 | 0.587 | 15.54 | 302.1 | 50.5 | 43
RV40 | 40 | 18000 | 90 | 77 | 105 | 513.3 | 0.759 | 20.05 | 389.7 | 49.9 | 43
RV40 | 40 | 18000 | 65 | 57 | 115 | 335.8 | 0.86 | 14.86 | 288.9 | 57.7 | 44
RV40 | 40 | 18000 | 70 | 57 | 115 | 346 | 1 | 17.8 | 346 | 56.5 | 44
RV40 | 40 | 18000 | 75 | 57 | 115 | 369.1 | 1 | 18.99 | 369.1 | 55.9 | 44
RV40 | 40 | 18000 | 80 | 57 | 115 | 392 | 1 | 20.16 | 392 | 55.5 | 44
RV40 | 40 | 18000 | 85 | 57 | 115 | 415.1 | 1 | 21.35 | 415.1 | 55.1 | 44
RV40 | 40 | 18000 | 90 | 57 | 115 | 438.3 | 1 | 22.55 | 438.3 | 54.7 | 44
RV40 | 40 | 18000 | 65 | 62 | 115 | 365.7 | 0.537 | 10.09 | 196.2 | 60 | 44
RV40 | 40 | 18000 | 70 | 62 | 115 | 369.2 | 0.78 | 14.8 | 287.8 | 57.4 | 44
RV40 | 40 | 18000 | 75 | 62 | 115 | 371.7 | 1 | 19.12 | 371.7 | 55.9 | 44
RV40 | 40 | 18000 | 80 | 62 | 115 | 394.7 | 1 | 20.3 | 394.7 | 55.5 | 44
RV40 | 40 | 18000 | 85 | 62 | 115 | 418.2 | 1 | 21.51 | 418.2 | 55.1 | 44
RV40 | 40 | 18000 | 90 | 62 | 115 | 441.6 | 1 | 22.72 | 441.6 | 54.6 | 44
RV40 | 40 | 18000 | 70 | 67 | 115 | 402.3 | 0.496 | 10.27 | 199.6 | 59.2 | 44
RV40 | 40 | 18000 | 75 | 67 | 115 | 404.8 | 0.719 | 14.97 | 291 | 57 | 44
RV40 | 40 | 18000 | 80 | 67 | 115 | 405.5 | 0.931 | 19.42 | 377.6 | 55.6 | 44
RV40 | 40 | 18000 | 85 | 67 | 115 | 420.9 | 1 | 21.65 | 420.9 | 55.1 | 44
RV40 | 40 | 18000 | 90 | 67 | 115 | 445 | 1 | 22.89 | 445 | 54.6 | 44
RV40 | 40 | 18000 | 75 | 72 | 115 | 440.2 | 0.455 | 10.31 | 200.5 | 59.1 | 44
RV40 | 40 | 18000 | 80 | 72 | 115 | 442.8 | 0.658 | 14.99 | 291.4 | 56.9 | 44
RV40 | 40 | 18000 | 85 | 72 | 115 | 443.5 | 0.85 | 19.4 | 377.1 | 55.6 | 44
RV40 | 40 | 18000 | 90 | 72 | 115 | 448.2 | 1 | 23.06 | 448.2 | 54.7 | 44
RV40 | 40 | 18000 | 80 | 77 | 115 | 481 | 0.415 | 10.27 | 199.7 | 58.9 | 44
RV40 | 40 | 18000 | 85 | 77 | 115 | 483 | 0.597 | 14.84 | 288.5 | 56.5 | 44
RV40 | 40 | 18000 | 90 | 77 | 115 | 482.8 | 0.78 | 19.36 | 376.4 | 55.4 | 44
RV40 | 40 | 18000 | 65 | 57 | 125 | 308.8 | 0.85 | 13.51 | 262.6 | 56.9 | 44
RV40 | 40 | 18000 | 70 | 57 | 125 | 315 | 1 | 16.2 | 315 | 56.8 | 44
RV40 | 40 | 18000 | 75 | 57 | 125 | 334.9 | 1 | 17.23 | 334.9 | 56.9 | 44
RV40 | 40 | 18000 | 80 | 57 | 125 | 355 | 1 | 18.26 | 355 | 57.1 | 44
RV40 | 40 | 18000 | 85 | 57 | 125 | 375 | 1 | 19.29 | 375 | 57.3 | 44
RV40 | 40 | 18000 | 90 | 57 | 125 | 395.1 | 1 | 20.32 | 395.1 | 57.4 | 44
RV40 | 40 | 18000 | 65 | 62 | 125 | 336.2 | 0.537 | 9.28 | 180.4 | 58.2 | 44
RV40 | 40 | 18000 | 70 | 62 | 125 | 337.7 | 0.78 | 13.54 | 263.3 | 57.3 | 44
RV40 | 40 | 18000 | 75 | 62 | 125 | 337.3 | 1 | 17.35 | 337.3 | 56.9 | 44
RV40 | 40 | 18000 | 80 | 62 | 125 | 357.4 | 1 | 18.38 | 357.4 | 57.1 | 44
RV40 | 40 | 18000 | 85 | 62 | 125 | 377.5 | 1 | 19.42 | 377.5 | 57.3 | 44
RV40 | 40 | 18000 | 90 | 62 | 125 | 397.9 | 1 | 20.47 | 397.9 | 57.4 | 44
RV40 | 40 | 18000 | 70 | 67 | 125 | 368.4 | 0.496 | 9.4 | 182.7 | 58.5 | 44
RV40 | 40 | 18000 | 75 | 67 | 125 | 368.9 | 0.719 | 13.64 | 265.1 | 57.7 | 44
RV40 | 40 | 18000 | 80 | 67 | 125 | 367.7 | 0.931 | 17.62 | 342.5 | 57.3 | 44
RV40 | 40 | 18000 | 85 | 67 | 125 | 380.2 | 1 | 19.56 | 380.2 | 57.3 | 44
RV40 | 40 | 18000 | 90 | 67 | 125 | 400.6 | 1 | 20.61 | 400.6 | 57.4 | 44
RV40 | 40 | 18000 | 75 | 72 | 125 | 401.8 | 0.455 | 9.41 | 183 | 58.8 | 44
RV40 | 40 | 18000 | 80 | 72 | 125 | 402 | 0.658 | 13.61 | 264.5 | 58 | 44
RV40 | 40 | 18000 | 85 | 72 | 125 | 400.3 | 0.861 | 17.72 | 344.5 | 57.7 | 44
RV40 | 40 | 18000 | 90 | 72 | 125 | 403.5 | 1 | 20.76 | 403.5 | 57.4 | 44
RV40 | 40 | 18000 | 80 | 77 | 125 | 438.4 | 0.415 | 9.36 | 182 | 59.1 | 44
RV40 | 40 | 18000 | 85 | 77 | 125 | 436.4 | 0.597 | 13.41 | 260.7 | 58.3 | 44
RV40 | 40 | 18000 | 90 | 77 | 125 | 434.7 | 0.79 | 17.65 | 343.2 | 58 | 44
RV50 | 50 | 12000 | 65 | 57 | 75 | 508.3 | 0.621 | 24.35 | 315.6 | 37.5 | 45
RV50 | 50 | 12000 | 70 | 57 | 75 | 505 | 0.743 | 28.96 | 375.3 | 37.5 | 45
RV50 | 50 | 12000 | 75 | 57 | 75 | 501.3 | 0.866 | 33.48 | 433.9 | 37.4 | 45
RV50 | 50 | 12000 | 80 | 57 | 75 | 508 | 0.941 | 36.88 | 477.9 | 37.3 | 45
RV50 | 50 | 12000 | 85 | 57 | 75 | 530.9 | 0.941 | 38.54 | 499.5 | 37.3 | 45
RV50 | 50 | 12000 | 90 | 57 | 75 | 553.4 | 0.941 | 40.17 | 520.6 | 37.2 | 45
RV50 | 50 | 12000 | 65 | 62 | 75 | 559.8 | 0.461 | 19.92 | 258.1 | 37.7 | 45
RV50 | 50 | 12000 | 70 | 62 | 75 | 556.4 | 0.574 | 24.64 | 319.3 | 37.6 | 45
RV50 | 50 | 12000 | 75 | 62 | 75 | 552.5 | 0.687 | 29.27 | 379.4 | 37.5 | 45
RV50 | 50 | 12000 | 80 | 62 | 75 | 548.8 | 0.79 | 33.46 | 433.7 | 37.4 | 45
RV50 | 50 | 12000 | 85 | 62 | 75 | 544.8 | 0.903 | 37.96 | 492 | 37.4 | 45
RV50 | 50 | 12000 | 90 | 62 | 75 | 557.6 | 0.941 | 40.48 | 524.6 | 37.3 | 45
RV50 | 50 | 12000 | 70 | 67 | 75 | 612.1 | 0.423 | 20 | 259.2 | 37.7 | 45
RV50 | 50 | 12000 | 75 | 67 | 75 | 608.2 | 0.527 | 24.72 | 320.4 | 37.6 | 45
RV50 | 50 | 12000 | 80 | 67 | 75 | 603.7 | 0.621 | 28.92 | 374.8 | 37.5 | 45
RV50 | 50 | 12000 | 85 | 67 | 75 | 598.8 | 0.724 | 33.47 | 433.8 | 37.4 | 45
RV50 | 50 | 12000 | 90 | 67 | 75 | 594.5 | 0.828 | 37.98 | 492.2 | 37.3 | 45
RV50 | 50 | 12000 | 75 | 72 | 75 | 668.2 | 0.386 | 19.89 | 257.8 | 37.6 | 45
RV50 | 50 | 12000 | 80 | 72 | 75 | 663.5 | 0.48 | 24.56 | 318.3 | 37.5 | 45
RV50 | 50 | 12000 | 85 | 72 | 75 | 658.2 | 0.574 | 29.14 | 377.7 | 37.4 | 45
RV50 | 50 | 12000 | 90 | 72 | 75 | 652.5 | 0.659 | 33.16 | 429.7 | 37.3 | 45
RV50 | 50 | 12000 | 80 | 77 | 75 | 728 | 0.348 | 19.55 | 253.4 | 37.4 | 45
RV50 | 50 | 12000 | 85 | 77 | 75 | 721.6 | 0.433 | 24.1 | 312.3 | 37.3 | 45
RV50 | 50 | 12000 | 90 | 77 | 75 | 715.3 | 0.517 | 28.56 | 370.1 | 37.1 | 45
RV50 | 50 | 12000 | 65 | 57 | 85 | 487.7 | 0.63 | 23.72 | 307.4 | 41.5 | 45
RV50 | 50 | 12000 | 70 | 57 | 85 | 484.3 | 0.753 | 28.12 | 364.5 | 41.4 | 45
RV50 | 50 | 12000 | 75 | 57 | 85 | 480.8 | 0.884 | 32.81 | 425.2 | 41.4 | 45
RV50 | 50 | 12000 | 80 | 57 | 85 | 491.4 | 0.941 | 35.67 | 462.3 | 41.4 | 45
RV50 | 50 | 12000 | 85 | 57 | 85 | 513.9 | 0.941 | 37.31 | 483.5 | 41.4 | 45
RV50 | 50 | 12000 | 90 | 57 | 85 | 536.4 | 0.941 | 38.94 | 504.6 | 41.4 | 45
RV50 | 50 | 12000 | 65 | 62 | 85 | 537.5 | 0.461 | 19.12 | 247.8 | 41.8 | 45
RV50 | 50 | 12000 | 70 | 62 | 85 | 534.2 | 0.574 | 23.66 | 306.6 | 41.7 | 45
RV50 | 50 | 12000 | 75 | 62 | 85 | 530.6 | 0.696 | 28.5 | 369.4 | 41.7 | 45
RV50 | 50 | 12000 | 80 | 62 | 85 | 527.1 | 0.809 | 32.91 | 426.5 | 41.6 | 45
RV50 | 50 | 12000 | 85 | 62 | 85 | 523.1 | 0.922 | 37.21 | 482.3 | 41.5 | 45
RV50 | 50 | 12000 | 90 | 62 | 85 | 540.5 | 0.941 | 39.24 | 508.5 | 41.5 | 45
RV50 | 50 | 12000 | 70 | 67 | 85 | 588.2 | 0.423 | 19.21 | 249 | 42 | 45
RV50 | 50 | 12000 | 75 | 67 | 85 | 584.9 | 0.527 | 23.77 | 308.1 | 41.9 | 45
RV50 | 50 | 12000 | 80 | 67 | 85 | 580.7 | 0.63 | 28.24 | 366 | 41.8 | 45
RV50 | 50 | 12000 | 85 | 67 | 85 | 576.1 | 0.734 | 32.62 | 422.8 | 41.7 | 45
RV50 | 50 | 12000 | 90 | 67 | 85 | 572.4 | 0.837 | 36.98 | 479.2 | 41.6 | 45
RV50 | 50 | 12000 | 75 | 72 | 85 | 643.2 | 0.386 | 19.14 | 248.1 | 42.1 | 45
RV50 | 50 | 12000 | 80 | 72 | 85 | 638.7 | 0.48 | 23.64 | 306.4 | 41.9 | 45
RV50 | 50 | 12000 | 85 | 72 | 85 | 633.6 | 0.574 | 28.06 | 363.6 | 41.8 | 45
RV50 | 50 | 12000 | 90 | 72 | 85 | 628.4 | 0.677 | 32.85 | 425.7 | 41.7 | 45
RV50 | 50 | 12000 | 80 | 77 | 85 | 700.7 | 0.348 | 18.82 | 243.9 | 42.1 | 45
RV50 | 50 | 12000 | 85 | 77 | 85 | 695.1 | 0.442 | 23.71 | 307.3 | 41.9 | 45
RV50 | 50 | 12000 | 90 | 77 | 85 | 688.9 | 0.527 | 28 | 362.9 | 41.8 | 45
RV50 | 50 | 12000 | 65 | 57 | 95 | 465.6 | 0.64 | 22.98 | 297.8 | 45.7 | 45
RV50 | 50 | 12000 | 70 | 57 | 95 | 462.6 | 0.771 | 27.53 | 356.8 | 45.7 | 45
RV50 | 50 | 12000 | 75 | 57 | 95 | 459.2 | 0.903 | 32 | 414.7 | 45.6 | 45
RV50 | 50 | 12000 | 80 | 57 | 95 | 473.7 | 0.941 | 34.38 | 445.6 | 45.7 | 45
RV50 | 50 | 12000 | 85 | 57 | 95 | 495.9 | 0.941 | 36 | 466.6 | 45.8 | 45
RV50 | 50 | 12000 | 90 | 57 | 95 | 518.4 | 0.941 | 37.63 | 487.7 | 45.9 | 45
RV50 | 50 | 12000 | 65 | 62 | 95 | 513.4 | 0.461 | 18.26 | 236.7 | 46.2 | 45
RV50 | 50 | 12000 | 70 | 62 | 95 | 510.6 | 0.583 | 22.98 | 297.8 | 46.1 | 45
RV50 | 50 | 12000 | 75 | 62 | 95 | 507.4 | 0.706 | 27.62 | 358 | 46 | 45
RV50 | 50 | 12000 | 80 | 62 | 95 | 504.1 | 0.818 | 31.84 | 412.6 | 45.9 | 45
RV50 | 50 | 12000 | 85 | 62 | 95 | 499.7 | 0.941 | 36.27 | 470.1 | 45.8 | 45
RV50 | 50 | 12000 | 90 | 62 | 95 | 522.5 | 0.941 | 37.92 | 491.5 | 45.9 | 45
RV50 | 50 | 12000 | 70 | 67 | 95 | 563.1 | 0.423 | 18.4 | 238.4 | 46.5 | 45
RV50 | 50 | 12000 | 75 | 67 | 95 | 559.9 | 0.536 | 23.16 | 300.2 | 46.4 | 45
RV50 | 50 | 12000 | 80 | 67 | 95 | 556.1 | 0.64 | 27.45 | 355.7 | 46.3 | 45
RV50 | 50 | 12000 | 85 | 67 | 95 | 551.9 | 0.753 | 32.05 | 415.4 | 46.2 | 45
RV50 | 50 | 12000 | 90 | 67 | 95 | 548.1 | 0.856 | 36.2 | 469.2 | 46.1 | 45
RV50 | 50 | 12000 | 75 | 72 | 95 | 615.3 | 0.386 | 18.31 | 237.3 | 46.8 | 45
RV50 | 50 | 12000 | 80 | 72 | 95 | 611.2 | 0.489 | 23.07 | 299 | 46.6 | 45
RV50 | 50 | 12000 | 85 | 72 | 95 | 606.6 | 0.583 | 27.3 | 353.8 | 46.5 | 45
RV50 | 50 | 12000 | 90 | 72 | 95 | 601.6 | 0.687 | 31.88 | 413.2 | 46.4 | 45
RV50 | 50 | 12000 | 80 | 77 | 95 | 670.8 | 0.348 | 18.02 | 233.5 | 47 | 45
RV50 | 50 | 12000 | 85 | 77 | 95 | 665.5 | 0.442 | 22.71 | 294.3 | 46.8 | 45
RV50 | 50 | 12000 | 90 | 77 | 95 | 660.1 | 0.536 | 27.31 | 354 | 46.7 | 45
RV50 | 50 | 12000 | 65 | 57 | 105 | 443.1 | 0.64 | 21.88 | 283.5 | 50.1 | 46
RV50 | 50 | 12000 | 70 | 57 | 105 | 440.3 | 0.781 | 26.53 | 343.8 | 50 | 46
RV50 | 50 | 12000 | 75 | 57 | 105 | 437.4 | 0.922 | 31.12 | 403.3 | 50 | 46
RV50 | 50 | 12000 | 80 | 57 | 105 | 455.6 | 0.941 | 33.08 | 428.7 | 50.2 | 46
RV50 | 50 | 12000 | 85 | 57 | 105 | 477.7 | 0.941 | 34.68 | 449.4 | 50.4 | 46
RV50 | 50 | 12000 | 90 | 57 | 105 | 499.6 | 0.941 | 36.27 | 470 | 50.6 | 46
RV50 | 50 | 12000 | 65 | 62 | 105 | 489.4 | 0.461 | 17.41 | 225.6 | 50.7 | 46
RV50 | 50 | 12000 | 70 | 62 | 105 | 486.9 | 0.593 | 22.27 | 288.6 | 50.6 | 46
RV50 | 50 | 12000 | 75 | 62 | 105 | 483.9 | 0.715 | 26.7 | 346 | 50.5 | 46
RV50 | 50 | 12000 | 80 | 62 | 105 | 480.8 | 0.837 | 31.06 | 402.6 | 50.4 | 46
RV50 | 50 | 12000 | 85 | 62 | 105 | 481.4 | 0.941 | 34.95 | 452.9 | 50.4 | 46
RV50 | 50 | 12000 | 90 | 62 | 105 | 503.5 | 0.941 | 36.55 | 473.7 | 50.6 | 46
RV50 | 50 | 12000 | 70 | 67 | 105 | 536.6 | 0.423 | 17.53 | 227.2 | 51.2 | 46
RV50 | 50 | 12000 | 75 | 67 | 105 | 533.7 | 0.536 | 22.08 | 286.2 | 51.1 | 46
RV50 | 50 | 12000 | 80 | 67 | 105 | 530 | 0.649 | 26.54 | 344 | 51 | 46
RV50 | 50 | 12000 | 85 | 67 | 105 | 526.3 | 0.762 | 30.95 | 401.1 | 50.8 | 46
RV50 | 50 | 12000 | 90 | 67 | 105 | 522.2 | 0.875 | 35.25 | 456.9 | 50.7 | 46
RV50 | 50 | 12000 | 75 | 72 | 105 | 586.4 | 0.386 | 17.45 | 226.2 | 51.6 | 46
RV50 | 50 | 12000 | 80 | 72 | 105 | 582.8 | 0.489 | 22 | 285.1 | 51.5 | 46
RV50 | 50 | 12000 | 85 | 72 | 105 | 578.6 | 0.593 | 26.46 | 342.9 | 51.3 | 46
RV50 | 50 | 12000 | 90 | 72 | 105 | 574.1 | 0.696 | 30.84 | 399.7 | 51.2 | 46
RV50 | 50 | 12000 | 80 | 77 | 105 | 639.6 | 0.357 | 17.64 | 228.6 | 52 | 46
RV50 | 50 | 12000 | 85 | 77 | 105 | 634.9 | 0.452 | 22.12 | 286.7 | 51.8 | 46
RV50 | 50 | 12000 | 90 | 77 | 105 | 630 | 0.546 | 26.53 | 343.8 | 51.6 | 46
RV50 | 50 | 12000 | 65 | 57 | 115 | 418.7 | 0.649 | 20.97 | 271.8 | 55.1 | 46
RV50 | 50 | 12000 | 70 | 57 | 115 | 416 | 0.8 | 25.66 | 332.6 | 55 | 46
RV50 | 50 | 12000 | 75 | 57 | 115 | 414.1 | 0.941 | 30.05 | 389.5 | 54.9 | 46
RV50 | 50 | 12000 | 80 | 57 | 115 | 435.6 | 0.941 | 31.62 | 409.8 | 55.2 | 46
RV50 | 50 | 12000 | 85 | 57 | 115 | 457 | 0.941 | 33.18 | 430 | 55.5 | 46
RV50 | 50 | 12000 | 90 | 57 | 115 | 478.4 | 0.941 | 34.72 | 450 | 55.7 | 46
RV50 | 50 | 12000 | 65 | 62 | 115 | 462.7 | 0.461 | 16.46 | 213.3 | 55.9 | 46
RV50 | 50 | 12000 | 70 | 62 | 115 | 460.5 | 0.593 | 21.06 | 272.9 | 55.7 | 46
RV50 | 50 | 12000 | 75 | 62 | 115 | 457.7 | 0.724 | 25.58 | 331.5 | 55.6 | 46
RV50 | 50 | 12000 | 80 | 62 | 115 | 453.9 | 0.865 | 30.31 | 392.8 | 55.4 | 46
RV50 | 50 | 12000 | 85 | 62 | 115 | 460.6 | 0.941 | 33.43 | 433.3 | 55.5 | 46
RV50 | 50 | 12000 | 90 | 62 | 115 | 482.2 | 0.941 | 35 | 453.6 | 55.7 | 46
RV50 | 50 | 12000 | 70 | 67 | 115 | 507.3 | 0.423 | 16.57 | 214.8 | 56.4 | 46
RV50 | 50 | 12000 | 75 | 67 | 115 | 504.7 | 0.546 | 21.25 | 275.4 | 56.2 | 46
RV50 | 50 | 12000 | 80 | 67 | 115 | 501.4 | 0.668 | 25.84 | 334.9 | 56.1 | 46
RV50 | 50 | 12000 | 85 | 67 | 115 | 498.2 | 0.781 | 30.02 | 389 | 56 | 46
RV50 | 50 | 12000 | 90 | 67 | 115 | 493.6 | 0.903 | 34.4 | 445.8 | 55.8 | 46
RV50 | 50 | 12000 | 75 | 72 | 115 | 554.8 | 0.386 | 16.51 | 214 | 57 | 46
RV50 | 50 | 12000 | 80 | 72 | 115 | 551.5 | 0.499 | 21.22 | 275 | 56.8 | 46
RV50 | 50 | 12000 | 85 | 72 | 115 | 547.8 | 0.612 | 25.85 | 335 | 56.6 | 46
RV50 | 50 | 12000 | 90 | 72 | 115 | 543.4 | 0.715 | 29.98 | 388.5 | 56.5 | 46
RV50 | 50 | 12000 | 80 | 77 | 115 | 605.5 | 0.358 | 16.71 | 216.5 | 57.5 | 46
RV50 | 50 | 12000 | 85 | 77 | 115 | 601.2 | 0.452 | 20.95 | 271.5 | 57.2 | 46
RV50 | 50 | 12000 | 90 | 77 | 115 | 596.5 | 0.555 | 25.55 | 331.1 | 57.1 | 46
RV50 | 50 | 12000 | 65 | 57 | 125 | 393.4 | 0.668 | 20.28 | 262.8 | 60.8 | 46
RV50 | 50 | 12000 | 70 | 57 | 125 | 391 | 0.818 | 24.69 | 320 | 60.4 | 46
RV50 | 50 | 12000 | 75 | 57 | 125 | 393.6 | 0.941 | 28.57 | 370.3 | 60.3 | 46
RV50 | 50 | 12000 | 80 | 57 | 125 | 414.7 | 0.941 | 30.1 | 390.1 | 60.6 | 46
RV50 | 50 | 12000 | 85 | 57 | 125 | 435.5 | 0.941 | 31.61 | 409.7 | 60.9 | 46
RV50 | 50 | 12000 | 90 | 57 | 125 | 456.4 | 0.941 | 33.13 | 429.4 | 61.2 | 46
RV50 | 50 | 12000 | 65 | 62 | 125 | 435.2 | 0.47 | 15.79 | 204.7 | 61.7 | 46
RV50 | 50 | 12000 | 70 | 62 | 125 | 433.1 | 0.602 | 20.12 | 260.8 | 61.2 | 46
RV50 | 50 | 12000 | 75 | 62 | 125 | 430.4 | 0.743 | 24.68 | 319.9 | 60.9 | 46
RV50 | 50 | 12000 | 80 | 62 | 125 | 426.4 | 0.894 | 29.41 | 381.1 | 60.7 | 46
RV50 | 50 | 12000 | 85 | 62 | 125 | 438.9 | 0.941 | 31.86 | 412.9 | 60.9 | 46
RV50 | 50 | 12000 | 90 | 62 | 125 | 460 | 0.941 | 33.39 | 432.7 | 61.2 | 46
RV50 | 50 | 12000 | 70 | 67 | 125 | 476.9 | 0.423 | 15.58 | 201.9 | 62.1 | 46
RV50 | 50 | 12000 | 75 | 67 | 125 | 475.2 | 0.555 | 20.35 | 263.8 | 61.8 | 46
RV50 | 50 | 12000 | 80 | 67 | 125 | 471.8 | 0.677 | 24.66 | 319.6 | 61.5 | 46
RV50 | 50 | 12000 | 85 | 67 | 125 | 468.9 | 0.809 | 29.27 | 379.4 | 61.4 | 46
RV50 | 50 | 12000 | 90 | 67 | 125 | 464.1 | 0.941 | 33.69 | 436.6 | 61.2 | 46
RV50 | 50 | 12000 | 75 | 72 | 125 | 522.1 | 0.386 | 15.54 | 201.4 | 62.7 | 46
RV50 | 50 | 12000 | 80 | 72 | 125 | 519.3 | 0.508 | 20.35 | 263.8 | 62.3 | 46
RV50 | 50 | 12000 | 85 | 72 | 125 | 515.6 | 0.621 | 24.71 | 320.2 | 62.1 | 46
RV50 | 50 | 12000 | 90 | 72 | 125 | 511.9 | 0.734 | 28.98 | 375.6 | 61.9 | 46
RV50 | 50 | 12000 | 80 | 77 | 125 | 570 | 0.358 | 15.73 | 203.8 | 63.2 | 46
RV50 | 50 | 12000 | 85 | 77 | 125 | 566.1 | 0.461 | 20.14 | 261 | 62.9 | 46
RV50 | 50 | 12000 | 90 | 77 | 125 | 561.9 | 0.565 | 24.48 | 317.2 | 62.7 | 46
RV50 | 50 | 15000 | 65 | 57 | 75 | 529.7 | 0.649 | 21.23 | 343.9 | 40.7 | 45
RV50 | 50 | 15000 | 70 | 57 | 75 | 526.8 | 0.781 | 25.39 | 411.3 | 40.6 | 45
RV50 | 50 | 15000 | 75 | 57 | 75 | 523.8 | 0.922 | 29.81 | 482.9 | 40.5 | 45
RV50 | 50 | 15000 | 80 | 57 | 75 | 544.6 | 0.941 | 31.62 | 512.3 | 40.4 | 45
RV50 | 50 | 15000 | 85 | 57 | 75 | 569.8 | 0.941 | 33.09 | 536.1 | 40.4 | 45
RV50 | 50 | 15000 | 90 | 57 | 75 | 594.4 | 0.941 | 34.52 | 559.2 | 40.3 | 45
RV50 | 50 | 15000 | 65 | 62 | 75 | 582.3 | 0.461 | 16.57 | 268.4 | 40.9 | 45
RV50 | 50 | 15000 | 70 | 62 | 75 | 579.3 | 0.593 | 21.2 | 343.4 | 40.7 | 45
RV50 | 50 | 15000 | 75 | 62 | 75 | 575.6 | 0.715 | 25.41 | 411.6 | 40.6 | 45
RV50 | 50 | 15000 | 80 | 62 | 75 | 572.4 | 0.847 | 29.92 | 484.7 | 40.5 | 45
RV50 | 50 | 15000 | 85 | 62 | 75 | 574 | 0.941 | 33.33 | 540 | 40.4 | 45
RV50 | 50 | 15000 | 90 | 62 | 75 | 598.8 | 0.941 | 34.77 | 563.3 | 40.3 | 45
RV50 | 50 | 15000 | 70 | 67 | 75 | 635.6 | 0.423 | 16.61 | 269.1 | 40.8 | 45
RV50 | 50 | 15000 | 75 | 67 | 75 | 631.8 | 0.536 | 20.91 | 338.8 | 40.7 | 45
RV50 | 50 | 15000 | 80 | 67 | 75 | 627.4 | 0.659 | 25.51 | 413.2 | 40.6 | 45
RV50 | 50 | 15000 | 85 | 67 | 75 | 622.9 | 0.772 | 29.67 | 480.6 | 40.5 | 45
RV50 | 50 | 15000 | 90 | 67 | 75 | 618.7 | 0.884 | 33.78 | 547.2 | 40.3 | 45
RV50 | 50 | 15000 | 75 | 72 | 75 | 693.1 | 0.386 | 16.5 | 267.3 | 40.7 | 45
RV50 | 50 | 15000 | 80 | 72 | 75 | 688.6 | 0.489 | 20.8 | 336.9 | 40.5 | 45
RV50 | 50 | 15000 | 85 | 72 | 75 | 683.4 | 0.602 | 25.4 | 411.5 | 40.4 | 45
RV50 | 50 | 15000 | 90 | 72 | 75 | 677.7 | 0.706 | 29.52 | 478.2 | 40.3 | 45
RV50 | 50 | 15000 | 80 | 77 | 75 | 752.7 | 0.358 | 16.61 | 269.1 | 40.5 | 45
RV50 | 50 | 15000 | 85 | 77 | 75 | 746.4 | 0.452 | 20.81 | 337.1 | 40.3 | 45
RV50 | 50 | 15000 | 90 | 77 | 75 | 740 | 0.546 | 24.93 | 403.8 | 40.2 | 45
RV50 | 50 | 15000 | 65 | 57 | 85 | 507.5 | 0.649 | 20.34 | 329.5 | 44.7 | 45
RV50 | 50 | 15000 | 70 | 57 | 85 | 504.9 | 0.8 | 24.92 | 403.7 | 44.6 | 45
RV50 | 50 | 15000 | 75 | 57 | 85 | 501.5 | 0.941 | 29.12 | 471.8 | 44.5 | 45
RV50 | 50 | 15000 | 80 | 57 | 85 | 526.2 | 0.941 | 30.56 | 495 | 44.6 | 45
RV50 | 50 | 15000 | 85 | 57 | 85 | 551.2 | 0.941 | 32.01 | 518.5 | 44.6 | 45
RV50 | 50 | 15000 | 90 | 57 | 85 | 576.4 | 0.941 | 33.47 | 542.2 | 44.6 | 45
RV50 | 50 | 15000 | 65 | 62 | 85 | 558.3 | 0.461 | 15.89 | 257.4 | 45.1 | 45
RV50 | 50 | 15000 | 70 | 62 | 85 | 555.7 | 0.593 | 20.33 | 329.3 | 44.9 | 45
RV50 | 50 | 15000 | 75 | 62 | 85 | 552.3 | 0.724 | 24.7 | 400.1 | 44.8 | 45
RV50 | 50 | 15000 | 80 | 62 | 85 | 549.4 | 0.856 | 29.03 | 470.3 | 44.7 | 45
RV50 | 50 | 15000 | 85 | 62 | 85 | 555.3 | 0.941 | 32.25 | 522.4 | 44.6 | 45
RV50 | 50 | 15000 | 90 | 62 | 85 | 580.6 | 0.941 | 33.72 | 546.2 | 44.6 | 45
RV50 | 50 | 15000 | 70 | 67 | 85 | 610.3 | 0.423 | 15.95 | 258.4 | 45.2 | 45
RV50 | 50 | 15000 | 75 | 67 | 85 | 607.1 | 0.546 | 20.45 | 331.3 | 45 | 45
RV50 | 50 | 15000 | 80 | 67 | 85 | 603 | 0.668 | 24.86 | 402.8 | 44.9 | 45
RV50 | 50 | 15000 | 85 | 67 | 85 | 599 | 0.79 | 29.22 | 473.4 | 44.8 | 45
RV50 | 50 | 15000 | 90 | 67 | 85 | 595.3 | 0.903 | 33.19 | 537.7 | 44.7 | 45
RV50 | 50 | 15000 | 75 | 72 | 85 | 665.6 | 0.386 | 15.85 | 256.7 | 45.3 | 45
RV50 | 50 | 15000 | 80 | 72 | 85 | 661.6 | 0.499 | 20.36 | 329.9 | 45.1 | 45
RV50 | 50 | 15000 | 85 | 72 | 85 | 656.8 | 0.612 | 24.8 | 401.7 | 45 | 45
RV50 | 50 | 15000 | 90 | 72 | 85 | 651.7 | 0.715 | 28.77 | 466 | 44.8 | 45
RV50 | 50 | 15000 | 80 | 77 | 85 | 723.7 | 0.357 | 15.97 | 258.7 | 45.2 | 45
RV50 | 50 | 15000 | 85 | 77 | 85 | 717.9 | 0.452 | 20.01 | 324.2 | 45.1 | 45
RV50 | 50 | 15000 | 90 | 77 | 85 | 711.9 | 0.555 | 24.4 | 395.2 | 44.9 | 45
RV50 | 50 | 15000 | 65 | 57 | 95 | 483.9 | 0.659 | 19.67 | 318.7 | 49 | 45
RV50 | 50 | 15000 | 70 | 57 | 95 | 481.7 | 0.809 | 24.06 | 389.7 | 48.9 | 45
RV50 | 50 | 15000 | 75 | 57 | 95 | 481.9 | 0.941 | 27.99 | 453.4 | 48.8 | 45
RV50 | 50 | 15000 | 80 | 57 | 95 | 506.8 | 0.941 | 29.43 | 476.8 | 49 | 45
RV50 | 50 | 15000 | 85 | 57 | 95 | 531.8 | 0.941 | 30.88 | 500.3 | 49.1 | 45
RV50 | 50 | 15000 | 90 | 57 | 95 | 556.3 | 0.941 | 32.3 | 523.3 | 49.2 | 45
RV50 | 50 | 15000 | 65 | 62 | 95 | 532.9 | 0.47 | 15.48 | 250.7 | 49.5 | 45
RV50 | 50 | 15000 | 70 | 62 | 95 | 530.8 | 0.602 | 19.73 | 319.6 | 49.4 | 45
RV50 | 50 | 15000 | 75 | 62 | 95 | 527.5 | 0.743 | 24.2 | 392 | 49.2 | 45
RV50 | 50 | 15000 | 80 | 62 | 95 | 524.8 | 0.875 | 28.35 | 459.2 | 49.1 | 45
RV50 | 50 | 15000 | 85 | 62 | 95 | 535.8 | 0.941 | 31.12 | 504.1 | 49.1 | 45
RV50 | 50 | 15000 | 90 | 62 | 95 | 560.4 | 0.941 | 32.54 | 527.2 | 49.2 | 45
RV50 | 50 | 15000 | 70 | 67 | 95 | 583 | 0.423 | 15.23 | 246.8 | 49.8 | 45
RV50 | 50 | 15000 | 75 | 67 | 95 | 580 | 0.555 | 19.87 | 321.9 | 49.6 | 45
RV50 | 50 | 15000 | 80 | 67 | 95 | 576.2 | 0.677 | 24.09 | 390.3 | 49.5 | 45
RV50 | 50 | 15000 | 85 | 67 | 95 | 572.4 | 0.8 | 28.25 | 457.7 | 49.4 | 45
RV50 | 50 | 15000 | 90 | 67 | 95 | 568.9 | 0.922 | 32.38 | 524.5 | 49.3 | 45
RV50 | 50 | 15000 | 75 | 72 | 95 | 635.8 | 0.386 | 15.14 | 245.2 | 50.1 | 45
RV50 | 50 | 15000 | 80 | 72 | 95 | 632.3 | 0.508 | 19.83 | 321.2 | 49.9 | 45
RV50 | 50 | 15000 | 85 | 72 | 95 | 627.8 | 0.621 | 24.06 | 389.8 | 49.7 | 45
RV50 | 50 | 15000 | 90 | 72 | 95 | 623.2 | 0.734 | 28.23 | 457.3 | 49.6 | 45
RV50 | 50 | 15000 | 80 | 77 | 95 | 691.5 | 0.357 | 15.26 | 247.2 | 50.2 | 45
RV50 | 50 | 15000 | 85 | 77 | 95 | 686.5 | 0.461 | 19.54 | 316.5 | 50 | 45
RV50 | 50 | 15000 | 90 | 77 | 95 | 680.9 | 0.564 | 23.72 | 384.3 | 49.9 | 45
RV50 | 50 | 15000 | 65 | 57 | 105 | 460.2 | 0.668 | 18.98 | 307.4 | 53.4 | 46
RV50 | 50 | 15000 | 70 | 57 | 105 | 457.9 | 0.828 | 23.4 | 379.1 | 53.3 | 46
RV50 | 50 | 15000 | 75 | 57 | 105 | 462.6 | 0.941 | 26.86 | 435.2 | 53.3 | 46
RV50 | 50 | 15000 | 80 | 57 | 105 | 487 | 0.941 | 28.28 | 458.2 | 53.5 | 46
RV50 | 50 | 15000 | 85 | 57 | 105 | 511.3 | 0.941 | 29.69 | 481 | 53.7 | 46
RV50 | 50 | 15000 | 90 | 57 | 105 | 535.3 | 0.941 | 31.09 | 503.6 | 53.9 | 46
RV50 | 50 | 15000 | 65 | 62 | 105 | 507 | 0.47 | 14.72 | 238.5 | 54.1 | 46
RV50 | 50 | 15000 | 70 | 62 | 105 | 505.1 | 0.612 | 19.07 | 308.9 | 53.9 | 46
RV50 | 50 | 15000 | 75 | 62 | 105 | 502.4 | 0.753 | 23.34 | 378.1 | 53.8 | 46
RV50 | 50 | 15000 | 80 | 62 | 105 | 498.6 | 0.903 | 27.8 | 450.3 | 53.6 | 46
RV50 | 50 | 15000 | 85 | 62 | 105 | 515.1 | 0.941 | 29.91 | 484.6 | 53.7 | 46
RV50 | 50 | 15000 | 90 | 62 | 105 | 539.3 | 0.941 | 31.32 | 507.4 | 53.9 | 46
RV50 | 50 | 15000 | 70 | 67 | 105 | 554.5 | 0.423 | 14.49 | 234.7 | 54.5 | 46
RV50 | 50 | 15000 | 75 | 67 | 105 | 551.9 | 0.555 | 18.91 | 306.4 | 54.3 | 46
RV50 | 50 | 15000 | 80 | 67 | 105 | 548.5 | 0.687 | 23.25 | 376.7 | 54.2 | 46
RV50 | 50 | 15000 | 85 | 67 | 105 | 545.3 | 0.818 | 27.55 | 446.3 | 54.1 | 46
RV50 | 50 | 15000 | 90 | 67 | 105 | 543.3 | 0.941 | 31.56 | 511.2 | 53.9 | 46
RV50 | 50 | 15000 | 75 | 72 | 105 | 604.8 | 0.395 | 14.75 | 239 | 55 | 46
RV50 | 50 | 15000 | 80 | 72 | 105 | 602 | 0.508 | 18.88 | 305.8 | 54.7 | 46
RV50 | 50 | 15000 | 85 | 72 | 105 | 597.8 | 0.63 | 23.26 | 376.8 | 54.6 | 46
RV50 | 50 | 15000 | 90 | 72 | 105 | 593.8 | 0.753 | 27.59 | 446.9 | 54.4 | 46
RV50 | 50 | 15000 | 80 | 77 | 105 | 658.4 | 0.358 | 14.53 | 235.4 | 55.3 | 46
RV50 | 50 | 15000 | 85 | 77 | 105 | 653.8 | 0.47 | 18.98 | 307.5 | 55 | 46
RV50 | 50 | 15000 | 90 | 77 | 105 | 648.9 | 0.583 | 23.36 | 378.5 | 54.9 | 46
RV50 | 50 | 15000 | 65 | 57 | 115 | 434.3 | 0.677 | 18.16 | 294.2 | 58.4 | 46
RV50 | 50 | 15000 | 70 | 57 | 115 | 431.9 | 0.847 | 22.57 | 365.7 | 58.3 | 46
RV50 | 50 | 15000 | 75 | 57 | 115 | 441.2 | 0.941 | 25.62 | 415.1 | 58.4 | 46
RV50 | 50 | 15000 | 80 | 57 | 115 | 464.7 | 0.941 | 26.99 | 437.2 | 58.7 | 46
RV50 | 50 | 15000 | 85 | 57 | 115 | 488.4 | 0.941 | 28.36 | 459.5 | 58.9 | 46
RV50 | 50 | 15000 | 90 | 57 | 115 | 511.8 | 0.941 | 29.72 | 481.5 | 59.2 | 46
RV50 | 50 | 15000 | 65 | 62 | 115 | 478.1 | 0.47 | 13.88 | 224.9 | 59.3 | 46
RV50 | 50 | 15000 | 70 | 62 | 115 | 476.5 | 0.621 | 18.27 | 295.9 | 59 | 46
RV50 | 50 | 15000 | 75 | 62 | 115 | 474.4 | 0.772 | 22.59 | 366 | 58.8 | 46
RV50 | 50 | 15000 | 80 | 62 | 115 | 471 | 0.922 | 26.81 | 434.3 | 58.7 | 46
RV50 | 50 | 15000 | 85 | 62 | 115 | 492.1 | 0.941 | 28.57 | 462.9 | 59 | 46
RV50 | 50 | 15000 | 90 | 62 | 115 | 515.8 | 0.941 | 29.95 | 485.2 | 59.2 | 46
RV50 | 50 | 15000 | 70 | 67 | 115 | 523.3 | 0.433 | 13.98 | 226.4 | 59.8 | 46
RV50 | 50 | 15000 | 75 | 67 | 115 | 521.2 | 0.574 | 18.46 | 299.1 | 59.6 | 46
RV50 | 50 | 15000 | 80 | 67 | 115 | 518.2 | 0.706 | 22.57 | 365.6 | 59.4 | 46
RV50 | 50 | 15000 | 85 | 67 | 115 | 515.4 | 0.847 | 26.94 | 436.4 | 59.2 | 46
RV50 | 50 | 15000 | 90 | 67 | 115 | 519.8 | 0.941 | 30.19 | 489 | 59.2 | 46
RV50 | 50 | 15000 | 75 | 72 | 115 | 571.2 | 0.395 | 13.93 | 225.7 | 60.3 | 46
RV50 | 50 | 15000 | 80 | 72 | 115 | 568.7 | 0.517 | 18.17 | 294.3 | 60.1 | 46
RV50 | 50 | 15000 | 85 | 72 | 115 | 564.9 | 0.649 | 22.64 | 366.7 | 59.9 | 46
RV50 | 50 | 15000 | 90 | 72 | 115 | 561.1 | 0.771 | 26.72 | 432.8 | 59.7 | 46
RV50 | 50 | 15000 | 80 | 77 | 115 | 621.8 | 0.358 | 13.72 | 222.3 | 60.8 | 46
RV50 | 50 | 15000 | 85 | 77 | 115 | 618 | 0.48 | 18.3 | 296.5 | 60.5 | 46
RV50 | 50 | 15000 | 90 | 77 | 115 | 613.5 | 0.593 | 22.44 | 363.6 | 60.3 | 46
RV50 | 50 | 15000 | 65 | 57 | 125 | 407.6 | 0.696 | 17.52 | 283.8 | 64.2 | 46
RV50 | 50 | 15000 | 70 | 57 | 125 | 405.3 | 0.875 | 21.89 | 354.6 | 63.7 | 46
RV50 | 50 | 15000 | 75 | 57 | 125 | 418.6 | 0.941 | 24.31 | 393.8 | 63.8 | 46
RV50 | 50 | 15000 | 80 | 57 | 125 | 441.6 | 0.941 | 25.64 | 415.4 | 64.1 | 46
RV50 | 50 | 15000 | 85 | 57 | 125 | 464.5 | 0.941 | 26.98 | 437 | 64.4 | 46
RV50 | 50 | 15000 | 90 | 57 | 125 | 487.5 | 0.941 | 28.31 | 458.7 | 64.7 | 46
RV50 | 50 | 15000 | 65 | 62 | 125 | 448.5 | 0.47 | 13.02 | 211 | 65.3 | 46
RV50 | 50 | 15000 | 70 | 62 | 125 | 447.3 | 0.64 | 17.67 | 286.2 | 64.6 | 46
RV50 | 50 | 15000 | 75 | 62 | 125 | 445.3 | 0.8 | 21.98 | 356.1 | 64.3 | 46
RV50 | 50 | 15000 | 80 | 62 | 125 | 444.8 | 0.941 | 25.83 | 418.5 | 64.1 | 46
RV50 | 50 | 15000 | 85 | 62 | 125 | 468 | 0.941 | 27.18 | 440.3 | 64.4 | 46
RV50 | 50 | 15000 | 90 | 62 | 125 | 491.3 | 0.941 | 28.53 | 462.2 | 64.7 | 46
RV50 | 50 | 15000 | 70 | 67 | 125 | 491.1 | 0.433 | 13.12 | 212.5 | 65.7 | 46
RV50 | 50 | 15000 | 75 | 67 | 125 | 489.5 | 0.583 | 17.62 | 285.5 | 65.1 | 46
RV50 | 50 | 15000 | 80 | 67 | 125 | 487 | 0.724 | 21.78 | 352.8 | 64.8 | 46
RV50 | 50 | 15000 | 85 | 67 | 125 | 484.3 | 0.875 | 26.16 | 423.8 | 64.6 | 46
RV50 | 50 | 15000 | 90 | 67 | 125 | 494.9 | 0.941 | 28.74 | 465.6 | 64.7 | 46
RV50 | 50 | 15000 | 75 | 72 | 125 | 536.6 | 0.395 | 13.09 | 212 | 66.2 | 46
RV50 | 50 | 15000 | 80 | 72 | 125 | 534.6 | 0.527 | 17.38 | 281.6 | 65.6 | 46
RV50 | 50 | 15000 | 85 | 72 | 125 | 531.3 | 0.668 | 21.91 | 354.9 | 65.4 | 46
RV50 | 50 | 15000 | 90 | 72 | 125 | 528 | 0.8 | 26.06 | 422.2 | 65.2 | 46
RV50 | 50 | 15000 | 80 | 77 | 125 | 584.3 | 0.358 | 12.9 | 208.9 | 66.6 | 46
RV50 | 50 | 15000 | 85 | 77 | 125 | 580.9 | 0.489 | 17.54 | 284.2 | 66.2 | 46
RV50 | 50 | 15000 | 90 | 77 | 125 | 576.8 | 0.611 | 21.77 | 352.7 | 66 | 46
RV50 | 50 | 17500 | 65 | 57 | 75 | 546.2 | 0.668 | 19.3 | 364.8 | 43.3 | 45
RV50 | 50 | 17500 | 70 | 57 | 75 | 543.5 | 0.818 | 23.53 | 444.8 | 43.2 | 45
RV50 | 50 | 17500 | 75 | 57 | 75 | 547 | 0.941 | 27.23 | 514.6 | 43.1 | 45
RV50 | 50 | 17500 | 80 | 57 | 75 | 574.1 | 0.941 | 28.58 | 540.1 | 43 | 45
RV50 | 50 | 17500 | 85 | 57 | 75 | 601.4 | 0.941 | 29.94 | 565.8 | 42.9 | 45
RV50 | 50 | 17500 | 90 | 57 | 75 | 628.8 | 0.941 | 31.3 | 591.6 | 42.7 | 45
RV50 | 50 | 17500 | 65 | 62 | 75 | 598.2 | 0.47 | 14.89 | 281.4 | 43.5 | 45
RV50 | 50 | 17500 | 70 | 62 | 75 | 595.5 | 0.612 | 19.27 | 364.2 | 43.3 | 45
RV50 | 50 | 17500 | 75 | 62 | 75 | 592.1 | 0.753 | 23.58 | 445.7 | 43.2 | 45
RV50 | 50 | 17500 | 80 | 62 | 75 | 589.6 | 0.894 | 27.88 | 526.9 | 43.1 | 45
RV50 | 50 | 17500 | 85 | 62 | 75 | 605.8 | 0.941 | 30.15 | 569.9 | 42.9 | 45
RV50 | 50 | 17500 | 90 | 62 | 75 | 633.3 | 0.941 | 31.52 | 595.8 | 42.8 | 45
RV50 | 50 | 17500 | 70 | 67 | 75 | 652.5 | 0.423 | 14.62 | 276.3 | 43.4 | 45
RV50 | 50 | 17500 | 75 | 67 | 75 | 649.2 | 0.555 | 19.06 | 360.3 | 43.3 | 45
RV50 | 50 | 17500 | 80 | 67 | 75 | 645.1 | 0.687 | 23.44 | 443 | 43.1 | 45
RV50 | 50 | 17500 | 85 | 67 | 75 | 641.1 | 0.818 | 27.76 | 524.7 | 43 | 45
RV50 | 50 | 17500 | 90 | 67 | 75 | 638.1 | 0.941 | 31.76 | 600.3 | 42.8 | 45
RV50 | 50 | 17500 | 75 | 72 | 75 | 710.6 | 0.395 | 14.86 | 280.8 | 43.3 | 45
RV50 | 50 | 17500 | 80 | 72 | 75 | 706.2 | 0.508 | 18.98 | 358.8 | 43.1 | 45
RV50 | 50 | 17500 | 85 | 72 | 75 | 701 | 0.63 | 23.38 | 441.9 | 42.9 | 45
RV50 | 50 | 17500 | 90 | 72 | 75 | 695.7 | 0.753 | 27.7 | 523.6 | 42.8 | 45
RV50 | 50 | 17500 | 80 | 77 | 75 | 770.8 | 0.357 | 14.58 | 275.5 | 43.1 | 45
RV50 | 50 | 17500 | 85 | 77 | 75 | 764.9 | 0.47 | 19.04 | 359.8 | 42.8 | 45
RV50 | 50 | 17500 | 90 | 77 | 75 | 758.7 | 0.583 | 23.41 | 442.5 | 42.7 | 45
RV50 | 50 | 17500 | 65 | 57 | 85 | 522.6 | 0.677 | 18.73 | 354 | 47.4 | 45
RV50 | 50 | 17500 | 70 | 57 | 85 | 520.5 | 0.837 | 23.06 | 435.8 | 47.3 | 45
RV50 | 50 | 17500 | 75 | 57 | 85 | 527.6 | 0.941 | 26.26 | 496.4 | 47.2 | 45
RV50 | 50 | 17500 | 80 | 57 | 85 | 554.7 | 0.941 | 27.61 | 521.9 | 47.2 | 45
RV50 | 50 | 17500 | 85 | 57 | 85 | 582.2 | 0.941 | 28.98 | 547.7 | 47.2 | 45
RV50 | 50 | 17500 | 90 | 57 | 85 | 609.3 | 0.941 | 30.33 | 573.2 | 47.1 | 45
RV50 | 50 | 17500 | 65 | 62 | 85 | 572.8 | 0.47 | 14.25 | 269.4 | 47.7 | 45
RV50 | 50 | 17500 | 70 | 62 | 85 | 570.5 | 0.621 | 18.74 | 354.2 | 47.6 | 45
RV50 | 50 | 17500 | 75 | 62 | 85 | 567.7 | 0.771 | 23.17 | 437.9 | 47.4 | 45
RV50 | 50 | 17500 | 80 | 62 | 85 | 565.2 | 0.913 | 27.29 | 515.8 | 47.3 | 45
RV50 | 50 | 17500 | 85 | 62 | 85 | 586.4 | 0.941 | 29.19 | 551.6 | 47.2 | 45
RV50 | 50 | 17500 | 90 | 62 | 85 | 613.8 | 0.941 | 30.55 | 577.4 | 47.2 | 45
RV50 | 50 | 17500 | 70 | 67 | 85 | 625.9 | 0.433 | 14.33 | 270.9 | 47.9 | 45
RV50 | 50 | 17500 | 75 | 67 | 85 | 623.1 | 0.564 | 18.61 | 351.7 | 47.7 | 45
RV50 | 50 | 17500 | 80 | 67 | 85 | 619.4 | 0.706 | 23.13 | 437.1 | 47.5 | 45
RV50 | 50 | 17500 | 85 | 67 | 85 | 615.8 | 0.837 | 27.28 | 515.6 | 47.4 | 45
RV50 | 50 | 17500 | 90 | 67 | 85 | 618.3 | 0.941 | 30.78 | 581.7 | 47.2 | 45
RV50 | 50 | 17500 | 75 | 72 | 85 | 681.5 | 0.395 | 14.25 | 269.3 | 47.9 | 45
RV50 | 50 | 17500 | 80 | 72 | 85 | 678 | 0.517 | 18.56 | 350.8 | 47.7 | 45
RV50 | 50 | 17500 | 85 | 72 | 85 | 673.1 | 0.64 | 22.78 | 430.6 | 47.6 | 45
RV50 | 50 | 17500 | 90 | 72 | 85 | 668.4 | 0.762 | 26.95 | 509.4 | 47.4 | 45
RV50 | 50 | 17500 | 80 | 77 | 85 | 740.4 | 0.358 | 14.01 | 264.7 | 47.9 | 45
RV50 | 50 | 17500 | 85 | 77 | 85 | 735.5 | 0.47 | 18.31 | 346 | 47.7 | 45
RV50 | 50 | 17500 | 90 | 77 | 85 | 729.8 | 0.593 | 22.88 | 432.5 | 47.5 | 45
RV50 | 50 | 17500 | 65 | 57 | 95 | 497.8 | 0.687 | 18.09 | 341.9 | 51.7 | 45
RV50 | 50 | 17500 | 70 | 57 | 95 | 496 | 0.856 | 22.47 | 424.6 | 51.6 | 45
RV50 | 50 | 17500 | 75 | 57 | 95 | 507 | 0.941 | 25.23 | 476.9 | 51.6 | 45
RV50 | 50 | 17500 | 80 | 57 | 95 | 534.2 | 0.941 | 26.59 | 502.6 | 51.7 | 45
RV50 | 50 | 17500 | 85 | 57 | 95 | 560.9 | 0.941 | 27.92 | 527.7 | 51.8 | 45
RV50 | 50 | 17500 | 90 | 57 | 95 | 587.3 | 0.941 | 29.23 | 552.5 | 51.9 | 45
RV50 | 50 | 17500 | 65 | 62 | 95 | 546.1 | 0.47 | 13.59 | 256.9 | 52.2 | 45
RV50 | 50 | 17500 | 70 | 62 | 95 | 544.3 | 0.63 | 18.15 | 343.1 | 52 | 45
RV50 | 50 | 17500 | 75 | 62 | 95 | 542.1 | 0.781 | 22.4 | 423.3 | 51.9 | 45
RV50 | 50 | 17500 | 80 | 62 | 95 | 539.4 | 0.931 | 26.58 | 502.4 | 51.7 | 45
RV50 | 50 | 17500 | 85 | 62 | 95 | 564.9 | 0.941 | 28.12 | 531.5 | 51.8 | 45
RV50 | 50 | 17500 | 90 | 62 | 95 | 591.4 | 0.941 | 29.44 | 556.4 | 51.9 | 45
RV50 | 50 | 17500 | 70 | 67 | 95 | 596.8 | 0.433 | 13.67 | 258.3 | 52.5 | 45
RV50 | 50 | 17500 | 75 | 67 | 95 | 594.6 | 0.574 | 18.05 | 341.2 | 52.3 | 45
RV50 | 50 | 17500 | 80 | 67 | 95 | 591.1 | 0.715 | 22.36 | 422.6 | 52.2 | 45
RV50 | 50 | 17500 | 85 | 67 | 95 | 588.3 | 0.856 | 26.65 | 503.7 | 52 | 45
RV50 | 50 | 17500 | 90 | 67 | 95 | 595.9 | 0.941 | 29.66 | 560.6 | 51.9 | 45
RV50 | 50 | 17500 | 75 | 72 | 95 | 650.3 | 0.395 | 13.59 | 256.9 | 52.8 | 45
RV50 | 50 | 17500 | 80 | 72 | 95 | 647.4 | 0.527 | 18.05 | 341.1 | 52.5 | 45
RV50 | 50 | 17500 | 85 | 72 | 95 | 642.8 | 0.659 | 22.4 | 423.3 | 52.4 | 45
RV50 | 50 | 17500 | 90 | 72 | 95 | 638.3 | 0.781 | 26.37 | 498.4 | 52.2 | 45
RV50 | 50 | 17500 | 80 | 77 | 95 | 707 | 0.358 | 13.38 | 252.8 | 52.9 | 45
RV50 | 50 | 17500 | 85 | 77 | 95 | 702.8 | 0.48 | 17.84 | 337.2 | 52.7 | 45
RV50 | 50 | 17500 | 90 | 77 | 95 | 697.6 | 0.602 | 22.22 | 420 | 52.5 | 45
RV50 | 50 | 17500 | 65 | 57 | 105 | 472.8 | 0.696 | 17.42 | 329.2 | 56.2 | 46
RV50 | 50 | 17500 | 70 | 57 | 105 | 471.1 | 0.875 | 21.81 | 412.2 | 56 | 46
RV50 | 50 | 17500 | 75 | 57 | 105 | 486.1 | 0.941 | 24.2 | 457.3 | 56.1 | 46
RV50 | 50 | 17500 | 80 | 57 | 105 | 512.5 | 0.941 | 25.51 | 482.1 | 56.4 | 46
RV50 | 50 | 17500 | 85 | 57 | 105 | 538.6 | 0.941 | 26.81 | 506.7 | 56.5 | 46
RV50 | 50 | 17500 | 90 | 57 | 105 | 564.4 | 0.941 | 28.09 | 530.9 | 56.7 | 46
RV50 | 50 | 17500 | 65 | 62 | 105 | 518.8 | 0.47 | 12.91 | 244 | 56.8 | 46
RV50 | 50 | 17500 | 70 | 62 | 105 | 517.5 | 0.64 | 17.51 | 331 | 56.6 | 46
RV50 | 50 | 17500 | 75 | 62 | 105 | 515.2 | 0.8 | 21.8 | 412 | 56.5 | 46
RV50 | 50 | 17500 | 80 | 62 | 105 | 516 | 0.941 | 25.69 | 485.5 | 56.4 | 46
RV50 | 50 | 17500 | 85 | 62 | 105 | 542.6 | 0.941 | 27.01 | 510.4 | 56.5 | 46
RV50 | 50 | 17500 | 90 | 62 | 105 | 568.6 | 0.941 | 28.3 | 534.9 | 56.7 | 46
RV50 | 50 | 17500 | 70 | 67 | 105 | 566.9 | 0.433 | 12.98 | 245.3 | 57.3 | 46
RV50 | 50 | 17500 | 75 | 67 | 105 | 565.1 | 0.583 | 17.44 | 329.6 | 57.1 | 46
RV50 | 50 | 17500 | 80 | 67 | 105 | 562.1 | 0.734 | 21.83 | 412.5 | 56.9 | 46
RV50 | 50 | 17500 | 85 | 67 | 105 | 559.6 | 0.875 | 25.9 | 489.6 | 56.7 | 46
RV50 | 50 | 17500 | 90 | 67 | 105 | 572.9 | 0.941 | 28.52 | 539 | 56.7 | 46
RV50 | 50 | 17500 | 75 | 72 | 105 | 618 | 0.395 | 12.92 | 244.2 | 57.7 | 46
RV50 | 50 | 17500 | 80 | 72 | 105 | 615.7 | 0.536 | 17.47 | 330.2 | 57.4 | 46
RV50 | 50 | 17500 | 85 | 72 | 105 | 611.6 | 0.668 | 21.61 | 408.5 | 57.2 | 46
RV50 | 50 | 17500 | 90 | 72 | 105 | 607.7 | 0.809 | 26.01 | 491.6 | 57.1 | 46
RV50 | 50 | 17500 | 80 | 77 | 105 | 672.5 | 0.367 | 13.05 | 246.7 | 58 | 46
RV50 | 50 | 17500 | 85 | 77 | 105 | 668.9 | 0.489 | 17.31 | 327.2 | 57.7 | 46
RV50 | 50 | 17500 | 90 | 77 | 105 | 664.1 | 0.612 | 21.49 | 406.1 | 57.5 | 46
RV50 | 50 | 17500 | 65 | 57 | 115 | 445.5 | 0.715 | 16.86 | 318.6 | 61.2 | 46
RV50 | 50 | 17500 | 70 | 57 | 115 | 443.4 | 0.903 | 21.19 | 400.4 | 61 | 46
RV50 | 50 | 17500 | 75 | 57 | 115 | 462.9 | 0.941 | 23.04 | 435.5 | 61.2 | 46
RV50 | 50 | 17500 | 80 | 57 | 115 | 488.5 | 0.941 | 24.32 | 459.6 | 61.5 | 46
RV50 | 50 | 17500 | 85 | 57 | 115 | 513.9 | 0.941 | 25.58 | 483.4 | 61.8 | 46
RV50 | 50 | 17500 | 90 | 57 | 115 | 539.1 | 0.941 | 26.84 | 507.2 | 62 | 46
RV50 | 50 | 17500 | 65 | 62 | 115 | 488.5 | 0.48 | 12.4 | 234.4 | 62.1 | 46
RV50 | 50 | 17500 | 70 | 62 | 115 | 487.8 | 0.649 | 16.75 | 316.6 | 61.7 | 46
RV50 | 50 | 17500 | 75 | 62 | 115 | 486.1 | 0.818 | 21.05 | 397.8 | 61.6 | 46
RV50 | 50 | 17500 | 80 | 62 | 115 | 491.9 | 0.941 | 24.49 | 462.8 | 61.5 | 46
RV50 | 50 | 17500 | 85 | 62 | 115 | 517.6 | 0.941 | 25.76 | 486.9 | 61.8 | 46
RV50 | 50 | 17500 | 90 | 62 | 115 | 542.9 | 0.941 | 27.03 | 510.8 | 62 | 46
RV50 | 50 | 17500 | 70 | 67 | 115 | 534.2 | 0.433 | 12.23 | 231.2 | 62.6 | 46
RV50 | 50 | 17500 | 75 | 67 | 115 | 532.9 | 0.593 | 16.71 | 315.9 | 62.3 | 46
RV50 | 50 | 17500 | 80 | 67 | 115 | 530.6 | 0.753 | 21.13 | 399.3 | 62.1 | 46
RV50 | 50 | 17500 | 85 | 67 | 115 | 528 | 0.903 | 25.23 | 476.9 | 61.9 | 46
RV50 | 50 | 17500 | 90 | 67 | 115 | 547.1 | 0.941 | 27.23 | 514.7 | 62 | 46
RV50 | 50 | 17500 | 75 | 72 | 115 | 582.7 | 0.395 | 12.18 | 230.2 | 63.1 | 46
RV50 | 50 | 17500 | 80 | 72 | 115 | 580.8 | 0.546 | 16.77 | 316.9 | 62.8 | 46
RV50 | 50 | 17500 | 85 | 72 | 115 | 577.3 | 0.687 | 20.98 | 396.5 | 62.6 | 46
RV50 | 50 | 17500 | 90 | 72 | 115 | 574 | 0.828 | 25.14 | 475.2 | 62.4 | 46
RV50 | 50 | 17500 | 80 | 77 | 115 | 634.6 | 0.367 | 12.32 | 232.8 | 63.6 | 46
RV50 | 50 | 17500 | 85 | 77 | 115 | 631.6 | 0.499 | 16.66 | 314.9 | 63.3 | 46
RV50 | 50 | 17500 | 90 | 77 | 115 | 627.6 | 0.63 | 20.93 | 395.6 | 63 | 46
RV50 | 50 | 17500 | 65 | 57 | 125 | 417.4 | 0.724 | 15.99 | 302.3 | 66.9 | 47
RV50 | 50 | 17500 | 70 | 57 | 125 | 415.2 | 0.931 | 20.46 | 386.7 | 66.4 | 47
RV50 | 50 | 17500 | 75 | 57 | 125 | 438.6 | 0.941 | 21.83 | 412.6 | 66.7 | 47
RV50 | 50 | 17500 | 80 | 57 | 125 | 463.4 | 0.941 | 23.07 | 436 | 67 | 47
RV50 | 50 | 17500 | 85 | 57 | 125 | 488 | 0.941 | 24.29 | 459.1 | 67.3 | 47
RV50 | 50 | 17500 | 90 | 57 | 125 | 512.5 | 0.941 | 25.51 | 482.1 | 67.6 | 47
RV50 | 50 | 17500 | 65 | 62 | 125 | 457.7 | 0.48 | 11.62 | 219.6 | 68.3 | 47
RV50 | 50 | 17500 | 70 | 62 | 125 | 457.4 | 0.668 | 16.16 | 305.5 | 67.4 | 47
RV50 | 50 | 17500 | 75 | 62 | 125 | 455.7 | 0.847 | 20.41 | 385.8 | 66.9 | 47
RV50 | 50 | 17500 | 80 | 62 | 125 | 466.8 | 0.941 | 23.23 | 439.1 | 67 | 47
RV50 | 50 | 17500 | 85 | 62 | 125 | 491.5 | 0.941 | 24.47 | 462.4 | 67.3 | 47
RV50 | 50 | 17500 | 90 | 62 | 125 | 516.2 | 0.941 | 25.7 | 485.7 | 67.6 | 47
RV50 | 50 | 17500 | 70 | 67 | 125 | 500.6 | 0.442 | 11.71 | 221.3 | 68.5 | 47
RV50 | 50 | 17500 | 75 | 67 | 125 | 500.3 | 0.611 | 16.19 | 305.9 | 67.9 | 47
RV50 | 50 | 17500 | 80 | 67 | 125 | 497.8 | 0.772 | 20.32 | 384.1 | 67.6 | 47
RV50 | 50 | 17500 | 85 | 67 | 125 | 495.3 | 0.941 | 24.66 | 466 | 67.3 | 47
RV50 | 50 | 17500 | 90 | 67 | 125 | 520.3 | 0.941 | 25.9 | 489.5 | 67.6 | 47
RV50 | 50 | 17500 | 75 | 72 | 125 | 546.4 | 0.404 | 11.69 | 221 | 69.1 | 47
RV50 | 50 | 17500 | 80 | 72 | 125 | 545 | 0.555 | 16.01 | 302.5 | 68.4 | 47
RV50 | 50 | 17500 | 85 | 72 | 125 | 541.9 | 0.706 | 20.23 | 382.4 | 68.1 | 47
RV50 | 50 | 17500 | 90 | 72 | 125 | 539.3 | 0.856 | 24.43 | 461.7 | 67.9 | 47
RV50 | 50 | 17500 | 80 | 77 | 125 | 595.5 | 0.367 | 11.56 | 218.5 | 69.6 | 47
RV50 | 50 | 17500 | 85 | 77 | 125 | 593 | 0.508 | 15.94 | 301.3 | 69 | 47
RV50 | 50 | 17500 | 90 | 77 | 125 | 589.2 | 0.649 | 20.23 | 382.4 | 68.7 | 47
RV50 | 50 | 20000 | 65 | 57 | 75 | 557.8 | 0.687 | 17.74 | 383.1 | 48.1 | 45
RV50 | 50 | 20000 | 70 | 57 | 75 | 556.3 | 0.866 | 22.29 | 481.5 | 47.9 | 45
RV50 | 50 | 20000 | 75 | 57 | 75 | 570.3 | 0.941 | 24.84 | 536.5 | 47.8 | 45
RV50 | 50 | 20000 | 80 | 57 | 75 | 599.5 | 0.941 | 26.11 | 564 | 47.7 | 45
RV50 | 50 | 20000 | 85 | 57 | 75 | 628.8 | 0.941 | 27.39 | 591.6 | 47.6 | 45
RV50 | 50 | 20000 | 90 | 57 | 75 | 657.9 | 0.941 | 28.66 | 619 | 47.4 | 45
RV50 | 50 | 20000 | 65 | 62 | 75 | 610.8 | 0.47 | 13.3 | 287.3 | 48.3 | 45
RV50 | 50 | 20000 | 70 | 62 | 75 | 608.7 | 0.63 | 17.76 | 383.7 | 48.1 | 45
RV50 | 50 | 20000 | 75 | 62 | 75 | 605.7 | 0.79 | 22.16 | 478.7 | 47.9 | 45
RV50 | 50 | 20000 | 80 | 62 | 75 | 603.9 | 0.941 | 26.3 | 568.1 | 47.7 | 45
RV50 | 50 | 20000 | 85 | 62 | 75 | 633.2 | 0.941 | 27.58 | 595.7 | 47.6 | 45
RV50 | 50 | 20000 | 90 | 62 | 75 | 662.4 | 0.941 | 28.85 | 623.1 | 47.4 | 45
RV50 | 50 | 20000 | 70 | 67 | 75 | 665.8 | 0.433 | 13.34 | 288.1 | 48.2 | 45
RV50 | 50 | 20000 | 75 | 67 | 75 | 663.4 | 0.574 | 17.62 | 380.7 | 48 | 45
RV50 | 50 | 20000 | 80 | 67 | 75 | 659.5 | 0.724 | 22.12 | 477.8 | 47.8 | 45
RV50 | 50 | 20000 | 85 | 67 | 75 | 655.8 | 0.866 | 26.28 | 567.6 | 47.6 | 45
RV50 | 50 | 20000 | 90 | 67 | 75 | 667.2 | 0.941 | 29.06 | 627.7 | 47.4 | 45
RV50 | 50 | 20000 | 75 | 72 | 75 | 723.7 | 0.395 | 13.24 | 285.9 | 48 | 45
RV50 | 50 | 20000 | 80 | 72 | 75 | 720.1 | 0.527 | 17.56 | 379.3 | 47.8 | 45
RV50 | 50 | 20000 | 85 | 72 | 75 | 715.2 | 0.668 | 22.12 | 477.7 | 47.6 | 45
RV50 | 50 | 20000 | 90 | 72 | 75 | 710.6 | 0.8 | 26.31 | 568.2 | 47.5 | 45
RV50 | 50 | 20000 | 80 | 77 | 75 | 784.2 | 0.358 | 12.98 | 280.4 | 47.8 | 45
RV50 | 50 | 20000 | 85 | 77 | 75 | 778.8 | 0.489 | 17.64 | 381 | 47.5 | 45
RV50 | 50 | 20000 | 90 | 77 | 75 | 772.6 | 0.611 | 21.87 | 472.4 | 47.4 | 45
RV50 | 50 | 20000 | 65 | 57 | 85 | 533.4 | 0.696 | 17.19 | 371.3 | 52.2 | 45
RV50 | 50 | 20000 | 70 | 57 | 85 | 532.4 | 0.875 | 21.56 | 465.8 | 52 | 45
RV50 | 50 | 20000 | 75 | 57 | 85 | 550.1 | 0.941 | 23.96 | 517.5 | 52 | 45
RV50 | 50 | 20000 | 80 | 57 | 85 | 579 | 0.941 | 25.22 | 544.8 | 52 | 45
RV50 | 50 | 20000 | 85 | 57 | 85 | 608.4 | 0.941 | 26.5 | 572.3 | 51.9 | 45
RV50 | 50 | 20000 | 90 | 57 | 85 | 637 | 0.941 | 27.75 | 599.3 | 51.9 | 45
RV50 | 50 | 20000 | 65 | 62 | 85 | 584.6 | 0.48 | 12.99 | 280.5 | 52.5 | 45
RV50 | 50 | 20000 | 70 | 62 | 85 | 583.1 | 0.64 | 17.27 | 373 | 52.3 | 45
RV50 | 50 | 20000 | 75 | 62 | 85 | 580.5 | 0.809 | 21.75 | 469.7 | 52.2 | 45
RV50 | 50 | 20000 | 80 | 62 | 85 | 583 | 0.941 | 25.39 | 548.4 | 52 | 45
RV50 | 50 | 20000 | 85 | 62 | 85 | 612.6 | 0.941 | 26.68 | 576.3 | 52 | 45
RV50 | 50 | 20000 | 90 | 62 | 85 | 641.2 | 0.941 | 27.93 | 603.3 | 51.9 | 45
RV50 | 50 | 20000 | 70 | 67 | 85 | 638.2 | 0.433 | 12.79 | 276.2 | 52.7 | 45
RV50 | 50 | 20000 | 75 | 67 | 85 | 636.5 | 0.583 | 17.19 | 371.3 | 52.4 | 45
RV50 | 50 | 20000 | 80 | 67 | 85 | 633 | 0.734 | 21.5 | 464.5 | 52.3 | 45
RV50 | 50 | 20000 | 85 | 67 | 85 | 629.8 | 0.884 | 25.78 | 556.9 | 52.1 | 45
RV50 | 50 | 20000 | 90 | 67 | 85 | 645.9 | 0.941 | 28.13 | 607.7 | 51.9 | 45
RV50 | 50 | 20000 | 75 | 72 | 85 | 693.7 | 0.395 | 12.69 | 274.1 | 52.7 | 45
RV50 | 50 | 20000 | 80 | 72 | 85 | 690.9 | 0.536 | 17.15 | 370.5 | 52.5 | 45
RV50 | 50 | 20000 | 85 | 72 | 85 | 686.5 | 0.677 | 21.53 | 465 | 52.3 | 45
RV50 | 50 | 20000 | 90 | 72 | 85 | 682.6 | 0.809 | 25.56 | 552.2 | 52.1 | 45
RV50 | 50 | 20000 | 80 | 77 | 85 | 752.7 | 0.367 | 12.79 | 276.2 | 52.7 | 45
RV50 | 50 | 20000 | 85 | 77 | 85 | 748 | 0.489 | 16.94 | 365.9 | 52.4 | 45
RV50 | 50 | 20000 | 90 | 77 | 85 | 742.5 | 0.621 | 21.34 | 461 | 52.2 | 45
RV50 | 50 | 20000 | 65 | 57 | 95 | 507.8 | 0.715 | 16.81 | 363.1 | 56.5 | 46
RV50 | 50 | 20000 | 70 | 57 | 95 | 506.6 | 0.903 | 21.18 | 457.5 | 56.4 | 46
RV50 | 50 | 20000 | 75 | 57 | 95 | 528.3 | 0.941 | 23.01 | 497 | 56.4 | 46
RV50 | 50 | 20000 | 80 | 57 | 95 | 557.2 | 0.941 | 24.27 | 524.2 | 56.5 | 46
RV50 | 50 | 20000 | 85 | 57 | 95 | 585.6 | 0.941 | 25.5 | 550.9 | 56.6 | 46
RV50 | 50 | 20000 | 90 | 57 | 95 | 613.5 | 0.941 | 26.72 | 577.2 | 56.7 | 46
RV50 | 50 | 20000 | 65 | 62 | 95 | 556.8 | 0.48 | 12.37 | 267.2 | 57 | 46
RV50 | 50 | 20000 | 70 | 62 | 95 | 556 | 0.649 | 16.71 | 360.9 | 56.8 | 46
RV50 | 50 | 20000 | 75 | 62 | 95 | 553.7 | 0.828 | 21.22 | 458.4 | 56.7 | 46
RV50 | 50 | 20000 | 80 | 62 | 95 | 561 | 0.941 | 24.43 | 527.7 | 56.6 | 46
RV50 | 50 | 20000 | 85 | 62 | 95 | 589.7 | 0.941 | 25.69 | 554.8 | 56.6 | 46
RV50 | 50 | 20000 | 90 | 62 | 95 | 617.8 | 0.941 | 26.91 | 581.2 | 56.7 | 46
RV50 | 50 | 20000 | 70 | 67 | 95 | 608 | 0.433 | 12.18 | 263.1 | 57.4 | 46
RV50 | 50 | 20000 | 75 | 67 | 95 | 606.6 | 0.593 | 16.64 | 359.5 | 57.1 | 46
RV50 | 50 | 20000 | 80 | 67 | 95 | 603.7 | 0.753 | 21.04 | 454.4 | 56.9 | 46
RV50 | 50 | 20000 | 85 | 67 | 95 | 600.9 | 0.903 | 25.12 | 542.7 | 56.7 | 46
RV50 | 50 | 20000 | 90 | 67 | 95 | 622.4 | 0.941 | 27.11 | 585.5 | 56.7 | 46
RV50 | 50 | 20000 | 75 | 72 | 95 | 661.2 | 0.405 | 12.38 | 267.5 | 57.6 | 46
RV50 | 50 | 20000 | 80 | 72 | 95 | 658.8 | 0.546 | 16.64 | 359.5 | 57.3 | 46
RV50 | 50 | 20000 | 85 | 72 | 95 | 655 | 0.687 | 20.82 | 449.8 | 57.1 | 46
RV50 | 50 | 20000 | 90 | 72 | 95 | 651.9 | 0.837 | 25.27 | 545.8 | 56.9 | 46
RV50 | 50 | 20000 | 80 | 77 | 95 | 718.1 | 0.367 | 12.2 | 263.5 | 57.8 | 46
RV50 | 50 | 20000 | 85 | 77 | 95 | 714.6 | 0.499 | 16.5 | 356.3 | 57.4 | 46
RV50 | 50 | 20000 | 90 | 77 | 95 | 709.6 | 0.63 | 20.71 | 447.3 | 57.2 | 46
RV50 | 50 | 20000 | 65 | 57 | 105 | 482 | 0.724 | 16.17 | 349.2 | 61 | 46
RV50 | 50 | 20000 | 70 | 57 | 105 | 481.1 | 0.922 | 20.54 | 443.6 | 60.8 | 46
RV50 | 50 | 20000 | 75 | 57 | 105 | 506.1 | 0.941 | 22.04 | 476.1 | 61 | 46
RV50 | 50 | 20000 | 80 | 57 | 105 | 534 | 0.941 | 23.26 | 502.4 | 61.3 | 46
RV50 | 50 | 20000 | 85 | 57 | 105 | 561.7 | 0.941 | 24.47 | 528.5 | 61.4 | 46
RV50 | 50 | 20000 | 90 | 57 | 105 | 589.1 | 0.941 | 25.66 | 554.2 | 61.5 | 46
RV50 | 50 | 20000 | 65 | 62 | 105 | 528.2 | 0.48 | 11.73 | 253.4 | 61.7 | 46
RV50 | 50 | 20000 | 70 | 62 | 105 | 527.7 | 0.668 | 16.32 | 352.5 | 61.5 | 46
RV50 | 50 | 20000 | 75 | 62 | 105 | 526.1 | 0.847 | 20.62 | 445.5 | 61.3 | 46
RV50 | 50 | 20000 | 80 | 62 | 105 | 537.7 | 0.941 | 23.42 | 505.9 | 61.3 | 46
RV50 | 50 | 20000 | 85 | 62 | 105 | 565.8 | 0.941 | 24.64 | 532.3 | 61.4 | 46
RV50 | 50 | 20000 | 90 | 62 | 105 | 593.2 | 0.941 | 25.84 | 558.1 | 61.5 | 46
RV50 | 50 | 20000 | 70 | 67 | 105 | 577.1 | 0.442 | 11.81 | 255.2 | 62.2 | 46
RV50 | 50 | 20000 | 75 | 67 | 105 | 576.1 | 0.612 | 16.31 | 352.3 | 61.9 | 46
RV50 | 50 | 20000 | 80 | 67 | 105 | 573.7 | 0.771 | 20.49 | 442.6 | 61.7 | 46
RV50 | 50 | 20000 | 85 | 67 | 105 | 571.1 | 0.931 | 24.62 | 531.9 | 61.5 | 46
RV50 | 50 | 20000 | 90 | 67 | 105 | 597.7 | 0.941 | 26.03 | 562.3 | 61.6 | 46
RV50 | 50 | 20000 | 75 | 72 | 105 | 627.7 | 0.404 | 11.75 | 253.9 | 62.6 | 46
RV50 | 50 | 20000 | 80 | 72 | 105 | 626.1 | 0.555 | 16.09 | 347.5 | 62.2 | 46
RV50 | 50 | 20000 | 85 | 72 | 105 | 622.9 | 0.706 | 20.35 | 439.5 | 62 | 46
RV50 | 50 | 20000 | 90 | 72 | 105 | 620.2 | 0.856 | 24.58 | 531 | 61.8 | 46
RV50 | 50 | 20000 | 80 | 77 | 105 | 682.3 | 0.367 | 11.59 | 250.3 | 62.9 | 46
RV50 | 50 | 20000 | 85 | 77 | 105 | 679.4 | 0.508 | 15.98 | 345.1 | 62.5 | 46
RV50 | 50 | 20000 | 90 | 77 | 105 | 675 | 0.649 | 20.29 | 438.2 | 62.3 | 46
RV50 | 50 | 20000 | 65 | 57 | 115 | 453.8 | 0.743 | 15.62 | 337.3 | 66.1 | 46
RV50 | 50 | 20000 | 70 | 57 | 115 | 454.4 | 0.941 | 19.79 | 427.5 | 65.9 | 46
RV50 | 50 | 20000 | 75 | 57 | 115 | 481.3 | 0.941 | 20.96 | 452.8 | 66.2 | 46
RV50 | 50 | 20000 | 80 | 57 | 115 | 508.4 | 0.941 | 22.14 | 478.3 | 66.5 | 46
RV50 | 50 | 20000 | 85 | 57 | 115 | 535.3 | 0.941 | 23.31 | 503.6 | 66.7 | 46
RV50 | 50 | 20000 | 90 | 57 | 115 | 562.2 | 0.941 | 24.49 | 528.9 | 66.9 | 46
RV50 | 50 | 20000 | 65 | 62 | 115 | 496.9 | 0.489 | 11.25 | 243.1 | 67.1 | 46
RV50 | 50 | 20000 | 70 | 62 | 115 | 497 | 0.677 | 15.59 | 336.7 | 66.6 | 46
RV50 | 50 | 20000 | 75 | 62 | 115 | 495.9 | 0.865 | 19.87 | 429.2 | 66.4 | 46
RV50 | 50 | 20000 | 80 | 62 | 115 | 512.2 | 0.941 | 22.31 | 481.8 | 66.5 | 46
RV50 | 50 | 20000 | 85 | 62 | 115 | 539.2 | 0.941 | 23.49 | 507.3 | 66.7 | 46
RV50 | 50 | 20000 | 90 | 62 | 115 | 566.2 | 0.941 | 24.66 | 532.6 | 67 | 46
RV50 | 50 | 20000 | 70 | 67 | 115 | 543.2 | 0.442 | 11.12 | 240.2 | 67.6 | 46
RV50 | 50 | 20000 | 75 | 67 | 115 | 543 | 0.621 | 15.61 | 337.2 | 67.2 | 46
RV50 | 50 | 20000 | 80 | 67 | 115 | 540.7 | 0.79 | 19.78 | 427.3 | 66.9 | 46
RV50 | 50 | 20000 | 85 | 67 | 115 | 543.1 | 0.941 | 23.65 | 510.9 | 66.8 | 46
RV50 | 50 | 20000 | 90 | 67 | 115 | 570.5 | 0.941 | 24.85 | 536.7 | 67 | 46
RV50 | 50 | 20000 | 75 | 72 | 115 | 591.2 | 0.405 | 11.07 | 239.2 | 68 | 46
RV50 | 50 | 20000 | 80 | 72 | 115 | 590.5 | 0.564 | 15.43 | 333.3 | 67.6 | 46
RV50 | 50 | 20000 | 85 | 72 | 115 | 587.7 | 0.724 | 19.71 | 425.7 | 67.4 | 46
RV50 | 50 | 20000 | 90 | 72 | 115 | 585.3 | 0.884 | 23.96 | 517.6 | 67.1 | 46
RV50 | 50 | 20000 | 80 | 77 | 115 | 643.1 | 0.376 | 11.2 | 242 | 68.5 | 46
RV50 | 50 | 20000 | 85 | 77 | 115 | 641.1 | 0.517 | 15.36 | 331.7 | 68.1 | 46
RV50 | 50 | 20000 | 90 | 77 | 115 | 637.3 | 0.668 | 19.71 | 425.7 | 67.8 | 46
RV50 | 50 | 20000 | 65 | 57 | 125 | 424.8 | 0.762 | 14.99 | 323.7 | 71.8 | 47
RV50 | 50 | 20000 | 70 | 57 | 125 | 429.4 | 0.941 | 18.7 | 403.9 | 71.4 | 47
RV50 | 50 | 20000 | 75 | 57 | 125 | 455.5 | 0.941 | 19.84 | 428.5 | 71.6 | 47
RV50 | 50 | 20000 | 80 | 57 | 125 | 481.8 | 0.941 | 20.98 | 453.2 | 72 | 47
RV50 | 50 | 20000 | 85 | 57 | 125 | 507.9 | 0.941 | 22.12 | 477.8 | 72.3 | 47
RV50 | 50 | 20000 | 90 | 57 | 125 | 533.9 | 0.941 | 23.25 | 502.3 | 72.6 | 47
RV50 | 50 | 20000 | 65 | 62 | 125 | 464.6 | 0.489 | 10.52 | 227.3 | 73.4 | 47
RV50 | 50 | 20000 | 70 | 62 | 125 | 465.3 | 0.696 | 15 | 323.9 | 72.2 | 47
RV50 | 50 | 20000 | 75 | 62 | 125 | 464.4 | 0.894 | 19.21 | 415 | 71.8 | 47
RV50 | 50 | 20000 | 80 | 62 | 125 | 485 | 0.941 | 21.12 | 456.3 | 72 | 47
RV50 | 50 | 20000 | 85 | 62 | 125 | 511.6 | 0.941 | 22.28 | 481.3 | 72.3 | 47
RV50 | 50 | 20000 | 90 | 62 | 125 | 537.7 | 0.941 | 23.42 | 505.9 | 72.6 | 47
RV50 | 50 | 20000 | 70 | 67 | 125 | 508.5 | 0.452 | 10.63 | 229.6 | 73.8 | 47
RV50 | 50 | 20000 | 75 | 67 | 125 | 509 | 0.64 | 15.07 | 325.6 | 72.8 | 47
RV50 | 50 | 20000 | 80 | 67 | 125 | 507 | 0.819 | 19.21 | 415 | 72.4 | 47
RV50 | 50 | 20000 | 85 | 67 | 125 | 515.3 | 0.941 | 22.44 | 484.8 | 72.3 | 47
RV50 | 50 | 20000 | 90 | 67 | 125 | 541.6 | 0.941 | 23.59 | 509.6 | 72.6 | 47
RV50 | 50 | 20000 | 75 | 72 | 125 | 554 | 0.414 | 10.62 | 229.3 | 74.1 | 47
RV50 | 50 | 20000 | 80 | 72 | 125 | 554.1 | 0.583 | 14.96 | 323.2 | 73.3 | 47
RV50 | 50 | 20000 | 85 | 72 | 125 | 551.8 | 0.753 | 19.23 | 415.3 | 73 | 47
RV50 | 50 | 20000 | 90 | 72 | 125 | 549.3 | 0.922 | 23.44 | 506.4 | 72.7 | 47
RV50 | 50 | 20000 | 80 | 77 | 125 | 603.1 | 0.376 | 10.5 | 226.9 | 74.5 | 47
RV50 | 50 | 20000 | 85 | 77 | 125 | 601.7 | 0.536 | 14.94 | 322.7 | 73.8 | 47
RV50 | 50 | 20000 | 90 | 77 | 125 | 598.2 | 0.696 | 19.28 | 416.4 | 73.5 | 47

## Gas Heating
Model | Tons | Phase | Gas Heat | Input - High Stage (MBH) | Output - High Stage (MBH) | Input - Low Stage (MBH) | Output - Low Stage (MBH) | Temp Rise - High Stage (°F) | Temp Rise - Low Stage (°F) | Thermal Efficiency (%) | Heat Code | Low Stage Basis | Source Page
KJ037 | 3 | 3-Phase | Low | 60 | 49 | 45 | 36.8 | 20-50 |  | 81 | N06 | 75% of full fire (catalog footnote); low-stage values derived | 20
KJ037 | 3 | 3-Phase | High | 80 | 65 | 56 | 45.5 | 25-65 |  | 81 | N08 | 70% of full fire (catalog footnote); low-stage values derived | 20
KJ049 | 4 | 3-Phase | Low | 60 | 49 | 45 | 36.8 | 20-50 |  | 81 | N06 | 75% of full fire (catalog footnote); low-stage values derived | 20
KJ049 | 4 | 3-Phase | Medium | 80 | 65 | 56 | 45.5 | 25-65 |  | 81 | N08 | 70% of full fire (catalog footnote); low-stage values derived | 20
KJ049 | 4 | 3-Phase | High | 120 | 97 | 84 | 67.9 | 35-70 |  | 81 | N12 | 70% of full fire (catalog footnote); low-stage values derived | 20
KJ061 | 5 | 3-Phase | Low | 80 | 65 | 56 | 45.5 | 25-65 |  | 81 | N08 | 70% of full fire (catalog footnote); low-stage values derived | 20
KJ061 | 5 | 3-Phase | Medium | 120 | 97 | 84 | 67.9 | 35-70 |  | 81 | N12 | 70% of full fire (catalog footnote); low-stage values derived | 20
KJ061 | 5 | 3-Phase | High | 160 | 130 | 112 | 91 | 45-75 |  | 81 | N16 | 70% of full fire (catalog footnote); low-stage values derived | 20
KJ078 | 6.5 | 3-Phase | Low | 120 | 97 | 72 | 58.2 | 20-50 |  | 81 | N12 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ078 | 6.5 | 3-Phase | High | 180 | 146 | 108 | 87.6 | 20-65 |  | 81 | N18 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ090 | 7.5 | 3-Phase | Low | 120 | 97 | 72 | 58.2 | 20-50 |  | 81 | N12 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ090 | 7.5 | 3-Phase | High | 180 | 146 | 108 | 87.6 | 20-65 |  | 81 | N18 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ102 | 8.5 | 3-Phase | Low | 120 | 97 | 72 | 58.2 | 20-50 |  | 81 | N12 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ102 | 8.5 | 3-Phase | High | 180 | 146 | 108 | 87.6 | 20-65 |  | 81 | N18 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ120 | 10 | 3-Phase | Low | 180 | 146 | 108 | 87.6 | 20-65 |  | 81 | N18 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ120 | 10 | 3-Phase | High | 240 | 194 | 144 | 116.4 | 30-60 |  | 81 | N24 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ150 | 12.5 | 3-Phase | Low | 180 | 146 | 108 | 87.6 | 20-65 |  | 81 | N18 | 60% of full fire (catalog footnote); low-stage values derived | 22
KJ150 | 12.5 | 3-Phase | High | 240 | 194 | 144 | 116.4 | 30-60 |  | 81 | N24 | 60% of full fire (catalog footnote); low-stage values derived | 22
LV15 | 15 | 3-Phase | Low | 220 | 178 | 165 | 134 | 15-45 |  | 81 | N(S)1 | Both stages published | 25
LV15 | 15 | 3-Phase | High | 400 | 324 | 300 | 243 | 35-65 |  | 81 | N(S)3 | Both stages published | 25
LV18 | 17.5 | 3-Phase | Low | 220 | 178 | 165 | 134 | 15-45 |  | 81 | N(S)1 | Both stages published | 25
LV18 | 17.5 | 3-Phase | High | 400 | 324 | 300 | 243 | 30-65 |  | 81 | N(S)3 | Both stages published | 25
LV20 | 20 | 3-Phase | Low | 220 | 178 | 165 | 134 | 15-45 |  | 81 | N(S)1 | Both stages published | 27
LV20 | 20 | 3-Phase | High | 400 | 324 | 300 | 243 | 30-65 |  | 81 | N(S)3 | Both stages published | 27
LV25 | 25 | 3-Phase | Low | 220 | 178 | 165 | 134 | 10-40 |  | 81 | N(S)1 | Both stages published | 27
LV25 | 25 | 3-Phase | High | 400 | 324 | 300 | 243 | 20-55 |  | 81 | N(S)3 | Both stages published | 27
LV28 | 27.5 | 3-Phase | Low | 220 | 178 | 165 | 134 | 10-40 |  | 81 | N(S)1 | Both stages published | 27
LV28 | 27.5 | 3-Phase | High | 400 | 324 | 300 | 243 | 20-55 |  | 81 | N(S)3 | Both stages published | 27
RV27 | 27.5 | 3-Phase | Low | 400 | 324 | 320 | 259 | 25-35 |  | 81 | N(S)1 | Both stages published | 21
RV27 | 27.5 | 3-Phase | High | 620 | 502 | 400 | 324 | 35-60 |  | 81 | N(S)3 | Both stages published | 21
RV30 | 30 | 3-Phase | Low | 400 | 324 | 320 | 259 | 20-35 |  | 81 | N(S)1 | Both stages published | 21
RV30 | 30 | 3-Phase | High | 620 | 502 | 400 | 324 | 35-55 |  | 81 | N(S)3 | Both stages published | 21
RV35 | 35 | 3-Phase | Low | 400 | 324 | 320 | 259 | 20-30 |  | 81 | N(S)1 | Both stages published | 23
RV35 | 35 | 3-Phase | High | 800 | 648 | 400 | 324 | 35-60 |  | 81 | N(S)3 | Both stages published | 23
RV40 | 40 | 3-Phase | Low | 400 | 324 | 320 | 259 | 15-25 |  | 81 | N(S)1 | Both stages published | 23
RV40 | 40 | 3-Phase | High | 800 | 648 | 400 | 324 | 35-50 |  | 81 | N(S)3 | Both stages published | 23
RV50 | 50 | 3-Phase | Low | 400 | 324 | 320 | 259 | 15-20 |  | 81 | N(S)1 | Both stages published | 25
RV50 | 50 | 3-Phase | High | 800 | 648 | 400 | 324 | 30-40 |  | 81 | N(S)3 | Both stages published | 25

## Electrical Data
Model | Tons | Motor | Power Supply | MCA - Base Unit | MOP - Base Unit | Conv. Outlet FLA | MCA - w/ Conv. Outlet | MOP - w/ Conv. Outlet | Power Exhaust FLA | MCA - w/ Power Exhaust | MOP - w/ Power Exhaust | MCA - w/ Conv. Outlet + Pwr Exhaust | MOP - w/ Conv. Outlet + Pwr Exhaust | Indoor Motor HP | MCA - w/ Modulating Pwr Exhaust (LV) | MOP - w/ Modulating Pwr Exhaust (LV)
KJ037 | 3 | B - Standard Static | 208/230/3/60 | 22.7/22.7 | 30/30 | 20/20 | 32.7/32.7 | 45/45 | 5.5/5.5 | 28.2/28.2 | 40/40 | 38.2/38.2 | 50/50 | 1-1/2
KJ037 | 3 | B - Standard Static | 460/3/60 | 10 | 15 | 20 | 15 | 20 | 2.2 | 12.2 | 15 | 17.2 | 20 | 1-1/2
KJ037 | 3 | B - Standard Static | 575/3/60 | 8.3 | 15 | 20 | 12.3 | 15 | 1.8 | 10.1 | 15 | 14.1 | 15 | 1-1/2
KJ037 | 3 | D - High Static | 208/230/3/60 | 22.7/22.7 | 30/30 | 20/20 | 32.7/32.7 | 45/45 | 5.5/5.5 | 28.2/28.2 | 40/40 | 38.2/38.2 | 50/50 | 1-1/2
KJ037 | 3 | D - High Static | 460/3/60 | 10 | 15 | 20 | 15 | 20 | 2.2 | 12.2 | 15 | 17.2 | 20 | 1-1/2
KJ037 | 3 | D - High Static | 575/3/60 | 8.3 | 15 | 20 | 12.3 | 15 | 1.8 | 10.1 | 15 | 14.1 | 15 | 1-1/2
KJ049 | 4 | B - Standard Static | 208/230/3/60 | 22/22 | 30/30 | 20/20 | 32/32 | 40/40 | 5.5/5.5 | 27.5/27.5 | 35/35 | 37.5/37.5 | 45/45 | 1-1/2
KJ049 | 4 | B - Standard Static | 460/3/60 | 11.6 | 15 | 20 | 16.6 | 20 | 2.2 | 13.8 | 20 | 18.8 | 25 | 1-1/2
KJ049 | 4 | B - Standard Static | 575/3/60 | 9.1 | 15 | 20 | 13.1 | 15 | 1.8 | 10.9 | 15 | 14.9 | 20 | 1-1/2
KJ049 | 4 | D - High Static | 208/230/3/60 | 22/22 | 30/30 | 20/20 | 32/32 | 40/40 | 5.5/5.5 | 27.5/27.5 | 35/35 | 37.5/37.5 | 45/45 | 1-1/2
KJ049 | 4 | D - High Static | 460/3/60 | 11.6 | 15 | 20 | 16.6 | 20 | 2.2 | 13.8 | 20 | 18.8 | 25 | 1-1/2
KJ049 | 4 | D - High Static | 575/3/60 | 9.1 | 15 | 20 | 13.1 | 15 | 1.8 | 10.9 | 15 | 14.9 | 20 | 1-1/2
KJ061 | 5 | B - Standard Static | 208/230/3/60 | 28.3/28.3 | 40/40 | 20/20 | 38.3/38.3 | 50/50 | 5.5/5.5 | 33.8/33.8 | 45/45 | 43.8/43.8 | 50/50 | 1-1/2
KJ061 | 5 | B - Standard Static | 460/3/60 | 14.3 | 20 | 20 | 19.3 | 25 | 2.2 | 16.5 | 20 | 21.5 | 25 | 1-1/2
KJ061 | 5 | B - Standard Static | 575/3/60 | 11.3 | 15 | 20 | 15.3 | 20 | 1.8 | 13.1 | 15 | 17.1 | 20 | 1-1/2
KJ061 | 5 | D - High Static | 208/230/3/60 | 29.6/29.6 | 40/40 | 20/20 | 39.6/39.6 | 50/50 | 5.5/5.5 | 35.1/35.1 | 45/45 | 45.1/45.1 | 60/60 | 2
KJ061 | 5 | D - High Static | 460/3/60 | 15 | 20 | 20 | 20 | 25 | 2.2 | 17.2 | 20 | 22.2 | 25 | 2
KJ061 | 5 | D - High Static | 575/3/60 | 11.7 | 15 | 20 | 15.7 | 20 | 1.8 | 13.5 | 15 | 17.5 | 20 | 2
KJ078 | 6.5 | B - Standard Static | 208/230/3/60 | 32.6/32.6 | 40/40 | 20/20 | 42.8/42.8 | 50/50 | 5.5/5.5 | 38.1/38.1 | 45/45 | 48.3/48.3 | 50/50 | 1-1/2
KJ078 | 6.5 | B - Standard Static | 460/3/60 | 17.6 | 20 | 20 | 22.7 | 25 | 2.2 | 19.8 | 20 | 24.9 | 25 | 1-1/2
KJ078 | 6.5 | B - Standard Static | 575/3/60 | 12.7 | 15 | 20 | 16.8 | 20 | 1.8 | 14.5 | 15 | 18.6 | 20 | 1-1/2
KJ078 | 6.5 | D - High Static | 208/230/3/60 | 32.6/32.6 | 40/40 | 20/20 | 42.8/42.8 | 50/50 | 5.5/5.5 | 38.1/38.1 | 45/45 | 48.3/48.3 | 50/50 | 2
KJ078 | 6.5 | D - High Static | 460/3/60 | 17.6 | 20 | 20 | 22.7 | 25 | 2.2 | 19.8 | 20 | 24.9 | 25 | 2
KJ078 | 6.5 | D - High Static | 575/3/60 | 12.7 | 15 | 20 | 16.8 | 20 | 1.8 | 14.5 | 15 | 18.6 | 20 | 2
KJ090 | 7.5 | B - Standard Static | 208/230/3/60 | 43.4/43.4 | 50/50 | 20/20 | 53.4/53.4 | 60/60 | 5.5/5.5 | 48.9/48.9 | 60/60 | 58.9/58.9 | 70/70 | 1-1/2
KJ090 | 7.5 | B - Standard Static | 460/3/60 | 20.9 | 25 | 20 | 25.9 | 30 | 2.2 | 23.1 | 25 | 28.1 | 30 | 1-1/2
KJ090 | 7.5 | B - Standard Static | 575/3/60 | 17.4 | 20 | 20 | 21.4 | 25 | 1.8 | 19.2 | 20 | 23.2 | 25 | 1-1/2
KJ090 | 7.5 | D - High Static | 208/230/3/60 | 47.7/47.7 | 60/60 | 20/20 | 57.7/57.7 | 70/70 | 5.5/5.5 | 53.2/53.2 | 60/60 | 63.2/63.2 | 70/70 | 3
KJ090 | 7.5 | D - High Static | 460/3/60 | 22.4 | 25 | 20 | 27.4 | 30 | 2.2 | 24.6 | 30 | 29.6 | 35 | 3
KJ090 | 7.5 | D - High Static | 575/3/60 | 18.8 | 20 | 20 | 22.8 | 25 | 1.8 | 20.6 | 25 | 24.6 | 25 | 3
KJ102 | 8.5 | B - Standard Static | 208/230/3/60 | 41.6/41.6 | 50/50 | 20/20 | 51.6/51.6 | 60/60 | 5.5/5.5 | 47.1/47.1 | 50/50 | 57.1/57.1 | 60/60 | 2
KJ102 | 8.5 | B - Standard Static | 460/3/60 | 22 | 25 | 20 | 27 | 30 | 2.2 | 24.2 | 30 | 29.2 | 35 | 2
KJ102 | 8.5 | B - Standard Static | 575/3/60 | 15.8 | 20 | 20 | 19.8 | 20 | 1.8 | 17.6 | 20 | 21.6 | 25 | 2
KJ102 | 8.5 | D - High Static | 208/230/3/60 | 46.1/46.1 | 50/50 | 20/20 | 56.1/56.1 | 60/60 | 5.5/5.5 | 51.6/51.6 | 60/60 | 61.6/61.6 | 70/70 | 3
KJ102 | 8.5 | D - High Static | 460/3/60 | 23.5 | 25 | 20 | 28.5 | 30 | 2.2 | 25.7 | 30 | 30.7 | 35 | 3
KJ102 | 8.5 | D - High Static | 575/3/60 | 17.3 | 20 | 20 | 21.3 | 25 | 1.8 | 19.1 | 20 | 23.1 | 25 | 3
KJ120 | 10 | B - Standard Static | 208/230/3/60 | 50.6/50.6 | 60/60 | 20/20 | 60.6/60.6 | 70/70 | 5.5/5.5 | 56.1/56.1 | 70/70 | 66.1/66.1 | 80/80 | 2
KJ120 | 10 | B - Standard Static | 460/3/60 | 23.8 | 30 | 20 | 28.8 | 35 | 2.2 | 26 | 30 | 31 | 35 | 2
KJ120 | 10 | B - Standard Static | 575/3/60 | 20.3 | 25 | 20 | 24.3 | 30 | 1.8 | 22.1 | 25 | 26.1 | 30 | 2
KJ120 | 10 | D - High Static | 208/230/3/60 | 54.8/54.8 | 70/70 | 20/20 | 64.8/64.8 | 80/80 | 5.5/5.5 | 60.3/60.3 | 70/70 | 70.3/70.3 | 80/80 | 3
KJ120 | 10 | D - High Static | 460/3/60 | 25.3 | 30 | 20 | 30.3 | 35 | 2.2 | 27.5 | 30 | 32.5 | 35 | 3
KJ120 | 10 | D - High Static | 575/3/60 | 21.7 | 25 | 20 | 25.7 | 30 | 1.8 | 23.5 | 25 | 27.5 | 30 | 3
KJ150 | 12.5 | B - Standard Static | 208/230/3/60 | 70.2/70.2 | 90/90 | 20/20 | 80.2/80.2 | 100/100 | 5.5/5.5 | 75.7/75.7 | 90/90 | 85.7/85.7 | 100/100 | 3
KJ150 | 12.5 | B - Standard Static | 460/3/60 | 30.3 | 35 | 20 | 35.3 | 40 | 2.2 | 32.5 | 40 | 37.5 | 45 | 3
KJ150 | 12.5 | B - Standard Static | 575/3/60 | 23.7 | 30 | 20 | 27.7 | 30 | 1.8 | 25.5 | 30 | 29.5 | 35 | 3
KJ150 | 12.5 | D - High Static | 208/230/3/60 | 77.4/77.4 | 90/90 | 20/20 | 87.4/87.4 | 100/100 | 5.5/5.5 | 82.9/82.9 | 100/100 | 92.9/92.9 | 110/110 | 5
KJ150 | 12.5 | D - High Static | 460/3/60 | 34.4 | 40 | 20 | 39.4 | 45 | 2.2 | 36.6 | 45 | 41.6 | 50 | 5
KJ150 | 12.5 | D - High Static | 575/3/60 | 26.6 | 30 | 20 | 30.6 | 35 | 1.8 | 28.4 | 35 | 32.4 | 40 | 5
LV15 | 15 | B - Standard Static | 208/230/3/60 | 73.7/73.7 | 90/90 | 9.6/8.7 | 83.3/82.4 | 100/100 | 5.0/5.0 | 83.7/83.7 | 100/100 | 93.3/92.4 | 110/110 | 2 | 87.1/87.1 | 110/110
LV15 | 15 | B - Standard Static | 460/3/60 | 35.8 | 45 | 4.3 | 40.1 | 50 | 2.2 | 40.2 | 50 | 44.5 | 50 | 2 | 42.6 | 50
LV15 | 15 | B - Standard Static | 575/3/60 | 27.6 | 35 | 3.5 | 31.1 | 40 | 1.5 | 30.6 | 35 | 34.1 | 40 | 2 | 33 | 40
LV15 | 15 | C - Medium Static | 208/230/3/60 | 73.7/73.7 | 90/90 | 9.6/8.7 | 83.3/82.4 | 100/100 | 5.0/5.0 | 83.7/83.7 | 100/100 | 93.3/92.4 | 110/110 | 3 | 87.1/87.1 | 110/110
LV15 | 15 | C - Medium Static | 460/3/60 | 35.8 | 45 | 4.3 | 40.1 | 50 | 2.2 | 40.2 | 50 | 44.5 | 50 | 3 | 42.6 | 50
LV15 | 15 | C - Medium Static | 575/3/60 | 27.6 | 35 | 3.5 | 31.1 | 40 | 1.5 | 30.6 | 35 | 34.1 | 40 | 3 | 33 | 40
LV15 | 15 | D - High Static | 208/230/3/60 | 80.9/80.9 | 100/100 | 9.6/8.7 | 90.5/89.6 | 110/110 | 5.0/5.0 | 90.9/90.9 | 110/110 | 100.5/99.6 | 125/110 | 5 | 94.3/94.3 | 110/110
LV15 | 15 | D - High Static | 460/3/60 | 39.6 | 50 | 4.3 | 43.9 | 50 | 2.2 | 44 | 50 | 48.3 | 60 | 5 | 46.4 | 50
LV15 | 15 | D - High Static | 575/3/60 | 30.4 | 35 | 3.5 | 33.9 | 40 | 1.5 | 33.4 | 40 | 36.9 | 45 | 5 | 35.8 | 45
LV18 | 17.5 | B - Standard Static | 208/230/3/60 | 85.9/85.9 | 110/110 | 9.6/8.7 | 95.5/94.6 | 125/125 | 5.0/5.0 | 95.9/95.9 | 125/125 | 105.5/104.6 | 125/125 | 3 | 99.3/99.3 | 125/125
LV18 | 17.5 | B - Standard Static | 460/3/60 | 42.4 | 50 | 4.3 | 46.7 | 60 | 2.2 | 46.8 | 60 | 51.1 | 60 | 3 | 49.2 | 60
LV18 | 17.5 | B - Standard Static | 575/3/60 | 35.8 | 45 | 3.5 | 39.3 | 50 | 1.5 | 38.8 | 50 | 42.3 | 50 | 3 | 41.2 | 50
LV18 | 17.5 | C - Medium Static | 208/230/3/60 | 93.1/93.1 | 125/125 | 9.6/8.7 | 102.7/101.8 | 125/125 | 5.0/5.0 | 103.1/103.1 | 125/125 | 112.7/111.8 | 125/125 | 5 | 106.5/106.5 | 125/125
LV18 | 17.5 | C - Medium Static | 460/3/60 | 46.2 | 60 | 4.3 | 50.5 | 60 | 2.2 | 50.6 | 60 | 54.9 | 70 | 5 | 53 | 60
LV18 | 17.5 | C - Medium Static | 575/3/60 | 38.6 | 50 | 3.5 | 42.1 | 50 | 1.5 | 41.6 | 50 | 45.1 | 50 | 5 | 44 | 50
LV18 | 17.5 | D - High Static | 208/230/3/60 | 102.7/102.7 | 125/125 | 9.6/8.7 | 112.3/111.4 | 125/125 | 5.0/5.0 | 112.7/112.7 | 125/125 | 122.3/121.4 | 150/150 | 7.5 | 116.1/116.1 | 125/125
LV18 | 17.5 | D - High Static | 460/3/60 | 50.6 | 60 | 4.3 | 54.9 | 70 | 2.2 | 55 | 70 | 59.3 | 70 | 7.5 | 57.4 | 70
LV18 | 17.5 | D - High Static | 575/3/60 | 42.4 | 50 | 3.5 | 45.9 | 60 | 1.5 | 45.4 | 50 | 48.9 | 60 | 7.5 | 47.8 | 60
LV20 | 20 | B - Standard Static | 208/230/3/60 | 110.0/111.2 | 125/150 | 9.6/8.7 | 119.6/119.9 | 150/150 | 5.0/5.0 | 120.0/121.2 | 150/150 | 129.6/129.9 | 150/150 | 5 | 123.4/124.6 | 150/150
LV20 | 20 | B - Standard Static | 460/3/60 | 54.4 | 70 | 4.3 | 58.7 | 70 | 2.2 | 58.8 | 70 | 63.1 | 80 | 5 | 61.2 | 70
LV20 | 20 | B - Standard Static | 575/3/60 | 45.1 | 60 | 3.5 | 48.6 | 60 | 1.5 | 48.1 | 60 | 51.6 | 60 | 5 | 50.5 | 60
LV20 | 20 | C - Medium Static | 208/230/3/60 | 110.0/111.2 | 125/150 | 9.6/8.7 | 119.6/119.9 | 150/150 | 5.0/5.0 | 120.0/121.2 | 150/150 | 129.6/129.9 | 150/150 | 5 | 123.4/124.6 | 150/150
LV20 | 20 | C - Medium Static | 460/3/60 | 54.4 | 70 | 4.3 | 58.7 | 70 | 2.2 | 58.8 | 70 | 63.1 | 80 | 5 | 61.2 | 70
LV20 | 20 | C - Medium Static | 575/3/60 | 45.1 | 60 | 3.5 | 48.6 | 60 | 1.5 | 48.1 | 60 | 51.6 | 60 | 5 | 50.5 | 60
LV20 | 20 | D - High Static | 208/230/3/60 | 119.6/120.8 | 150/150 | 9.6/8.7 | 129.2/129.5 | 150/150 | 5.0/5.0 | 129.6/130.8 | 150/150 | 139.2/139.5 | 175/175 | 7.5 | 133.0/134.2 | 150/150
LV20 | 20 | D - High Static | 460/3/60 | 58.8 | 70 | 4.3 | 63.1 | 80 | 2.2 | 63.2 | 80 | 67.5 | 80 | 7.5 | 65.6 | 80
LV20 | 20 | D - High Static | 575/3/60 | 48.9 | 60 | 3.5 | 52.4 | 60 | 1.5 | 51.9 | 60 | 55.4 | 70 | 7.5 | 54.3 | 60
LV25 | 25 | B - Standard Static | 208/230/3/60 | 120.7/121.9 | 150/150 | 9.6/8.7 | 130.3/130.6 | 150/150 | 5.0/5.0 | 130.7/131.9 | 150/150 | 140.3/140.6 | 175/175 | 5 | 134.1/135.3 | 175/175
LV25 | 25 | B - Standard Static | 460/3/60 | 58.3 | 70 | 4.3 | 62.6 | 80 | 2.2 | 62.7 | 80 | 67 | 80 | 5 | 65.1 | 80
LV25 | 25 | B - Standard Static | 575/3/60 | 49.3 | 60 | 3.5 | 52.8 | 60 | 1.5 | 52.3 | 60 | 55.8 | 70 | 5 | 54.7 | 70
LV25 | 25 | C - Medium Static | 208/230/3/60 | 130.3/131.5 | 150/150 | 9.6/8.7 | 139.9/140.2 | 175/175 | 5.0/5.0 | 140.3/141.5 | 175/175 | 149.9/150.2 | 175/175 | 7.5 | 143.7/144.9 | 175/175
LV25 | 25 | C - Medium Static | 460/3/60 | 62.7 | 80 | 4.3 | 67 | 80 | 2.2 | 67.1 | 80 | 71.4 | 90 | 7.5 | 69.5 | 80
LV25 | 25 | C - Medium Static | 575/3/60 | 53.1 | 60 | 3.5 | 56.6 | 70 | 1.5 | 56.1 | 70 | 59.6 | 70 | 7.5 | 58.5 | 70
LV25 | 25 | D - High Static | 208/230/3/60 | 139.9/141.1 | 175/175 | 9.6/8.7 | 149.5/149.8 | 175/175 | 5.0/5.0 | 149.9/151.1 | 175/175 | 159.5/159.8 | 200/200 | 10 | 153.3/154.5 | 175/175
LV25 | 25 | D - High Static | 460/3/60 | 67.1 | 80 | 4.3 | 71.4 | 90 | 2.2 | 71.5 | 90 | 75.8 | 90 | 10 | 73.9 | 90
LV25 | 25 | D - High Static | 575/3/60 | 55.8 | 70 | 3.5 | 59.3 | 70 | 1.5 | 58.8 | 70 | 62.3 | 70 | 10 | 61.2 | 70
LV28 | 27.5 | B - Standard Static | 208/230/3/60 | 137.9/137.9 | 175/175 | 9.6/8.7 | 147.5/146.6 | 175/175 | 5.0/5.0 | 147.9/147.9 | 175/175 | 157.5/156.6 | 200/200 | 7.5 | 151.3/151.3 | 175/175
LV28 | 27.5 | B - Standard Static | 460/3/60 | 69.1 | 90 | 4.3 | 73.4 | 90 | 2.2 | 73.5 | 90 | 77.8 | 100 | 7.5 | 75.9 | 90
LV28 | 27.5 | B - Standard Static | 575/3/60 | 57 | 70 | 3.5 | 60.5 | 70 | 1.5 | 60 | 70 | 63.5 | 80 | 7.5 | 62.4 | 80
LV28 | 27.5 | C - Medium Static | 208/230/3/60 | 147.5/147.5 | 175/175 | 9.6/8.7 | 157.1/156.2 | 200/200 | 5.0/5.0 | 157.5/157.5 | 200/200 | 167.1/166.2 | 200/200 | 10 | 160.9/160.9 | 200/200
LV28 | 27.5 | C - Medium Static | 460/3/60 | 73.5 | 90 | 4.3 | 77.8 | 100 | 2.2 | 77.9 | 100 | 82.2 | 100 | 10 | 80.3 | 100
LV28 | 27.5 | C - Medium Static | 575/3/60 | 59.7 | 70 | 3.5 | 63.2 | 80 | 1.5 | 62.7 | 80 | 66.2 | 80 | 10 | 65.1 | 80
LV28 | 27.5 | D - High Static | 208/230/3/60 | 147.5/147.5 | 175/175 | 9.6/8.7 | 157.1/156.2 | 200/200 | 5.0/5.0 | 157.5/157.5 | 200/200 | 167.1/166.2 | 200/200 | 12 | 160.9/160.9 | 200/200
LV28 | 27.5 | D - High Static | 460/3/60 | 73.5 | 90 | 4.3 | 77.8 | 100 | 2.2 | 77.9 | 100 | 82.2 | 100 | 12 | 80.3 | 100
LV28 | 27.5 | D - High Static | 575/3/60 | 59.7 | 70 | 3.5 | 63.2 | 80 | 1.5 | 62.7 | 80 | 66.2 | 80 | 12 | 65.1 | 80
RV27 | 27.5 | B - Standard Static | 208/230/3/60 | 140.8/141.6 | 175/175 | 14.4/13 | 155.2/154.6 | 200/200 | 8/8.4 | 148.8/150 | 175/175 | 163.2/163 | 200/200 | 7.5
RV27 | 27.5 | B - Standard Static | 460/3/60 | 67.6 | 80 | 6.5 | 74.1 | 90 | 4.2 | 71.8 | 90 | 78.3 | 90 | 7.5
RV27 | 27.5 | B - Standard Static | 575/3/60 | 57.3 | 70 | 5.2 | 62.5 | 80 | 3.2 | 60.5 | 70 | 65.7 | 80 | 7.5
RV27 | 27.5 | C - Medium Static | 208/230/3/60 | 146.8/147.6 | 175/175 | 14.4/13 | 161.2/160.6 | 200/200 | 8/8.4 | 154.8/156 | 200/200 | 169.2/169 | 200/200 | 10
RV27 | 27.5 | C - Medium Static | 460/3/60 | 70.6 | 90 | 6.5 | 77.1 | 90 | 4.2 | 74.8 | 90 | 81.3 | 100 | 10
RV27 | 27.5 | C - Medium Static | 575/3/60 | 59.3 | 70 | 5.2 | 64.5 | 80 | 3.2 | 62.5 | 80 | 67.7 | 80 | 10
RV27 | 27.5 | D - High Static | 208/230/3/60 | 160.8/161.6 | 200/200 | 14.4/13 | 175.2/174.6 | 200/200 | 8/8.4 | 168.8/170 | 200/200 | 183.2/183 | 225/225 | 15
RV27 | 27.5 | D - High Static | 460/3/60 | 77.6 | 90 | 6.5 | 84.1 | 100 | 4.2 | 81.8 | 100 | 88.3 | 100 | 15
RV27 | 27.5 | D - High Static | 575/3/60 | 66.3 | 80 | 5.2 | 71.5 | 90 | 3.2 | 69.5 | 80 | 74.7 | 90 | 15
RV30 | 30 | B - Standard Static | 208/230/3/60 | 148.9/149.7 | 175/175 | 14.4/13 | 163.3/162.7 | 200/200 | 8/8.4 | 156.9/158.1 | 200/200 | 171.3/171.1 | 200/200 | 7.5
RV30 | 30 | B - Standard Static | 460/3/60 | 72.5 | 90 | 6.5 | 79 | 100 | 4.2 | 76.7 | 100 | 83.2 | 100 | 7.5
RV30 | 30 | B - Standard Static | 575/3/60 | 62 | 80 | 5.2 | 67.2 | 80 | 3.2 | 65.2 | 80 | 70.4 | 90 | 7.5
RV30 | 30 | C - Medium Static | 208/230/3/60 | 154.9/155.7 | 200/200 | 14.4/13 | 169.3/168.7 | 200/200 | 8/8.4 | 162.9/164.1 | 200/200 | 177.3/177.1 | 225/225 | 10
RV30 | 30 | C - Medium Static | 460/3/60 | 75.5 | 90 | 6.5 | 82 | 100 | 4.2 | 79.7 | 100 | 86.2 | 100 | 10
RV30 | 30 | C - Medium Static | 575/3/60 | 64 | 80 | 5.2 | 69.2 | 80 | 3.2 | 67.2 | 80 | 72.4 | 90 | 10
RV30 | 30 | D - High Static | 208/230/3/60 | 168.9/169.7 | 200/200 | 14.4/13 | 183.3/182.7 | 225/225 | 8/8.4 | 176.9/178.1 | 225/225 | 191.3/191.1 | 225/225 | 15
RV30 | 30 | D - High Static | 460/3/60 | 82.5 | 100 | 6.5 | 89 | 110 | 4.2 | 86.7 | 110 | 93.2 | 110 | 15
RV30 | 30 | D - High Static | 575/3/60 | 71 | 90 | 5.2 | 76.2 | 90 | 3.2 | 74.2 | 90 | 79.4 | 100 | 15
RV35 | 35 | B - Standard Static | 208/230/3/60 | 158.6/159.4 | 200/200 | 14.4/13 | 173/172.4 | 225/225 | 14.4/13.6 | 173/173 | 225/225 | 187.4/186 | 225/225 | 7.5
RV35 | 35 | B - Standard Static | 460/3/60 | 81.5 | 100 | 6.5 | 88 | 110 | 6.8 | 88.3 | 110 | 94.8 | 110 | 7.5
RV35 | 35 | B - Standard Static | 575/3/60 | 71.7 | 90 | 5.2 | 76.9 | 100 | 5.4 | 77.1 | 100 | 82.3 | 100 | 7.5
RV35 | 35 | C - Medium Static | 208/230/3/60 | 164.6/165.4 | 200/200 | 14.4/13 | 179/178.4 | 225/225 | 14.4/13.6 | 179/179 | 225/225 | 193.4/192 | 225/225 | 10
RV35 | 35 | C - Medium Static | 460/3/60 | 84.5 | 110 | 6.5 | 91 | 110 | 6.8 | 91.3 | 110 | 97.8 | 125 | 10
RV35 | 35 | C - Medium Static | 575/3/60 | 73.7 | 90 | 5.2 | 78.9 | 100 | 5.4 | 79.1 | 100 | 84.3 | 100 | 10
RV35 | 35 | D - High Static | 208/230/3/60 | 178.6/179.4 | 225/225 | 14.4/13 | 193/192.4 | 225/225 | 14.4/13.6 | 193/193 | 225/225 | 207.4/206 | 250/250 | 15
RV35 | 35 | D - High Static | 460/3/60 | 91.5 | 110 | 6.5 | 98 | 125 | 6.8 | 98.3 | 125 | 104.8 | 125 | 15
RV35 | 35 | D - High Static | 575/3/60 | 80.7 | 100 | 5.2 | 85.9 | 110 | 5.4 | 86.1 | 110 | 91.3 | 110 | 15
RV40 | 40 | B - Standard Static | 208/230/3/60 | 164.6/165.4 | 200/200 | 14.4/13 | 179/178.4 | 225/225 | 14.4/13.6 | 179/179 | 225/225 | 193.4/192 | 225/225 | 10
RV40 | 40 | B - Standard Static | 460/3/60 | 84.5 | 110 | 6.5 | 91 | 110 | 6.8 | 91.3 | 110 | 97.8 | 125 | 10
RV40 | 40 | B - Standard Static | 575/3/60 | 73.7 | 90 | 5.2 | 78.9 | 100 | 5.4 | 79.1 | 100 | 84.3 | 100 | 10
RV40 | 40 | C - Medium Static | 208/230/3/60 | 178.6/179.4 | 225/225 | 14.4/13 | 193/192.4 | 225/225 | 14.4/13.6 | 193/193 | 225/225 | 207.4/206 | 250/250 | 15
RV40 | 40 | C - Medium Static | 460/3/60 | 91.5 | 110 | 6.5 | 98 | 125 | 6.8 | 98.3 | 125 | 104.8 | 125 | 15
RV40 | 40 | C - Medium Static | 575/3/60 | 80.7 | 100 | 5.2 | 85.9 | 110 | 5.4 | 86.1 | 110 | 91.3 | 110 | 15
RV40 | 40 | D - High Static | 208/230/3/60 | 197.5/198.3 | 250/250 | 14.4/13 | 211.9/211.3 | 250/250 | 14.4/13.6 | 211.9/211.9 | 250/250 | 226.3/224.9 | 250/250 | 20
RV40 | 40 | D - High Static | 460/3/60 | 97.5 | 125 | 6.5 | 104 | 125 | 6.8 | 104.3 | 125 | 110.8 | 125 | 20
RV40 | 40 | D - High Static | 575/3/60 | 84.7 | 100 | 5.2 | 89.9 | 110 | 5.4 | 90.1 | 110 | 95.3 | 110 | 20
RV50 | 50 | B - Standard Static | 208/230/3/60 | 225.6/224 | 300/250 | 14.4/13 | 240/237 | 300/300 | 14.4/13.6 | 240/237.6 | 300/300 | 254.4/250.6 | 325/325 | 10
RV50 | 50 | B - Standard Static | 460/3/60 | 108.6 | 125 | 6.5 | 115.1 | 150 | 6.8 | 115.4 | 150 | 121.9 | 150 | 10
RV50 | 50 | B - Standard Static | 575/3/60 | 84.8 | 110 | 5.2 | 90 | 110 | 5.4 | 90.2 | 110 | 95.4 | 110 | 10
RV50 | 50 | C - Medium Static | 208/230/3/60 | 239.6/238 | 300/300 | 14.4/13 | 254/251 | 325/325 | 14.4/13.6 | 254/251.6 | 325/325 | 268.4/264.6 | 325/325 | 15
RV50 | 50 | C - Medium Static | 460/3/60 | 115.6 | 150 | 6.5 | 122.1 | 150 | 6.8 | 122.4 | 150 | 128.9 | 150 | 15
RV50 | 50 | C - Medium Static | 575/3/60 | 91.8 | 110 | 5.2 | 97 | 125 | 5.4 | 97.2 | 125 | 102.4 | 125 | 15
RV50 | 50 | D - High Static | 208/230/3/60 | 272.4/270.8 | 325/325 | 14.4/13 | 286.8/283.8 | 350/350 | 14.4/13.6 | 286.8/284.4 | 350/350 | 301.2/297.4 | 350/350 | 20
RV50 | 50 | D - High Static | 460/3/60 | 121.6 | 150 | 6.5 | 128.1 | 150 | 6.8 | 128.4 | 150 | 134.9 | 150 | 20
RV50 | 50 | D - High Static | 575/3/60 | 95.8 | 110 | 5.2 | 101 | 125 | 5.4 | 101.2 | 125 | 106.4 | 125 | 20

## Notes
TempMaster RTU Capacity Tables - Omni Pro KJ (3-12.5 ton), Omni Choice LV (15-27.5 ton) and Omni Select RV (27.5-50 ton), R-454B Gas/Electric
Sources: R-454B TempMaster Omni Pro KJ 3-12.5 Ton Standard Efficiency - Technical Guide (EN_US); R-454B TempMaster Omni Choice LV 15-27.5 Ton Standard Efficiency - Technical Guide (EN_US); R-454B TempMaster Omni Select 27.5-50 Ton - Technical Guide (EN_US). Extracted 10/20/2026 from the PDFs in DATA/DATA FILES.
Checked against GAS PACKS DATA.xlsx: at each schedule row's own CFM and 80/67°F EAT / 95°F OA, the cooling tables reproduce every KJ, LV and RV row's total and sensible capacity, and the calculated RV electrical reproduces every RV row's MCA and MOCP.
Cooling
Long form, one row per cabinet / CFM / entering DB / entering WB / outdoor DB, matching the Daikin workbook layout.
MBh is gross total capacity; Sensible MBh is gross sensible. S/T = Sensible / Total. ∆T = Sensible x 1000 / (1.08 x CFM).
KJ publishes one total capacity per WB row (same for every DB) plus Total Input kW (compressors + condenser fans, no blower). LV publishes total and sensible per DB and no kW, so Total Input is blank for LV. RV publishes total, sensible and total input (TI) per DB.
RV rows are the RV (vertical supply) tables; RH/RX/RY share the same cooling tables in the guide.
Combinations the catalog prints as "-" (DB too close to WB) are omitted.
Gas Heating
Heat sizes use the same Low/Medium/High names as GAS PACKS DATA.xlsx for each cabinet (e.g. KJ049: N06 Low, N08 Medium, N12 High).
KJ publishes full-fire input/output only. Low-stage input and output are derived from the catalog footnotes: N06 = 75%, N08/N12/N16 on KJ037-061 = 70%, all KJ078-150 = 60% of full fire.
LV and RV publish both stages directly. Only the staged N(S)1 (Low) and N(S)3 (High) heat options are included; the modulating T3 option is not on the schedule and is left out.
Both catalogs publish one temperature-rise range per heat option; it is listed under High Stage and Low Stage is blank.
Electrical Data
Gas/electric units (no electric heat). 208/230 V values are shown "208/230" like the Daikin workbook; 460 and 575 V rows follow.
KJ: Base and w/ Power Exhaust columns come from the "without powered convenience outlet" tables (55-58); Conv. Outlet columns from the "with powered convenience outlet" tables (59-62). Motor B = standard, D = high static blower.
KJ Conv. Outlet FLA is the catalog's "Pwr Conv Outlet" figure, printed as 20 at every voltage - the 120 V receptacle rating, not current at unit voltage. The outlet's effect at unit voltage is already in the MCA/MOP w/ Conv. Outlet columns (e.g. KJ037 208 V: 22.7 -> 32.7 A).
LV: values from the VFD 2-stage tables (62-70), which match the IntelliSpeed 2-stage ("P") blower on the schedule. Conv. Outlet columns use the catalog's "w/ 120V transformer" figures (the transformer feeds the powered outlet). Power Exhaust = on/off power exhaust; modulating power exhaust is in the last two columns. Motor B/C/D = standard/medium/high static.
Indoor Motor HP from KJ Table 29 and LV Table 52 (LV "Low" static option = standard).
KJ catalog Table 56 is titled "KJ061-150" but lists KJ078-150, like its companion tables.
RV: CALCULATED, not printed - the Omni Select guide publishes no MCA/MOP tables, only the UL 60335-2-40 method (p.75) and component currents. MCA = 1.25 x largest motor + other motors + other loads; MOP = 2.25 x largest motor + the same, rounded down to a standard size (25 A ... 300, 325, 350 A; raised to the next size up if that falls below MCA). Motors: two compressors (Table 51, 2-stage IntelliSpeed - the "P" air volume on the schedule), four standard-ambient condenser fans (Table 54), the VFD supply fan for the static level (Table 56), and for power exhaust two non-VFD exhaust motors (Table 57, amps per motor). Other loads = the powered convenience outlet only (Table 59); the control transformer is left out, as TempMaster's selection software does. These reproduce every RV MCA and MOCP on GAS PACKS DATA.xlsx, including 325 A on RV50 at 208 V.
RV supply fan: Table 56 labels its first group "27.5 ton to 30 ton"; 35 ton uses that group too (the schedule's RV35 MCA only reproduces with its 15 hp, 42 A fan). Power Exhaust FLA = both motors.
Catalog issues found during extraction
- KJ078 Table 12 (p.32), 3250 CFM / 62°F WB / 115°F OA / 90°F DB: catalog prints sensible 79.8 MBh above total 75.4 MBh - misprint, row omitted.
- RV27 cooling table (p.35), 9625 CFM / 62°F WB / 125°F OA / 65°F DB: catalog prints 0.0 for every value - row omitted.
- RV40 Table 17 (pp.42-44) prints sensible capacity above total capacity at dry-coil conditions in 241 cells (e.g. 10000 CFM / 62°F WB / 75°F OA / 90°F DB: TC 425.0, SC 430.3). Sensible is capped at total for those cells - slightly conservative; total is as printed.
- RV35 Table 16 (pp.39-41): the Total Input (kW) column is misprinted for the 125°F outdoor block (7-15 kW where 85-115°F read 28-51 kW) and for 15750 CFM at 85°F (14.7 kW). Capacities in those blocks follow the normal trend and are used; the kW values are kept as printed and are not used by the site.
- RV30 Table 15 (pp.37-38): continuation pages reprint the "75 (°F)" header above rows that continue the 95°F / 115°F blocks (confirmed from the values). They are recorded under the correct outdoor temperature.
- KJ049 Table 10 (p.27): the catalog prints no 62°F WB row at 2000 CFM for 95°F/105°F outdoor air; those combinations are absent here too (not an extraction gap).