## SCHEDULE
SCHEDULE RANGE | [23 empty] | FILTERS | [7 empty] | DOCUMENTATION
FAN COIL UNITS | [23 empty] | SERIES | CABINET | SIZE | MOTOR | ELECTRICAL | HEATING | COOLING COIL ROWS | ELECTRIC HEAT | SUBMITTAL | ENGINEERING MANUAL
MAKE | MODEL | SERIES | CABINET | AHRI 440 CERTIFIED | Fan Data |  |  | Cooling Coil (AHRI 440) |  |  |  |  | Heating | [5 empty] | Electrical Data |  |  |  | BASE UNIT WEIGHT (LBS)
[5 empty] | CFM | MOTOR | MOTOR HP | ROWS | TOTAL CAPACITY (BTU/h) | SENSIBLE CAPACITY (BTU/h) | GPM | WPD (FT) | HEAT TYPE | HW CAPACITY (MBH) | HW GPM | HW WPD (FT) | ELECTRIC HEAT (KW) | HEATER AMPS | VOLT/PH | MOTOR FLA | MCA (CALC) | MOP (CALC)
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | PSC | 1/30 | 3 | 7780 | 5920 | 1.5 | 3.3 | NONE | - | - | - | - | - | 115/1 | 0.5 | 0.6 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | PSC | 1/30 | 3 | 7780 | 5920 | 1.5 | 3.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.5 | 11.5 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | PSC | 1/30 | 3 | 7780 | 5920 | 1.5 | 3.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.5 | 16.9 | 20 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | PSC | 1/30 | 3 | 7780 | 5920 | 1.5 | 3.3 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 115/1 | 0.5 | 0.6 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | PSC | 1/30 | 3 | 7780 | 5920 | 1.5 | 3.3 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 115/1 | 0.5 | 0.6 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | NONE | - | - | - | - | - | 115/1 | 0.7 | 0.9 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.7 | 11.7 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.7 | 17.1 | 20 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 115/1 | 0.7 | 0.9 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 115/1 | 0.7 | 0.9 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | NONE | - | - | - | - | - | 277/1 | 0.4 | 0.5 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.4 | 5 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.4 | 7.3 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 277/1 | 0.4 | 0.5 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 270 | ECM (3-SPEED) | 1/4 | 3 | 7780 | 5920 | 1.5 | 3.3 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 277/1 | 0.4 | 0.5 | 15 | 24 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 02 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | PSC | 1/30 | 3 | 9690 | 7120 | 1.9 | 5.3 | NONE | - | - | - | - | - | 115/1 | 0.5 | 0.6 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | PSC | 1/30 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.5 | 11.5 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | PSC | 1/30 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.5 | 16.9 | 20 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | PSC | 1/30 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.5 | 22.4 | 25 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | PSC | 1/30 | 3 | 9690 | 7120 | 1.9 | 5.3 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 115/1 | 0.5 | 0.6 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | PSC | 1/30 | 3 | 9690 | 7120 | 1.9 | 5.3 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 115/1 | 0.5 | 0.6 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | NONE | - | - | - | - | - | 115/1 | 1 | 1.2 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1 | 12.1 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1 | 17.5 | 20 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1 | 23 | 25 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 115/1 | 1 | 1.2 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 115/1 | 1 | 1.2 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 277/1 | 0.5 | 0.6 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 9690 | 7120 | 1.9 | 5.3 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 277/1 | 0.5 | 0.6 | 15 | 28 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 03 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | NONE | - | - | - | - | - | 115/1 | 0.8 | 1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.8 | 11.9 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.8 | 17.2 | 20 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.8 | 22.8 | 25 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 115/1 | 0.8 | 1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 115/1 | 0.8 | 1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | PSC | 1/20 | 3 | 14740 | 10400 | 2.9 | 12.8 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | NONE | - | - | - | - | - | 115/1 | 1.5 | 1.9 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.5 | 12.8 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.5 | 18.1 | 20 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.5 | 23.6 | 25 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 115/1 | 1.5 | 1.9 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 115/1 | 1.5 | 1.9 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | NONE | - | - | - | - | - | 208-230/1 | 0.9 | 1.1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.9 | 7.1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.9 | 10.1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.9 | 13.1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 208-230/1 | 0.9 | 1.1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 208-230/1 | 0.9 | 1.1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | NONE | - | - | - | - | - | 277/1 | 0.8 | 1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.8 | 5.5 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.8 | 7.8 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.8 | 10 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 277/1 | 0.8 | 1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 427 | ECM (3-SPEED) | 1/4 | 3 | 14740 | 10400 | 2.9 | 12.8 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 277/1 | 0.8 | 1 | 15 | 36 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | NONE | - | - | - | - | - | 115/1 | 0.8 | 1 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.8 | 11.9 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.8 | 17.2 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.8 | 22.8 | 25 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.8 | 28.1 | 30 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.8 | 33.6 | 35 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 115/1 | 0.8 | 1 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 115/1 | 0.8 | 1 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 277/1 | 0.5 | 0.6 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | PSC | 1/20 | 3 | 17680 | 12640 | 3.5 | 7.1 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 277/1 | 0.5 | 0.6 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 115/1 | 2.6 | 3.2 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 115/1 | 2.6 | 3.2 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | NONE | - | - | - | - | - | 208-230/1 | 1.6 | 2 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.6 | 8 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.6 | 11 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.6 | 14 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1.6 | 17 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.6 | 20 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1.6 | 23 | 25 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1.6 | 26 | 30 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 208-230/1 | 1.6 | 2 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 208-230/1 | 1.6 | 2 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | NONE | - | - | - | - | - | 277/1 | 1.3 | 1.6 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.3 | 6.1 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.3 | 8.4 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.3 | 10.6 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.3 | 12.9 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.3 | 15.1 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.3 | 17.4 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.3 | 19.6 | 20 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 277/1 | 1.3 | 1.6 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 529 | ECM (3-SPEED) | 1/4 | 3 | 17680 | 12640 | 3.5 | 7.1 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 277/1 | 1.3 | 1.6 | 15 | 47 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | NONE | - | - | - | - | - | 115/1 | 1.1 | 1.4 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.1 | 12.2 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.1 | 17.6 | 20 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.1 | 23.1 | 25 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.1 | 28.5 | 30 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.1 | 34 | 35 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 115/1 | 1.1 | 1.4 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 115/1 | 1.1 | 1.4 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 277/1 | 0.5 | 0.6 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | PSC | 1/10 | 3 | 22610 | 15920 | 4.5 | 13.1 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 277/1 | 0.5 | 0.6 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | NONE | - | - | - | - | - | 115/1 | 2.3 | 2.9 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.3 | 13.8 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.3 | 19.1 | 20 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.3 | 24.6 | 25 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.3 | 30 | 30 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.3 | 35.5 | 40 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 115/1 | 2.3 | 2.9 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 115/1 | 2.3 | 2.9 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.4 | 7.7 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.4 | 10.8 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1.4 | 16.8 | 20 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1.4 | 22.8 | 25 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1.4 | 25.7 | 30 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1.4 | 28.8 | 30 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1.4 | 31.8 | 35 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | NONE | - | - | - | - | - | 277/1 | 1.2 | 1.5 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.2 | 6 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.2 | 8.2 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.2 | 10.5 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.2 | 12.8 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.2 | 15 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.2 | 17.2 | 20 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.2 | 19.5 | 20 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.2 | 21.8 | 25 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.2 | 24.1 | 25 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 277/1 | 1.2 | 1.5 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 651 | ECM (3-SPEED) | 1/4 | 3 | 22610 | 15920 | 4.5 | 13.1 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 277/1 | 1.2 | 1.5 | 15 | 58 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | NONE | - | - | - | - | - | 115/1 | 1.1 | 1.4 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.1 | 12.2 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.1 | 17.6 | 20 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.1 | 23.1 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.1 | 28.5 | 30 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.1 | 34 | 35 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 115/1 | 1.1 | 1.4 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 115/1 | 1.1 | 1.4 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.5 | 25.5 | 30 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.5 | 27.8 | 30 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 277/1 | 0.5 | 0.6 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | PSC | 1/10 | 3 | 24090 | 17050 | 4.8 | 14.9 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 277/1 | 0.5 | 0.6 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | NONE | - | - | - | - | - | 115/1 | 3.7 | 4.6 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 3.7 | 15.5 | 20 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 3.7 | 20.9 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 3.7 | 26.4 | 30 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 3.7 | 31.8 | 35 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 3.7 | 37.2 | 40 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 115/1 | 3.7 | 4.6 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 115/1 | 3.7 | 4.6 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | NONE | - | - | - | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.3 | 8.9 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.3 | 11.9 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.3 | 14.9 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.3 | 17.9 | 20 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.3 | 20.9 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.3 | 23.9 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.3 | 26.9 | 30 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.3 | 29.9 | 30 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.3 | 32.9 | 35 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.3 | 35.9 | 40 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.3 | 38.9 | 40 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 277/1 | 1.9 | 2.4 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 710 | ECM (3-SPEED) | 1/4 | 3 | 24090 | 17050 | 4.8 | 14.9 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 277/1 | 1.9 | 2.4 | 15 | 65 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 09 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | NONE | - | - | - | - | - | 115/1 | 1.6 | 2 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.6 | 12.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.6 | 18.2 | 20 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.6 | 23.8 | 25 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.6 | 29.1 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.6 | 34.6 | 35 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 115/1 | 1.6 | 2 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 115/1 | 1.6 | 2 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 277/1 | 1 | 1.2 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | PSC | (2) 1/20 | 3 | 31890 | 22740 | 6.4 | 13.8 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 277/1 | 1 | 1.2 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | NONE | - | - | - | - | - | 115/1 | 3.9 | 4.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 3.9 | 15.8 | 20 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 3.9 | 21.1 | 25 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 3.9 | 26.6 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 3.9 | 32 | 35 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 3.9 | 37.5 | 40 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 115/1 | 3.9 | 4.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 115/1 | 3.9 | 4.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | NONE | - | - | - | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.3 | 8.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.3 | 11.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.3 | 14.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.3 | 17.9 | 20 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.3 | 20.9 | 25 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.3 | 23.9 | 25 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.3 | 26.9 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.3 | 29.9 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.3 | 32.9 | 35 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.3 | 35.9 | 40 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.3 | 38.9 | 40 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.3 | 42 | 45 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.3 | 45 | 45 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | NONE | - | - | - | - | - | 277/1 | 2 | 2.5 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2 | 7 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2 | 9.2 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2 | 11.5 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2 | 13.8 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2 | 16 | 20 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2 | 18.2 | 20 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2 | 20.5 | 25 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2 | 22.8 | 25 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2 | 25.1 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2 | 27.4 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2 | 29.6 | 30 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2 | 31.9 | 35 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2 | 34.1 | 35 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 277/1 | 2 | 2.5 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 967 | ECM (3-SPEED) | (2) 1/4 | 3 | 31890 | 22740 | 6.4 | 13.8 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 277/1 | 2 | 2.5 | 15 | 81 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | NONE | - | - | - | - | - | 115/1 | 1.6 | 2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.6 | 12.9 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.6 | 18.2 | 20 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.6 | 23.8 | 25 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.6 | 29.1 | 30 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.6 | 34.6 | 35 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.6 | 40 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.6 | 45.5 | 50 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 115/1 | 1.6 | 2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 115/1 | 1.6 | 2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 277/1 | 1 | 1.2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | PSC | (2) 1/20 | 3 | 33450 | 24470 | 6.7 | 5 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 277/1 | 1 | 1.2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | NONE | - | - | - | - | - | 115/1 | 3.2 | 4 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 3.2 | 14.9 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 3.2 | 20.2 | 25 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 3.2 | 25.7 | 30 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 3.2 | 31.1 | 35 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 3.2 | 36.6 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 3.2 | 42 | 45 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 3.2 | 47.5 | 50 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 115/1 | 3.2 | 4 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 115/1 | 3.2 | 4 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 208-230/1 | 2 | 2.5 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 208-230/1 | 2 | 2.5 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | NONE | - | - | - | - | - | 277/1 | 1.6 | 2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.6 | 6.5 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.6 | 8.8 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.6 | 11 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.6 | 13.2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.6 | 15.5 | 20 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.6 | 17.8 | 20 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.6 | 20 | 20 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.6 | 22.2 | 25 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.6 | 24.6 | 25 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.6 | 26.9 | 30 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.6 | 29.1 | 30 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.6 | 31.4 | 35 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.6 | 33.6 | 35 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.6 | 35.9 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.6 | 38.1 | 40 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.6 | 40.4 | 45 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.6 | 42.6 | 45 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.6 | 44.9 | 45 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.6 | 47.1 | 50 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 277/1 | 1.6 | 2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLP-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | YES | 1075 | ECM (3-SPEED) | (2) 1/4 | 3 | 33450 | 24470 | 6.7 | 5 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 277/1 | 1.6 | 2 | 15 | 91 | HL LOW-PROFILE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 321 | PSC | 1/30 | 3 | 8860 | 6800 | 1.8 | 4.2 | NONE | - | - | - | - | - | 115/1 | 0.5 | 0.6 | 15 | 22 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 02 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 321 | PSC | 1/30 | 3 | 8860 | 6800 | 1.8 | 4.2 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 115/1 | 0.5 | 0.6 | 15 | 22 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 02 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-02 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 321 | PSC | 1/30 | 3 | 8860 | 6800 | 1.8 | 4.2 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 115/1 | 0.5 | 0.6 | 15 | 22 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 02 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 356 | PSC | 1/30 | 3 | 10820 | 7980 | 2.2 | 6.6 | NONE | - | - | - | - | - | 115/1 | 0.5 | 0.6 | 15 | 25 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 356 | PSC | 1/30 | 3 | 10820 | 7980 | 2.2 | 6.6 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 115/1 | 0.5 | 0.6 | 15 | 25 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 03 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-03 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 356 | PSC | 1/30 | 3 | 10820 | 7980 | 2.2 | 6.6 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 115/1 | 0.5 | 0.6 | 15 | 25 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 03 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 517 | PSC | 1/20 | 3 | 16820 | 12020 | 3.3 | 17.4 | NONE | - | - | - | - | - | 115/1 | 0.8 | 1 | 15 | 33 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 517 | PSC | 1/20 | 3 | 16820 | 12020 | 3.3 | 17.4 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 115/1 | 0.8 | 1 | 15 | 33 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 04 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 517 | PSC | 1/20 | 3 | 16820 | 12020 | 3.3 | 17.4 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 115/1 | 0.8 | 1 | 15 | 33 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 04 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 517 | PSC | 1/20 | 3 | 16820 | 12020 | 3.3 | 17.4 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 33 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 517 | PSC | 1/20 | 3 | 16820 | 12020 | 3.3 | 17.4 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 277/1 | 0.5 | 0.6 | 15 | 33 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 04 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-04 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 517 | PSC | 1/20 | 3 | 16820 | 12020 | 3.3 | 17.4 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 277/1 | 0.5 | 0.6 | 15 | 33 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 04 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 654 | PSC | 1/10 | 3 | 20710 | 14970 | 4.1 | 9.7 | NONE | - | - | - | - | - | 115/1 | 1.1 | 1.4 | 15 | 43 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 654 | PSC | 1/10 | 3 | 20710 | 14970 | 4.1 | 9.7 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 115/1 | 1.1 | 1.4 | 15 | 43 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 654 | PSC | 1/10 | 3 | 20710 | 14970 | 4.1 | 9.7 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 115/1 | 1.1 | 1.4 | 15 | 43 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 654 | PSC | 1/10 | 3 | 20710 | 14970 | 4.1 | 9.7 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 43 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 654 | PSC | 1/10 | 3 | 20710 | 14970 | 4.1 | 9.7 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 277/1 | 0.5 | 0.6 | 15 | 43 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-06 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 654 | PSC | 1/10 | 3 | 20710 | 14970 | 4.1 | 9.7 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 277/1 | 0.5 | 0.6 | 15 | 43 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 745 | PSC | 1/6 | 3 | 24700 | 17580 | 4.9 | 15.5 | NONE | - | - | - | - | - | 115/1 | 2.1 | 2.6 | 15 | 53 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 745 | PSC | 1/6 | 3 | 24700 | 17580 | 4.9 | 15.5 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 115/1 | 2.1 | 2.6 | 15 | 53 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 745 | PSC | 1/6 | 3 | 24700 | 17580 | 4.9 | 15.5 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 115/1 | 2.1 | 2.6 | 15 | 53 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 745 | PSC | 1/6 | 3 | 24700 | 17580 | 4.9 | 15.5 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 53 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 745 | PSC | 1/6 | 3 | 24700 | 17580 | 4.9 | 15.5 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 277/1 | 0.9 | 1.1 | 15 | 53 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-08 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 745 | PSC | 1/6 | 3 | 24700 | 17580 | 4.9 | 15.5 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 277/1 | 0.9 | 1.1 | 15 | 53 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 765 | PSC | 1/6 | 3 | 25340 | 18040 | 5 | 16.6 | NONE | - | - | - | - | - | 115/1 | 2.1 | 2.6 | 15 | 60 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 09 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 765 | PSC | 1/6 | 3 | 25340 | 18040 | 5 | 16.6 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 115/1 | 2.1 | 2.6 | 15 | 60 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 09 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 765 | PSC | 1/6 | 3 | 25340 | 18040 | 5 | 16.6 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 115/1 | 2.1 | 2.6 | 15 | 60 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 09 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 765 | PSC | 1/6 | 3 | 25340 | 18040 | 5 | 16.6 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 60 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 09 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 765 | PSC | 1/6 | 3 | 25340 | 18040 | 5 | 16.6 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 277/1 | 0.9 | 1.1 | 15 | 60 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 09 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-09 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 765 | PSC | 1/6 | 3 | 25340 | 18040 | 5 | 16.6 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 277/1 | 0.9 | 1.1 | 15 | 60 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 09 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1166 | PSC | (2) 1/10 | 3 | 36050 | 26100 | 7.2 | 18 | NONE | - | - | - | - | - | 115/1 | 2.2 | 2.8 | 15 | 74 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1166 | PSC | (2) 1/10 | 3 | 36050 | 26100 | 7.2 | 18 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 115/1 | 2.2 | 2.8 | 15 | 74 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1166 | PSC | (2) 1/10 | 3 | 36050 | 26100 | 7.2 | 18 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 115/1 | 2.2 | 2.8 | 15 | 74 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1166 | PSC | (2) 1/10 | 3 | 36050 | 26100 | 7.2 | 18 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 74 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1166 | PSC | (2) 1/10 | 3 | 36050 | 26100 | 7.2 | 18 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 277/1 | 1 | 1.2 | 15 | 74 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-10 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1166 | PSC | (2) 1/10 | 3 | 36050 | 26100 | 7.2 | 18 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 277/1 | 1 | 1.2 | 15 | 74 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1434 | PSC | (2) 1/10 | 3 | 41210 | 30660 | 8.3 | 8.1 | NONE | - | - | - | - | - | 115/1 | 2.2 | 2.8 | 15 | 83 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1434 | PSC | (2) 1/10 | 3 | 41210 | 30660 | 8.3 | 8.1 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 115/1 | 2.2 | 2.8 | 15 | 83 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1434 | PSC | (2) 1/10 | 3 | 41210 | 30660 | 8.3 | 8.1 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 115/1 | 2.2 | 2.8 | 15 | 83 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1434 | PSC | (2) 1/10 | 3 | 41210 | 30660 | 8.3 | 8.1 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 83 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1434 | PSC | (2) 1/10 | 3 | 41210 | 30660 | 8.3 | 8.1 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 277/1 | 1 | 1.2 | 15 | 83 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLF-12 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | YES | 1434 | PSC | (2) 1/10 | 3 | 41210 | 30660 | 8.3 | 8.1 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 277/1 | 1 | 1.2 | 15 | 83 | HL LOW-PROFILE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | PSC | 1/30 | 3 | 7360 | 5590 | 1.5 | 2.9 | NONE | - | - | - | - | - | 115/1 | 0.5 | 0.6 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | PSC | 1/30 | 3 | 7360 | 5590 | 1.5 | 2.9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.5 | 11.5 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | PSC | 1/30 | 3 | 7360 | 5590 | 1.5 | 2.9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.5 | 16.9 | 20 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | PSC | 1/30 | 3 | 7360 | 5590 | 1.5 | 2.9 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 115/1 | 0.5 | 0.6 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | PSC | 1/30 | 3 | 7360 | 5590 | 1.5 | 2.9 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 115/1 | 0.5 | 0.6 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | NONE | - | - | - | - | - | 115/1 | 0.7 | 0.9 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.7 | 11.7 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.7 | 17.1 | 20 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 115/1 | 0.7 | 0.9 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 115/1 | 0.7 | 0.9 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | NONE | - | - | - | - | - | 277/1 | 0.4 | 0.5 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.4 | 5 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.4 | 7.3 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | 1-ROW HW | 11.8 | 0.6 | 0.77 | - | - | 277/1 | 0.4 | 0.5 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-02 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 252 | ECM (3-SPEED) | 1/4 | 3 | 7360 | 5590 | 1.5 | 2.9 | 2-ROW HW | 20.3 | 1 | 4.92 | - | - | 277/1 | 0.4 | 0.5 | 15 | 56 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | PSC | 1/30 | 3 | 9180 | 6700 | 1.8 | 4.8 | NONE | - | - | - | - | - | 115/1 | 0.5 | 0.6 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | PSC | 1/30 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.5 | 11.5 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | PSC | 1/30 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.5 | 16.9 | 20 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | PSC | 1/30 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.5 | 22.4 | 25 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | PSC | 1/30 | 3 | 9180 | 6700 | 1.8 | 4.8 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 115/1 | 0.5 | 0.6 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | PSC | 1/30 | 3 | 9180 | 6700 | 1.8 | 4.8 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 115/1 | 0.5 | 0.6 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | NONE | - | - | - | - | - | 115/1 | 1 | 1.2 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1 | 12.1 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1 | 17.5 | 20 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1 | 23 | 25 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 115/1 | 1 | 1.2 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 115/1 | 1 | 1.2 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | 1-ROW HW | 13.4 | 0.7 | 1.11 | - | - | 277/1 | 0.5 | 0.6 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-03 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 287 | ECM (3-SPEED) | 1/4 | 3 | 9180 | 6700 | 1.8 | 4.8 | 2-ROW HW | 23.2 | 1.2 | 7.28 | - | - | 277/1 | 0.5 | 0.6 | 15 | 63 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | NONE | - | - | - | - | - | 115/1 | 0.8 | 1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.8 | 11.9 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.8 | 17.2 | 20 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.8 | 22.8 | 25 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 115/1 | 0.8 | 1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 115/1 | 0.8 | 1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 277/1 | 0.5 | 0.6 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | PSC | 1/20 | 3 | 14070 | 9880 | 2.8 | 12.2 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 277/1 | 0.5 | 0.6 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | NONE | - | - | - | - | - | 115/1 | 1.5 | 1.9 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.5 | 12.8 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.5 | 18.1 | 20 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.5 | 23.6 | 25 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 115/1 | 1.5 | 1.9 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 115/1 | 1.5 | 1.9 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | NONE | - | - | - | - | - | 208-230/1 | 0.9 | 1.1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.9 | 7.1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.9 | 10.1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.9 | 13.1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 208-230/1 | 0.9 | 1.1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 208-230/1 | 0.9 | 1.1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | NONE | - | - | - | - | - | 277/1 | 0.8 | 1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.8 | 5.5 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.8 | 7.8 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.8 | 10 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | 1-ROW HW | 19.2 | 1 | 3.07 | - | - | 277/1 | 0.8 | 1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-04 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 399 | ECM (3-SPEED) | 1/4 | 3 | 14070 | 9880 | 2.8 | 12.2 | 2-ROW HW | 32.4 | 1.7 | 19.25 | - | - | 277/1 | 0.8 | 1 | 15 | 75 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | NONE | - | - | - | - | - | 115/1 | 0.8 | 1 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.8 | 11.9 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.8 | 17.2 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.8 | 22.8 | 25 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.8 | 28.1 | 30 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.8 | 33.6 | 35 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 115/1 | 0.8 | 1 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 115/1 | 0.8 | 1 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 277/1 | 0.5 | 0.6 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | PSC | 1/20 | 3 | 16500 | 11750 | 3.3 | 6.2 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 277/1 | 0.5 | 0.6 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 115/1 | 2.6 | 3.2 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 115/1 | 2.6 | 3.2 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | NONE | - | - | - | - | - | 208-230/1 | 1.6 | 2 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.6 | 8 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.6 | 11 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.6 | 14 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1.6 | 17 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.6 | 20 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1.6 | 23 | 25 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1.6 | 26 | 30 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 208-230/1 | 1.6 | 2 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 208-230/1 | 1.6 | 2 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | NONE | - | - | - | - | - | 277/1 | 1.3 | 1.6 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.3 | 6.1 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.3 | 8.4 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.3 | 10.6 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.3 | 12.9 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.3 | 15.1 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.3 | 17.4 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.3 | 19.6 | 20 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | 1-ROW HW | 24.9 | 1.3 | 6.62 | - | - | 277/1 | 1.3 | 1.6 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-06 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 485 | ECM (3-SPEED) | 1/4 | 3 | 16500 | 11750 | 3.3 | 6.2 | 2-ROW HW | 39.9 | 2 | 4.08 | - | - | 277/1 | 1.3 | 1.6 | 15 | 92 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | NONE | - | - | - | - | - | 115/1 | 1.1 | 1.4 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.1 | 12.2 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.1 | 17.6 | 20 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.1 | 23.1 | 25 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.1 | 28.5 | 30 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.1 | 34 | 35 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 115/1 | 1.1 | 1.4 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 115/1 | 1.1 | 1.4 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 277/1 | 0.5 | 0.6 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | PSC | 1/10 | 3 | 21370 | 14980 | 4.3 | 11.7 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 277/1 | 0.5 | 0.6 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | NONE | - | - | - | - | - | 115/1 | 2.3 | 2.9 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.3 | 13.8 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.3 | 19.1 | 20 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.3 | 24.6 | 25 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.3 | 30 | 30 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.3 | 35.5 | 40 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 115/1 | 2.3 | 2.9 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 115/1 | 2.3 | 2.9 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.4 | 7.7 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.4 | 10.8 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1.4 | 16.8 | 20 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1.4 | 22.8 | 25 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1.4 | 25.7 | 30 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1.4 | 28.8 | 30 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1.4 | 31.8 | 35 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | NONE | - | - | - | - | - | 277/1 | 1.2 | 1.5 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.2 | 6 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.2 | 8.2 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.2 | 10.5 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.2 | 12.8 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.2 | 15 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.2 | 17.2 | 20 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.2 | 19.5 | 20 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.2 | 21.8 | 25 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.2 | 24.1 | 25 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | 1-ROW HW | 29.9 | 1.5 | 11.53 | - | - | 277/1 | 1.2 | 1.5 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-08 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 21370 | 14980 | 4.3 | 11.7 | 2-ROW HW | 48.4 | 2.5 | 7.21 | - | - | 277/1 | 1.2 | 1.5 | 15 | 108 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | NONE | - | - | - | - | - | 115/1 | 1.1 | 1.4 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.1 | 12.2 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.1 | 17.6 | 20 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.1 | 23.1 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.1 | 28.5 | 30 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.1 | 34 | 35 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 115/1 | 1.1 | 1.4 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 115/1 | 1.1 | 1.4 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.5 | 25.5 | 30 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.5 | 27.8 | 30 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 277/1 | 0.5 | 0.6 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | PSC | 1/10 | 3 | 23430 | 16540 | 4.6 | 14 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 277/1 | 0.5 | 0.6 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | NONE | - | - | - | - | - | 115/1 | 3.7 | 4.6 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 3.7 | 15.5 | 20 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 3.7 | 20.9 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 3.7 | 26.4 | 30 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 3.7 | 31.8 | 35 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 3.7 | 37.2 | 40 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 115/1 | 3.7 | 4.6 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 115/1 | 3.7 | 4.6 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | NONE | - | - | - | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.3 | 8.9 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.3 | 11.9 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.3 | 14.9 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.3 | 17.9 | 20 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.3 | 20.9 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.3 | 23.9 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.3 | 26.9 | 30 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.3 | 29.9 | 30 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.3 | 32.9 | 35 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.3 | 35.9 | 40 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.3 | 38.9 | 40 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | 1-ROW HW | 32.2 | 1.7 | 13.74 | - | - | 277/1 | 1.9 | 2.4 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-09 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 682 | ECM (3-SPEED) | 1/4 | 3 | 23430 | 16540 | 4.6 | 14 | 2-ROW HW | 52.2 | 2.7 | 8.59 | - | - | 277/1 | 1.9 | 2.4 | 15 | 118 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 09 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | NONE | - | - | - | - | - | 115/1 | 1.6 | 2 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.6 | 12.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.6 | 18.2 | 20 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.6 | 23.8 | 25 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.6 | 29.1 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.6 | 34.6 | 35 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 115/1 | 1.6 | 2 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 115/1 | 1.6 | 2 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 277/1 | 1 | 1.2 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 3 | 30210 | 21420 | 6 | 12.3 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 277/1 | 1 | 1.2 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | NONE | - | - | - | - | - | 115/1 | 3.9 | 4.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 3.9 | 15.8 | 20 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 3.9 | 21.1 | 25 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 3.9 | 26.6 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 3.9 | 32 | 35 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 3.9 | 37.5 | 40 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 115/1 | 3.9 | 4.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 115/1 | 3.9 | 4.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | NONE | - | - | - | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.3 | 8.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.3 | 11.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.3 | 14.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.3 | 17.9 | 20 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.3 | 20.9 | 25 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.3 | 23.9 | 25 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.3 | 26.9 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.3 | 29.9 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.3 | 32.9 | 35 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.3 | 35.9 | 40 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.3 | 38.9 | 40 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.3 | 42 | 45 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.3 | 45 | 45 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 208-230/1 | 2.3 | 2.9 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | NONE | - | - | - | - | - | 277/1 | 2 | 2.5 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2 | 7 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2 | 9.2 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2 | 11.5 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2 | 13.8 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2 | 16 | 20 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2 | 18.2 | 20 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2 | 20.5 | 25 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2 | 22.8 | 25 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2 | 25.1 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2 | 27.4 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2 | 29.6 | 30 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2 | 31.9 | 35 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2 | 34.1 | 35 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | 1-ROW HW | 42.4 | 2.2 | 3.41 | - | - | 277/1 | 2 | 2.5 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-10 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 3 | 30210 | 21420 | 6 | 12.3 | 2-ROW HW | 68.3 | 3.5 | 2.15 | - | - | 277/1 | 2 | 2.5 | 15 | 141 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | NONE | - | - | - | - | - | 115/1 | 1.6 | 2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.6 | 12.9 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.6 | 18.2 | 20 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.6 | 23.8 | 25 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.6 | 29.1 | 30 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.6 | 34.6 | 35 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.6 | 40 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.6 | 45.5 | 50 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 115/1 | 1.6 | 2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 115/1 | 1.6 | 2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 277/1 | 1 | 1.2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | PSC | (2) 1/20 | 3 | 35060 | 24540 | 7 | 19.6 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 277/1 | 1 | 1.2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | NONE | - | - | - | - | - | 115/1 | 3.2 | 4 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 3.2 | 14.9 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 3.2 | 20.2 | 25 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 3.2 | 25.7 | 30 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 3.2 | 31.1 | 35 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 3.2 | 36.6 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 3.2 | 42 | 45 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 3.2 | 47.5 | 50 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 115/1 | 3.2 | 4 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 115/1 | 3.2 | 4 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 208-230/1 | 2 | 2.5 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 208-230/1 | 2 | 2.5 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | NONE | - | - | - | - | - | 277/1 | 1.6 | 2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.6 | 6.5 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.6 | 8.8 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.6 | 11 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.6 | 13.2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.6 | 15.5 | 20 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.6 | 17.8 | 20 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.6 | 20 | 20 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.6 | 22.2 | 25 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.6 | 24.6 | 25 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.6 | 26.9 | 30 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.6 | 29.1 | 30 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.6 | 31.4 | 35 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.6 | 33.6 | 35 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.6 | 35.9 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.6 | 38.1 | 40 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.6 | 40.4 | 45 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.6 | 42.6 | 45 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.6 | 44.9 | 45 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.6 | 47.1 | 50 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | 1-ROW HW | 46.6 | 2.4 | 4.8 | - | - | 277/1 | 1.6 | 2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HLE-12 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | YES | 992 | ECM (3-SPEED) | (2) 1/4 | 3 | 35060 | 24540 | 7 | 19.6 | 2-ROW HW | 76.4 | 3.9 | 3.13 | - | - | 277/1 | 1.6 | 2 | 15 | 158 | HL LOW-PROFILE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec HL Fan Coil Catalog ET115.26-EG10
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 115/1 | 2.6 | 3.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 115/1 | 2.6 | 3.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 208-230/1 | 1 | 1.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 208-230/1 | 1 | 1.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 277/1 | 0.9 | 1.1 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | PSC | 1/6 | 4 | 21000 | 15400 | 4.8 | 8.2 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 277/1 | 0.9 | 1.1 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 115/1 | 4.8 | 6 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 115/1 | 4.8 | 6 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 277/1 | 2.6 | 3.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 642 | ECM (3-SPEED) | 1/3 | 4 | 21000 | 15400 | 4.8 | 8.2 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 277/1 | 2.6 | 3.2 | 15 | 87 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | NONE | - | - | - | - | - | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 115/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | NONE | - | - | - | - | - | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 208-230/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | NONE | - | - | - | - | - | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | PSC | 1/4 | 4 | 29600 | 21500 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 277/1 | - | - | - | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 4.8 | 54.9 | 60 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 4.8 | 60.4 | 70 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 115/1 | 4.8 | 6 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 115/1 | 4.8 | 6 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 277/1 | 2.6 | 3.2 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 900 | ECM (3-SPEED) | 1/3 | 4 | 29600 | 21500 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 277/1 | 2.6 | 3.2 | 15 | 95 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 4.9 | 55 | 60 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 4.9 | 60.5 | 70 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 115/1 | 4.9 | 6.1 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 115/1 | 4.9 | 6.1 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 208-230/1 | 2 | 2.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 208-230/1 | 2 | 2.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 277/1 | 1.9 | 2.4 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | PSC | 1/4 | 4 | 29700 | 21900 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 277/1 | 1.9 | 2.4 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 4.8 | 54.9 | 60 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 4.8 | 60.4 | 70 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 115/1 | 4.8 | 6 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 115/1 | 4.8 | 6 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 277/1 | 2.6 | 3.2 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 29700 | 21900 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 277/1 | 2.6 | 3.2 | 15 | 101 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | NONE | - | - | - | - | - | 115/1 | 5.2 | 6.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 5.2 | 17.4 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 5.2 | 22.8 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 5.2 | 28.2 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 5.2 | 33.6 | 35 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 5.2 | 39.1 | 40 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 5.2 | 44.5 | 45 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 5.2 | 50 | 50 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 5.2 | 55.4 | 60 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 5.2 | 60.9 | 70 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 115/1 | 5.2 | 6.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 115/1 | 5.2 | 6.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 208-230/1 | 2 | 2.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 208-230/1 | 2 | 2.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.8 | 6.8 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.8 | 9 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.8 | 11.2 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.8 | 13.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.8 | 15.8 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.8 | 18 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.8 | 20.2 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.8 | 22.5 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.8 | 24.9 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.8 | 27.1 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.8 | 29.4 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 277/1 | 1.8 | 2.2 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | PSC | (2) 1/6 | 4 | 39700 | 30600 | 9.2 | 4.1 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 277/1 | 1.8 | 2.2 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 115/1 | 9.6 | 12 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 115/1 | 9.6 | 12 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 208-230/1 | 5.6 | 7 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 208-230/1 | 5.6 | 7 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 277/1 | 5.2 | 6.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1398 | ECM (3-SPEED) | (2) 1/3 | 4 | 39700 | 30600 | 9.2 | 4.1 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 277/1 | 5.2 | 6.5 | 15 | 141 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | NONE | - | - | - | - | - | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 115/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | NONE | - | - | - | - | - | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 208-230/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | NONE | - | - | - | - | - | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | PSC | 1/4 | 4 | 51800 | 38600 | 11.7 | 7.5 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 277/1 | - | - | - | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 115/1 | 9.6 | 12 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 115/1 | 9.6 | 12 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 5.6 | 64.1 | 70 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 5.6 | 67.1 | 70 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 208-230/1 | 5.6 | 7 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 208-230/1 | 5.6 | 7 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 277/1 | 5.2 | 6.5 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1698 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 38600 | 11.7 | 7.5 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 277/1 | 5.2 | 6.5 | 15 | 150 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 14 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.8 | 23.1 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.8 | 28.5 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.8 | 34 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.8 | 39.4 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.8 | 44.9 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.8 | 50.2 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.8 | 55.7 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.8 | 61.1 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.8 | 66.6 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 115/1 | 9.8 | 12.2 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 115/1 | 9.8 | 12.2 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 4 | 11 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 4 | 14 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4 | 17 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4 | 20 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4 | 23 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4 | 26 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4 | 29 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4 | 32 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4 | 35 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4 | 38 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4 | 41 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4 | 44.1 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4 | 47.1 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4 | 50.1 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4 | 53.1 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4 | 56.1 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4 | 59.1 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 4 | 62.1 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 4 | 65.1 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 208-230/1 | 4 | 5 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 208-230/1 | 4 | 5 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 3.8 | 9.2 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 3.8 | 11.5 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 3.8 | 13.8 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 3.8 | 16 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 3.8 | 18.2 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 3.8 | 20.5 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 3.8 | 22.8 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 3.8 | 25 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 3.8 | 27.4 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 3.8 | 29.6 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 3.8 | 31.9 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 3.8 | 34.1 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 3.8 | 36.4 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 3.8 | 38.6 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 3.8 | 40.9 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 3.8 | 43.1 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 3.8 | 45.4 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 3.8 | 47.6 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 3.8 | 49.9 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 277/1 | 3.8 | 4.8 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | PSC | (2) 1/4 | 4 | 51800 | 41100 | 11.7 | 2.4 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 277/1 | 3.8 | 4.8 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 115/1 | 9.6 | 12 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 115/1 | 9.6 | 12 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 5.6 | 64.1 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 5.6 | 67.1 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 5.6 | 73.1 | 80 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 5.6 | 79.1 | 80 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 208-230/1 | 5.6 | 7 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 208-230/1 | 5.6 | 7 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 5.2 | 56.1 | 60 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 5.2 | 60.6 | 70 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 277/1 | 5.2 | 6.5 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1936 | ECM (3-SPEED) | (2) 1/3 | 4 | 51800 | 41100 | 11.7 | 2.4 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 277/1 | 5.2 | 6.5 | 15 | 157 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 16 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.8 | 23.1 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.8 | 28.5 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.8 | 34 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.8 | 39.4 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.8 | 44.9 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.8 | 50.2 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.8 | 55.7 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.8 | 61.1 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.8 | 66.6 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 115/1 | 9.8 | 12.2 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 115/1 | 9.8 | 12.2 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 4 | 11 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 4 | 14 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4 | 17 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4 | 20 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4 | 23 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4 | 26 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4 | 29 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4 | 32 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4 | 35 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4 | 38 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4 | 41 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4 | 44.1 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4 | 47.1 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4 | 50.1 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4 | 53.1 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4 | 56.1 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4 | 59.1 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 4 | 62.1 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 4 | 65.1 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 208-230/1 | 4 | 5 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 208-230/1 | 4 | 5 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 3.8 | 9.2 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 3.8 | 11.5 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 3.8 | 13.8 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 3.8 | 16 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 3.8 | 18.2 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 3.8 | 20.5 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 3.8 | 22.8 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 3.8 | 25 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 3.8 | 27.4 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 3.8 | 29.6 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 3.8 | 31.9 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 3.8 | 34.1 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 3.8 | 36.4 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 3.8 | 38.6 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 3.8 | 40.9 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 3.8 | 43.1 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 3.8 | 45.4 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 3.8 | 47.6 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 3.8 | 49.9 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 277/1 | 3.8 | 4.8 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | PSC | (2) 1/4 | 4 | 58100 | 44100 | 13.2 | 3.3 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 277/1 | 3.8 | 4.8 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 115/1 | 9.6 | 12 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 115/1 | 9.6 | 12 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 5.6 | 64.1 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 5.6 | 67.1 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 5.6 | 73.1 | 80 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 5.6 | 79.1 | 80 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 208-230/1 | 5.6 | 7 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 208-230/1 | 5.6 | 7 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 5.2 | 56.1 | 60 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 5.2 | 60.6 | 70 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 277/1 | 5.2 | 6.5 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1938 | ECM (3-SPEED) | (2) 1/3 | 4 | 58100 | 44100 | 13.2 | 3.3 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 277/1 | 5.2 | 6.5 | 15 | 164 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 18 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.8 | 23.1 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.8 | 28.5 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.8 | 34 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.8 | 39.4 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.8 | 44.9 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.8 | 50.2 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.8 | 55.7 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.8 | 61.1 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.8 | 66.6 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 115/1 | 9.8 | 12.2 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 115/1 | 9.8 | 12.2 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 4 | 11 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 4 | 14 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4 | 17 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4 | 20 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4 | 23 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4 | 26 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4 | 29 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4 | 32 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4 | 35 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4 | 38 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4 | 41 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4 | 44.1 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4 | 47.1 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4 | 50.1 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4 | 53.1 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4 | 56.1 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4 | 59.1 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 4 | 62.1 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 4 | 65.1 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 4 | 71.1 | 80 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 4 | 77.1 | 80 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 208-230/1 | 4 | 5 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 208-230/1 | 4 | 5 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 3.8 | 9.2 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 3.8 | 11.5 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 3.8 | 13.8 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 3.8 | 16 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 3.8 | 18.2 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 3.8 | 20.5 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 3.8 | 22.8 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 3.8 | 25 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 3.8 | 27.4 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 3.8 | 29.6 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 3.8 | 31.9 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 3.8 | 34.1 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 3.8 | 36.4 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 3.8 | 38.6 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 3.8 | 40.9 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 3.8 | 43.1 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 3.8 | 45.4 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 3.8 | 47.6 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 3.8 | 49.9 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 3.8 | 54.4 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 3.8 | 58.9 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 277/1 | 3.8 | 4.8 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | PSC | (2) 1/4 | 4 | 62200 | 46000 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 277/1 | 3.8 | 4.8 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 115/1 | 9.6 | 12 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 115/1 | 9.6 | 12 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 5.6 | 64.1 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 5.6 | 67.1 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 5.6 | 73.1 | 80 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 5.6 | 79.1 | 80 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 13 | 62.5 | 208-230/1 | 5.6 | 85.1 | 90 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 208-230/1 | 5.6 | 7 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 208-230/1 | 5.6 | 7 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 5.2 | 56.1 | 60 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 5.2 | 60.6 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 13 | 46.9 | 277/1 | 5.2 | 65.1 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | ELECTRIC | - | - | - | 14 | 50.5 | 277/1 | 5.2 | 69.6 | 70 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 14 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 277/1 | 5.2 | 6.5 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPP-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | YES | 1947 | ECM (3-SPEED) | (2) 1/2 | 4 | 62200 | 46000 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 277/1 | 5.2 | 6.5 | 15 | 170 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED DUCTED | 20 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 115/1 | 2.6 | 3.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 115/1 | 2.6 | 3.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 208-230/1 | 1 | 1.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 208-230/1 | 1 | 1.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 277/1 | 0.9 | 1.1 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | PSC | 1/6 | 4 | 21500 | 15800 | 4.9 | 8.4 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 277/1 | 0.9 | 1.1 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 115/1 | 4.8 | 6 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 115/1 | 4.8 | 6 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | 1-ROW HW | 17.5 | 0.9 | 1.6 | - | - | 277/1 | 2.6 | 3.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-06 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 668 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15800 | 4.9 | 8.4 | 2-ROW HW | 30.2 | 1.5 | 1.4 | - | - | 277/1 | 2.6 | 3.2 | 15 | 68 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | NONE | - | - | - | - | - | 115/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 115/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 115/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | NONE | - | - | - | - | - | 208-230/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 208-230/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 208-230/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | NONE | - | - | - | - | - | 277/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 277/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | PSC | 1/4 | 4 | 29900 | 21800 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 277/1 | - | - | - | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 115/1 | 4.8 | 6 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 115/1 | 4.8 | 6 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | 1-ROW HW | 24.3 | 1.2 | 3.2 | - | - | 277/1 | 2.6 | 3.2 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-08 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 922 | ECM (3-SPEED) | 1/3 | 4 | 29900 | 21800 | 6.7 | 9.3 | 2-ROW HW | 41.8 | 2.1 | 2.6 | - | - | 277/1 | 2.6 | 3.2 | 15 | 73 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 115/1 | 4.9 | 6.1 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 115/1 | 4.9 | 6.1 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 208-230/1 | 2 | 2.5 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 208-230/1 | 2 | 2.5 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 277/1 | 1.9 | 2.4 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | PSC | 1/4 | 4 | 30000 | 22200 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 277/1 | 1.9 | 2.4 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 115/1 | 4.8 | 6 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 115/1 | 4.8 | 6 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | 1-ROW HW | 27.8 | 1.4 | 0.8 | - | - | 277/1 | 2.6 | 3.2 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-10 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 939 | ECM (3-SPEED) | 1/3 | 4 | 30000 | 22200 | 6.7 | 4.2 | 2-ROW HW | 52.4 | 2.7 | 4.1 | - | - | 277/1 | 2.6 | 3.2 | 15 | 77 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | NONE | - | - | - | - | - | 115/1 | 5.2 | 6.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 115/1 | 5.2 | 6.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 115/1 | 5.2 | 6.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 208-230/1 | 2 | 2.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 208-230/1 | 2 | 2.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 277/1 | 1.8 | 2.2 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | PSC | (2) 1/6 | 4 | 40700 | 31500 | 9.4 | 4.3 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 277/1 | 1.8 | 2.2 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 115/1 | 9.6 | 12 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 115/1 | 9.6 | 12 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 208-230/1 | 5.6 | 7 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 208-230/1 | 5.6 | 7 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | 1-ROW HW | 34.5 | 1.8 | 0.9 | - | - | 277/1 | 5.2 | 6.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-12 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1459 | ECM (3-SPEED) | (2) 1/3 | 4 | 40700 | 31500 | 9.4 | 4.3 | 2-ROW HW | 61.8 | 3.2 | 1.8 | - | - | 277/1 | 5.2 | 6.5 | 15 | 114 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | NONE | - | - | - | - | - | 115/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 115/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 115/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | NONE | - | - | - | - | - | 208-230/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 208-230/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 208-230/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | NONE | - | - | - | - | - | 277/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 277/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | PSC | 1/4 | 4 | 53000 | 39500 | 12 | 7.9 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 277/1 | - | - | - | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 115/1 | 9.6 | 12 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 115/1 | 9.6 | 12 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 208-230/1 | 5.6 | 7 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 208-230/1 | 5.6 | 7 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | 1-ROW HW | 41.3 | 2.1 | 1.7 | - | - | 277/1 | 5.2 | 6.5 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-14 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1748 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 39500 | 12 | 7.9 | 2-ROW HW | 73.4 | 3.8 | 2.6 | - | - | 277/1 | 5.2 | 6.5 | 15 | 119 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 14 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 115/1 | 9.8 | 12.2 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 115/1 | 9.8 | 12.2 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 208-230/1 | 4 | 5 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 208-230/1 | 4 | 5 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 277/1 | 3.8 | 4.8 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | PSC | (2) 1/4 | 4 | 53000 | 42100 | 12 | 2.5 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 277/1 | 3.8 | 4.8 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 115/1 | 9.6 | 12 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 115/1 | 9.6 | 12 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 208-230/1 | 5.6 | 7 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 208-230/1 | 5.6 | 7 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | 1-ROW HW | 48.1 | 2.5 | 2.4 | - | - | 277/1 | 5.2 | 6.5 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-16 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1985 | ECM (3-SPEED) | (2) 1/3 | 4 | 53000 | 42100 | 12 | 2.5 | 2-ROW HW | 85.1 | 4.4 | 3.6 | - | - | 277/1 | 5.2 | 6.5 | 15 | 124 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 16 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 115/1 | 9.8 | 12.2 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 115/1 | 9.8 | 12.2 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 208-230/1 | 4 | 5 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 208-230/1 | 4 | 5 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 277/1 | 3.8 | 4.8 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 277/1 | 3.8 | 4.8 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 115/1 | 9.6 | 12 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 115/1 | 9.6 | 12 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 208-230/1 | 5.6 | 7 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 208-230/1 | 5.6 | 7 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | 1-ROW HW | 54.9 | 2.8 | 3.2 | - | - | 277/1 | 5.2 | 6.5 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-18 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 2005 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | 2-ROW HW | 96.8 | 5 | 4.9 | - | - | 277/1 | 5.2 | 6.5 | 15 | 128 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 18 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 115/1 | 9.8 | 12.2 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 115/1 | 9.8 | 12.2 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 208-230/1 | 4 | 5 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 208-230/1 | 4 | 5 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 277/1 | 3.8 | 4.8 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | PSC | (2) 1/4 | 4 | 62800 | 46600 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 277/1 | 3.8 | 4.8 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 115/1 | 9.6 | 12 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 115/1 | 9.6 | 12 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 208-230/1 | 5.6 | 7 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 208-230/1 | 5.6 | 7 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | 1-ROW HW | 61 | 3.1 | 4.1 | - | - | 277/1 | 5.2 | 6.5 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPF-20 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | YES | 1986 | ECM (3-SPEED) | (2) 1/2 | 4 | 62800 | 46600 | 14.1 | 4 | 2-ROW HW | 107.5 | 5.5 | 6.1 | - | - | 277/1 | 5.2 | 6.5 | 15 | 132 | HP HIGH-PERFORMANCE HORIZONTAL | CONCEALED FREE RETURN | 20 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | PSC | 1/6 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-06 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 663 | ECM (3-SPEED) | 1/3 | 4 | 21500 | 15700 | 4.9 | 8.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 137 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | NONE | - | - | - | - | - | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | NONE | - | - | - | - | - | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | PSC | 1/4 | 4 | 26900 | 20500 | 6 | 4.6 | NONE | - | - | - | - | - | 277/1 | - | - | - | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 4.8 | 54.9 | 60 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 4.8 | 60.4 | 70 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-08 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 918 | ECM (3-SPEED) | 1/3 | 4 | 26900 | 20500 | 6 | 4.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 146 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 4.9 | 55 | 60 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 4.9 | 60.5 | 70 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | PSC | 1/4 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 4.8 | 54.9 | 60 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 4.8 | 60.4 | 70 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-10 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 957 | ECM (3-SPEED) | 1/3 | 4 | 30800 | 22800 | 7 | 4.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 158 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | NONE | - | - | - | - | - | 115/1 | 5.2 | 6.5 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 5.2 | 17.4 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 5.2 | 22.8 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 5.2 | 28.2 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 5.2 | 33.6 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 5.2 | 39.1 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 5.2 | 44.5 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 5.2 | 50 | 50 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 5.2 | 55.4 | 60 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 5.2 | 60.9 | 70 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.8 | 6.8 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.8 | 9 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.8 | 11.2 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.8 | 13.5 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.8 | 15.8 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.8 | 18 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.8 | 20.2 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.8 | 22.5 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.8 | 24.9 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.8 | 27.1 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.8 | 29.4 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.8 | 31.6 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.8 | 33.9 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.8 | 36.1 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.8 | 38.4 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.8 | 40.6 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | PSC | (2) 1/6 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.8 | 42.9 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-12 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1431 | ECM (3-SPEED) | (2) 1/3 | 4 | 40400 | 31100 | 9.4 | 4.3 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 202 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | NONE | - | - | - | - | - | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | NONE | - | - | - | - | - | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | PSC | 1/4 | 4 | 51900 | 38700 | 11.7 | 7.5 | NONE | - | - | - | - | - | 277/1 | - | - | - | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 5.6 | 64.1 | 70 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 5.6 | 67.1 | 70 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-14 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1710 | ECM (3-SPEED) | (2) 1/3 | 4 | 51900 | 38700 | 11.7 | 7.5 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 219 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 14 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.8 | 23.1 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.8 | 28.5 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.8 | 34 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.8 | 39.4 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.8 | 44.9 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.8 | 50.2 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.8 | 55.7 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.8 | 61.1 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.8 | 66.6 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 4 | 11 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 4 | 14 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4 | 17 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4 | 20 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4 | 23 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4 | 26 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4 | 29 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4 | 32 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4 | 35 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4 | 38 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4 | 41 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4 | 44.1 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4 | 47.1 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4 | 50.1 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4 | 53.1 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4 | 56.1 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4 | 59.1 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 4 | 62.1 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 4 | 65.1 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 4 | 71.1 | 80 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 4 | 77.1 | 80 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 3.8 | 9.2 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 3.8 | 11.5 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 3.8 | 13.8 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 3.8 | 16 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 3.8 | 18.2 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 3.8 | 20.5 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 3.8 | 22.8 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 3.8 | 25 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 3.8 | 27.4 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 3.8 | 29.6 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 3.8 | 31.9 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 3.8 | 34.1 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 3.8 | 36.4 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 3.8 | 38.6 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 3.8 | 40.9 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 3.8 | 43.1 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 3.8 | 45.4 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 3.8 | 47.6 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 3.8 | 49.9 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 3.8 | 54.4 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | PSC | (2) 1/4 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 3.8 | 58.9 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | PSC | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 5.6 | 64.1 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 5.6 | 67.1 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 5.6 | 73.1 | 80 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 5.6 | 79.1 | 80 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 5.2 | 56.1 | 60 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-16 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 1970 | ECM (3-SPEED) | (2) 1/3 | 4 | 52800 | 41900 | 12 | 2.5 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 5.2 | 60.6 | 70 | 228 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.8 | 23.1 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.8 | 28.5 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.8 | 34 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.8 | 39.4 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.8 | 44.9 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.8 | 50.2 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.8 | 55.7 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.8 | 61.1 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.8 | 66.6 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 4 | 11 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 4 | 14 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4 | 17 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4 | 20 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4 | 23 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4 | 26 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4 | 29 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4 | 32 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4 | 35 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4 | 38 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4 | 41 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4 | 44.1 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4 | 47.1 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4 | 50.1 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4 | 53.1 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4 | 56.1 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4 | 59.1 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 4 | 62.1 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 4 | 65.1 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 4 | 71.1 | 80 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 4 | 77.1 | 80 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 3.8 | 9.2 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 3.8 | 11.5 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 3.8 | 13.8 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 3.8 | 16 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 3.8 | 18.2 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 3.8 | 20.5 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 3.8 | 22.8 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 3.8 | 25 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 3.8 | 27.4 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 3.8 | 29.6 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 3.8 | 31.9 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 3.8 | 34.1 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 3.8 | 36.4 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 3.8 | 38.6 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 3.8 | 40.9 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 3.8 | 43.1 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 3.8 | 45.4 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 3.8 | 47.6 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 3.8 | 49.9 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 3.8 | 54.4 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | PSC | (2) 1/4 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 3.8 | 58.9 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | PSC | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 5.6 | 64.1 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 5.6 | 67.1 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 5.6 | 73.1 | 80 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 5.6 | 79.1 | 80 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 5.2 | 56.1 | 60 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-18 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2007 | ECM (3-SPEED) | (2) 1/3 | 4 | 59500 | 45300 | 13.5 | 3.5 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 5.2 | 60.6 | 70 | 240 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 18 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.8 | 23.1 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.8 | 28.5 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.8 | 34 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.8 | 39.4 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.8 | 44.9 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.8 | 50.2 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.8 | 55.7 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.8 | 61.1 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.8 | 66.6 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 4 | 11 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 4 | 14 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4 | 17 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4 | 20 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4 | 23 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4 | 26 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4 | 29 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4 | 32 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4 | 35 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4 | 38 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4 | 41 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4 | 44.1 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4 | 47.1 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4 | 50.1 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4 | 53.1 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4 | 56.1 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4 | 59.1 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 4 | 62.1 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 4 | 65.1 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 4 | 71.1 | 80 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 4 | 77.1 | 80 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 13 | 62.5 | 208-230/1 | 4 | 83.1 | 90 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | NONE | - | - | - | - | - | 277/1 | 3.8 | 4.8 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 3.8 | 9.2 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 3.8 | 11.5 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 3.8 | 13.8 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 3.8 | 16 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 3.8 | 18.2 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 3.8 | 20.5 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 3.8 | 22.8 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 3.8 | 25 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 3.8 | 27.4 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 3.8 | 29.6 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 3.8 | 31.9 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 3.8 | 34.1 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 3.8 | 36.4 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 3.8 | 38.6 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 3.8 | 40.9 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 3.8 | 43.1 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 3.8 | 45.4 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 3.8 | 47.6 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 3.8 | 49.9 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 3.8 | 54.4 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 3.8 | 58.9 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 13 | 46.9 | 277/1 | 3.8 | 63.4 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | PSC | (2) 1/4 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 14 | 50.5 | 277/1 | 3.8 | 67.9 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | PSC | 277/1 | ELECTRIC | 4 | 14 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 9.6 | 22.9 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 9.6 | 28.2 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | NONE | - | - | - | - | - | 208-230/1 | 5.6 | 7 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 5.6 | 13 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 5.6 | 16 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5.6 | 19 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5.6 | 22 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5.6 | 25 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5.6 | 28 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5.6 | 31 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5.6 | 34 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5.6 | 37 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5.6 | 40 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5.6 | 43 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5.6 | 46.1 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5.6 | 49.1 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5.6 | 52.1 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5.6 | 55.1 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5.6 | 58.1 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5.6 | 61.1 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 9.5 | 45.7 | 208-230/1 | 5.6 | 64.1 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 10 | 48.1 | 208-230/1 | 5.6 | 67.1 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 11 | 52.9 | 208-230/1 | 5.6 | 73.1 | 80 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 12 | 57.7 | 208-230/1 | 5.6 | 79.1 | 80 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 13 | 62.5 | 208-230/1 | 5.6 | 85.1 | 90 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 5.2 | 11 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 5.2 | 13.3 | 15 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 5.2 | 56.1 | 60 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 5.2 | 60.6 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 13 | 46.9 | 277/1 | 5.2 | 65.1 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | HPE-20 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | YES | 2002 | ECM (3-SPEED) | (2) 1/2 | 4 | 63500 | 47100 | 14.3 | 4.2 | ELECTRIC | - | - | - | 14 | 50.5 | 277/1 | 5.2 | 69.6 | 70 | 250 | HP HIGH-PERFORMANCE HORIZONTAL | EXPOSED CABINET | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 14 |  | Enviro-Tec HP Fan Coil Catalog ET115.26-EG3
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | 1-ROW HW | 12.5 | 1.3 | 1.5 | - | - | 115/1 | 2.7 | 3.4 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | 2-ROW HW | 21.2 | 2.2 | 1.5 | - | - | 115/1 | 2.7 | 3.4 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1.4 | 16.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1.4 | 22.8 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1.4 | 25.7 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | 1-ROW HW | 12.5 | 1.3 | 1.5 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | 2-ROW HW | 21.2 | 2.2 | 1.5 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | 1-ROW HW | 12.5 | 1.3 | 1.5 | - | - | 277/1 | 1 | 1.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | PSC | 1/6 | 4 | 13600 | 9400 | 2.7 | 3.2 | 2-ROW HW | 21.2 | 2.2 | 1.5 | - | - | 277/1 | 1 | 1.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | NONE | - | - | - | - | - | 115/1 | 5 | 6.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 5 | 28 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 5 | 33.4 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 5 | 38.9 | 40 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 5 | 44.2 | 45 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 5 | 49.8 | 50 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | 1-ROW HW | 12.5 | 1.3 | 1.5 | - | - | 115/1 | 5 | 6.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | 2-ROW HW | 21.2 | 2.2 | 1.5 | - | - | 115/1 | 5 | 6.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | NONE | - | - | - | - | - | 208-230/1 | 3 | 3.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 3 | 15.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 3 | 18.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 3 | 21.8 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 3 | 24.8 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 3 | 27.8 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | 1-ROW HW | 12.5 | 1.3 | 1.5 | - | - | 208-230/1 | 3 | 3.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | 2-ROW HW | 21.2 | 2.2 | 1.5 | - | - | 208-230/1 | 3 | 3.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | 1-ROW HW | 12.5 | 1.3 | 1.5 | - | - | 277/1 | 2.6 | 3.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-04 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 400 | ECM (3-SPEED) | 1/3 | 4 | 13600 | 9400 | 2.7 | 3.2 | 2-ROW HW | 21.2 | 2.2 | 1.5 | - | - | 277/1 | 2.6 | 3.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 2.7 | 52.3 | 60 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 2.7 | 57.8 | 60 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | 1-ROW HW | 14.9 | 1.5 | 2.1 | - | - | 115/1 | 2.7 | 3.4 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | 2-ROW HW | 26.4 | 2.7 | 2.2 | - | - | 115/1 | 2.7 | 3.4 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1.4 | 16.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1.4 | 22.8 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1.4 | 25.7 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1.4 | 28.8 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1.4 | 31.8 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1.4 | 34.8 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1.4 | 37.8 | 40 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1.4 | 40.9 | 45 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1.4 | 43.9 | 45 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | 1-ROW HW | 14.9 | 1.5 | 2.1 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | 2-ROW HW | 26.4 | 2.7 | 2.2 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | 1-ROW HW | 14.9 | 1.5 | 2.1 | - | - | 277/1 | 1 | 1.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | PSC | 1/6 | 4 | 18000 | 12900 | 3.6 | 3.6 | 2-ROW HW | 26.4 | 2.7 | 2.2 | - | - | 277/1 | 1 | 1.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | NONE | - | - | - | - | - | 115/1 | 5 | 6.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 5 | 28 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 5 | 33.4 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 5 | 38.9 | 40 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 5 | 44.2 | 45 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 5 | 49.8 | 50 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 5 | 55.1 | 60 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 5 | 60.6 | 70 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | 1-ROW HW | 14.9 | 1.5 | 2.1 | - | - | 115/1 | 5 | 6.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | 2-ROW HW | 26.4 | 2.7 | 2.2 | - | - | 115/1 | 5 | 6.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | NONE | - | - | - | - | - | 208-230/1 | 3 | 3.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 3 | 15.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 3 | 18.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 3 | 21.8 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 3 | 24.8 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 3 | 27.8 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 3 | 30.8 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 3 | 33.8 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 3 | 36.8 | 40 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 3 | 39.8 | 40 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 3 | 42.9 | 45 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 3 | 45.9 | 50 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | 1-ROW HW | 14.9 | 1.5 | 2.1 | - | - | 208-230/1 | 3 | 3.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | 2-ROW HW | 26.4 | 2.7 | 2.2 | - | - | 208-230/1 | 3 | 3.8 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | 1-ROW HW | 14.9 | 1.5 | 2.1 | - | - | 277/1 | 2.6 | 3.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-06 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 600 | ECM (3-SPEED) | 1/3 | 4 | 18000 | 12900 | 3.6 | 3.6 | 2-ROW HW | 26.4 | 2.7 | 2.2 | - | - | 277/1 | 2.6 | 3.2 | 15 | 81 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 4.9 | 55 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 4.9 | 60.5 | 70 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | 1-ROW HW | 20.5 | 2.1 | 4.9 | - | - | 115/1 | 4.9 | 6.1 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | 2-ROW HW | 36.3 | 3.7 | 4.9 | - | - | 115/1 | 4.9 | 6.1 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | NONE | - | - | - | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.2 | 14.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.2 | 17.8 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.2 | 20.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.2 | 23.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.2 | 26.8 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.2 | 29.8 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.2 | 32.8 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.2 | 35.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.2 | 38.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.2 | 41.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.2 | 44.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.2 | 47.9 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.2 | 50.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.2 | 53.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.2 | 56.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | 1-ROW HW | 20.5 | 2.1 | 4.9 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | 2-ROW HW | 36.3 | 3.7 | 4.9 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | NONE | - | - | - | - | - | 277/1 | 2 | 2.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2 | 11.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2 | 13.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2 | 16 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2 | 18.2 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2 | 20.5 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2 | 22.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2 | 25.1 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2 | 27.4 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2 | 29.6 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2 | 31.9 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2 | 34.1 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2 | 36.4 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2 | 38.6 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2 | 40.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2 | 43.1 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | 1-ROW HW | 20.5 | 2.1 | 4.9 | - | - | 277/1 | 2 | 2.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | PSC | 1/4 | 4 | 24300 | 17200 | 4.9 | 4.8 | 2-ROW HW | 36.3 | 3.7 | 4.9 | - | - | 277/1 | 2 | 2.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | NONE | - | - | - | - | - | 115/1 | 5 | 6.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 5 | 28 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 5 | 33.4 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 5 | 38.9 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 5 | 44.2 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 5 | 49.8 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 5 | 55.1 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 5 | 60.6 | 70 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | 1-ROW HW | 20.5 | 2.1 | 4.9 | - | - | 115/1 | 5 | 6.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | 2-ROW HW | 36.3 | 3.7 | 4.9 | - | - | 115/1 | 5 | 6.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | NONE | - | - | - | - | - | 208-230/1 | 3 | 3.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 3 | 15.8 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 3 | 18.8 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 3 | 21.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 3 | 24.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 3 | 27.8 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 3 | 30.8 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 3 | 33.8 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 3 | 36.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 3 | 39.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 3 | 42.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 3 | 45.9 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 3 | 48.9 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 3 | 51.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 3 | 54.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 3 | 57.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | 1-ROW HW | 20.5 | 2.1 | 4.9 | - | - | 208-230/1 | 3 | 3.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | 2-ROW HW | 36.3 | 3.7 | 4.9 | - | - | 208-230/1 | 3 | 3.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | 1-ROW HW | 20.5 | 2.1 | 4.9 | - | - | 277/1 | 2.6 | 3.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-08 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 800 | ECM (3-SPEED) | 1/3 | 4 | 24300 | 17200 | 4.9 | 4.8 | 2-ROW HW | 36.3 | 3.7 | 4.9 | - | - | 277/1 | 2.6 | 3.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 4.9 | 55 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 4.9 | 60.5 | 70 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | 1-ROW HW | 30.7 | 3.2 | 2.9 | - | - | 115/1 | 4.9 | 6.1 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | 2-ROW HW | 52.9 | 5.4 | 4.3 | - | - | 115/1 | 4.9 | 6.1 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | NONE | - | - | - | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.2 | 14.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.2 | 17.8 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.2 | 20.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.2 | 23.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.2 | 26.8 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.2 | 29.8 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.2 | 32.8 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.2 | 35.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.2 | 38.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.2 | 41.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.2 | 44.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.2 | 47.9 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.2 | 50.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.2 | 53.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.2 | 56.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | 1-ROW HW | 30.7 | 3.2 | 2.9 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | 2-ROW HW | 52.9 | 5.4 | 4.3 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | NONE | - | - | - | - | - | 277/1 | 2 | 2.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2 | 11.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2 | 13.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2 | 16 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2 | 18.2 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2 | 20.5 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2 | 22.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2 | 25.1 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2 | 27.4 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2 | 29.6 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2 | 31.9 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2 | 34.1 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2 | 36.4 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2 | 38.6 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2 | 40.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2 | 43.1 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2 | 45.4 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2 | 47.6 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 2 | 52.1 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | 1-ROW HW | 30.7 | 3.2 | 2.9 | - | - | 277/1 | 2 | 2.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | PSC | 1/4 | 4 | 33600 | 23000 | 6.7 | 5.8 | 2-ROW HW | 52.9 | 5.4 | 4.3 | - | - | 277/1 | 2 | 2.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | NONE | - | - | - | - | - | 115/1 | 5 | 6.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 5 | 28 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 5 | 33.4 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 5 | 38.9 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 5 | 44.2 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 5 | 49.8 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 5 | 55.1 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 5 | 60.6 | 70 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | 1-ROW HW | 30.7 | 3.2 | 2.9 | - | - | 115/1 | 5 | 6.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | 2-ROW HW | 52.9 | 5.4 | 4.3 | - | - | 115/1 | 5 | 6.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | NONE | - | - | - | - | - | 208-230/1 | 3 | 3.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 3 | 15.8 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 3 | 18.8 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 3 | 21.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 3 | 24.8 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 3 | 27.8 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 3 | 30.8 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 3 | 33.8 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 3 | 36.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 3 | 39.8 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 3 | 42.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 3 | 45.9 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 3 | 48.9 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 3 | 51.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 3 | 54.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 3 | 57.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | 1-ROW HW | 30.7 | 3.2 | 2.9 | - | - | 208-230/1 | 3 | 3.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | 2-ROW HW | 52.9 | 5.4 | 4.3 | - | - | 208-230/1 | 3 | 3.8 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 2.6 | 52.9 | 60 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | 1-ROW HW | 30.7 | 3.2 | 2.9 | - | - | 277/1 | 2.6 | 3.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-10 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1000 | ECM (3-SPEED) | 1/3 | 4 | 33600 | 23000 | 6.7 | 5.8 | 2-ROW HW | 52.9 | 5.4 | 4.3 | - | - | 277/1 | 2.6 | 3.2 | 15 | 103 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | NONE | - | - | - | - | - | 115/1 | 9.6 | 12 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.6 | 33.8 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.6 | 39.1 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.6 | 44.6 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.6 | 50 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.6 | 55.5 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.6 | 60.9 | 70 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.6 | 66.4 | 70 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 1-ROW HW | 33.5 | 3.4 | 3.4 | - | - | 115/1 | 9.6 | 12 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 2-ROW HW | 58.5 | 6 | 5.2 | - | - | 115/1 | 9.6 | 12 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | NONE | - | - | - | - | - | 208-230/1 | 4 | 5 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4 | 17 | 20 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4 | 20 | 20 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4 | 23 | 25 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4 | 26 | 30 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4 | 29 | 30 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4 | 32 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4 | 35 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4 | 38 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4 | 41 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4 | 44.1 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4 | 47.1 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4 | 50.1 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4 | 53.1 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4 | 56.1 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4 | 59.1 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 1-ROW HW | 33.5 | 3.4 | 3.4 | - | - | 208-230/1 | 4 | 5 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 2-ROW HW | 58.5 | 6 | 5.2 | - | - | 208-230/1 | 4 | 5 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | NONE | - | - | - | - | - | 277/1 | 3.6 | 4.5 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 3.6 | 13.5 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 3.6 | 15.8 | 20 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 3.6 | 18 | 20 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 3.6 | 20.2 | 25 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 3.6 | 22.5 | 25 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 3.6 | 24.8 | 25 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 3.6 | 27.1 | 30 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 3.6 | 29.4 | 30 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 3.6 | 31.6 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 3.6 | 33.9 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 3.6 | 36.1 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 3.6 | 38.4 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 3.6 | 40.6 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 3.6 | 42.9 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 3.6 | 45.1 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 3.6 | 47.4 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 3.6 | 49.6 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 3.6 | 54.1 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 1-ROW HW | 33.5 | 3.4 | 3.4 | - | - | 277/1 | 3.6 | 4.5 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | PSC | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 2-ROW HW | 58.5 | 6 | 5.2 | - | - | 277/1 | 3.6 | 4.5 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | NONE | - | - | - | - | - | 115/1 | 7.7 | 9.6 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 7.7 | 31.4 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 7.7 | 36.8 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 7.7 | 42.3 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 7.7 | 47.6 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 7.7 | 53.1 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 7.7 | 58.5 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 7.7 | 64 | 70 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 1-ROW HW | 33.5 | 3.4 | 3.4 | - | - | 115/1 | 7.7 | 9.6 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 2-ROW HW | 58.5 | 6 | 5.2 | - | - | 115/1 | 7.7 | 9.6 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | NONE | - | - | - | - | - | 208-230/1 | 5 | 6.2 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 5 | 18.2 | 20 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 5 | 21.2 | 25 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 5 | 24.2 | 25 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 5 | 27.2 | 30 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 5 | 30.2 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 5 | 33.2 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 5 | 36.2 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 5 | 39.2 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 5 | 42.2 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 5 | 45.4 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 5 | 48.4 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 5 | 51.4 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 5 | 54.4 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 5 | 57.4 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 5 | 60.4 | 70 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 1-ROW HW | 33.5 | 3.4 | 3.4 | - | - | 208-230/1 | 5 | 6.2 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 2-ROW HW | 58.5 | 6 | 5.2 | - | - | 208-230/1 | 5 | 6.2 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | NONE | - | - | - | - | - | 277/1 | 4.1 | 5.1 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 4.1 | 14.1 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 4.1 | 16.4 | 20 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 4.1 | 18.6 | 20 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 4.1 | 20.9 | 25 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 4.1 | 23.1 | 25 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 4.1 | 25.4 | 30 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 4.1 | 27.8 | 30 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 4.1 | 30 | 30 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 4.1 | 32.2 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 4.1 | 34.5 | 35 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 4.1 | 36.8 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 4.1 | 39 | 40 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 4.1 | 41.2 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 4.1 | 43.5 | 45 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 4.1 | 45.8 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 4.1 | 48 | 50 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 4.1 | 50.2 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 4.1 | 54.8 | 60 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 1-ROW HW | 33.5 | 3.4 | 3.4 | - | - | 277/1 | 4.1 | 5.1 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-12 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | YES | 1200 | ECM (3-SPEED) | 1/2 | 4 | 40400 | 27500 | 8.1 | 8.2 | 2-ROW HW | 58.5 | 6 | 5.2 | - | - | 277/1 | 4.1 | 5.1 | 15 | 106 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.8 | 34 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.8 | 39.4 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.8 | 44.9 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.8 | 50.2 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.8 | 55.7 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.8 | 61.1 | 70 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.8 | 66.6 | 70 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | 1-ROW HW | 50.4 | 5.2 | 4.4 | - | - | 115/1 | 9.8 | 12.2 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | 2-ROW HW | 89 | 9.1 | 12.3 | - | - | 115/1 | 9.8 | 12.2 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | NONE | - | - | - | - | - | 208-230/1 | 4.4 | 5.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4.4 | 17.5 | 20 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4.4 | 20.5 | 25 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4.4 | 23.5 | 25 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4.4 | 26.5 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4.4 | 29.5 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4.4 | 32.5 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4.4 | 35.5 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4.4 | 38.5 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4.4 | 41.5 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4.4 | 44.6 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4.4 | 47.6 | 50 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4.4 | 50.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4.4 | 53.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4.4 | 56.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4.4 | 59.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | 1-ROW HW | 50.4 | 5.2 | 4.4 | - | - | 208-230/1 | 4.4 | 5.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | 2-ROW HW | 89 | 9.1 | 12.3 | - | - | 208-230/1 | 4.4 | 5.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | NONE | - | - | - | - | - | 277/1 | 4 | 5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 4 | 14 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 4 | 16.2 | 20 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 4 | 18.5 | 20 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 4 | 20.8 | 25 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 4 | 23 | 25 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 4 | 25.2 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 4 | 27.6 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 4 | 29.9 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 4 | 32.1 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 4 | 34.4 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 4 | 36.6 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 4 | 38.9 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 4 | 41.1 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 4 | 43.4 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 4 | 45.6 | 50 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 4 | 47.9 | 50 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 4 | 50.1 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 4 | 54.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 4 | 59.1 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 13 | 46.9 | 277/1 | 4 | 63.6 | 70 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | 1-ROW HW | 50.4 | 5.2 | 4.4 | - | - | 277/1 | 4 | 5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | PSC | (2) 1/4 | 4 | 57600 | 38400 | 11.5 | 9.8 | 2-ROW HW | 89 | 9.1 | 12.3 | - | - | 277/1 | 4 | 5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | NONE | - | - | - | - | - | 115/1 | 10 | 12.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 10 | 34.2 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 10 | 39.6 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 10 | 45.1 | 50 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 10 | 50.5 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 10 | 56 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 10 | 61.4 | 70 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 10 | 66.9 | 70 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | 1-ROW HW | 50.4 | 5.2 | 4.4 | - | - | 115/1 | 10 | 12.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | 2-ROW HW | 89 | 9.1 | 12.3 | - | - | 115/1 | 10 | 12.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | NONE | - | - | - | - | - | 208-230/1 | 6 | 7.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 6 | 19.5 | 20 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 6 | 22.5 | 25 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 6 | 25.5 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 6 | 28.5 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 6 | 31.5 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 6 | 34.5 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 6 | 37.5 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 6 | 40.5 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 6 | 43.5 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 6 | 46.6 | 50 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 6 | 49.6 | 50 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 6 | 52.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 6 | 55.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 6 | 58.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 6 | 61.6 | 70 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | 1-ROW HW | 50.4 | 5.2 | 4.4 | - | - | 208-230/1 | 6 | 7.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | 2-ROW HW | 89 | 9.1 | 12.3 | - | - | 208-230/1 | 6 | 7.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | NONE | - | - | - | - | - | 277/1 | 5.2 | 6.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 5.2 | 15.5 | 20 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 5.2 | 17.8 | 20 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 5.2 | 20 | 20 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 5.2 | 22.2 | 25 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 5.2 | 24.5 | 25 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 5.2 | 26.8 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 5.2 | 29.1 | 30 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 5.2 | 31.4 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 5.2 | 33.6 | 35 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 5.2 | 35.9 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 5.2 | 38.1 | 40 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 5.2 | 40.4 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 5.2 | 42.6 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 5.2 | 44.9 | 45 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 5.2 | 47.1 | 50 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 5.2 | 49.4 | 50 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 5.2 | 51.6 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 5.2 | 56.1 | 60 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 5.2 | 60.6 | 70 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | ELECTRIC | - | - | - | 13 | 46.9 | 277/1 | 5.2 | 65.1 | 70 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | 1-ROW HW | 50.4 | 5.2 | 4.4 | - | - | 277/1 | 5.2 | 6.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-16 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 1600 | ECM (3-SPEED) | 2/3 | 4 | 57600 | 38400 | 11.5 | 9.8 | 2-ROW HW | 89 | 9.1 | 12.3 | - | - | 277/1 | 5.2 | 6.5 | 15 | 128 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 16 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | NONE | - | - | - | - | - | 115/1 | 9.8 | 12.2 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 9.8 | 34 | 35 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 9.8 | 39.4 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 9.8 | 44.9 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 9.8 | 50.2 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 9.8 | 55.7 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 9.8 | 61.1 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 9.8 | 66.6 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | 1-ROW HW | 56 | 5.7 | 5.4 | - | - | 115/1 | 9.8 | 12.2 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | 2-ROW HW | 100.9 | 10.3 | 15.7 | - | - | 115/1 | 9.8 | 12.2 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | NONE | - | - | - | - | - | 208-230/1 | 4.4 | 5.5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 4.4 | 17.5 | 20 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 4.4 | 20.5 | 25 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 4.4 | 23.5 | 25 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 4.4 | 26.5 | 30 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 4.4 | 29.5 | 30 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 4.4 | 32.5 | 35 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 4.4 | 35.5 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 4.4 | 38.5 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 4.4 | 41.5 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 4.4 | 44.6 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 4.4 | 47.6 | 50 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 4.4 | 50.6 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 4.4 | 53.6 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 4.4 | 56.6 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 4.4 | 59.6 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | 1-ROW HW | 56 | 5.7 | 5.4 | - | - | 208-230/1 | 4.4 | 5.5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | 2-ROW HW | 100.9 | 10.3 | 15.7 | - | - | 208-230/1 | 4.4 | 5.5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | NONE | - | - | - | - | - | 277/1 | 4 | 5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 4 | 14 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 4 | 16.2 | 20 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 4 | 18.5 | 20 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 4 | 20.8 | 25 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 4 | 23 | 25 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 4 | 25.2 | 30 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 4 | 27.6 | 30 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 4 | 29.9 | 30 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 4 | 32.1 | 35 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 4 | 34.4 | 35 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 4 | 36.6 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 4 | 38.9 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 4 | 41.1 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 4 | 43.4 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 4 | 45.6 | 50 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 4 | 47.9 | 50 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 4 | 50.1 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 4 | 54.6 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 4 | 59.1 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 13 | 46.9 | 277/1 | 4 | 63.6 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | 1-ROW HW | 56 | 5.7 | 5.4 | - | - | 277/1 | 4 | 5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | PSC | (2) 1/4 | 4 | 66400 | 45700 | 13.3 | 4.3 | 2-ROW HW | 100.9 | 10.3 | 15.7 | - | - | 277/1 | 4 | 5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | NONE | - | - | - | - | - | 115/1 | 15.4 | 19.2 | 20 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 15.4 | 41 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 15.4 | 46.4 | 50 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 15.4 | 51.9 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 15.4 | 57.2 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 15.4 | 62.7 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4.5 | 39.1 | 115/1 | 15.4 | 68.1 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5 | 43.5 | 115/1 | 15.4 | 73.6 | 80 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | 1-ROW HW | 56 | 5.7 | 5.4 | - | - | 115/1 | 15.4 | 19.2 | 20 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | 2-ROW HW | 100.9 | 10.3 | 15.7 | - | - | 115/1 | 15.4 | 19.2 | 20 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | NONE | - | - | - | - | - | 208-230/1 | 10 | 12.5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 10 | 24.5 | 25 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 10 | 27.5 | 30 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 10 | 30.5 | 35 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 10 | 33.5 | 35 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 10 | 36.5 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 10 | 39.5 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 10 | 42.5 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 10 | 45.5 | 50 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 10 | 48.5 | 50 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 10 | 51.6 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 10 | 54.6 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 10 | 57.6 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 10 | 60.6 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 10 | 63.6 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 10 | 66.6 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | 1-ROW HW | 56 | 5.7 | 5.4 | - | - | 208-230/1 | 10 | 12.5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | 2-ROW HW | 100.9 | 10.3 | 15.7 | - | - | 208-230/1 | 10 | 12.5 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | NONE | - | - | - | - | - | 277/1 | 8.2 | 10.2 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 8.2 | 19.2 | 20 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 8.2 | 21.5 | 25 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 8.2 | 23.8 | 25 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 8.2 | 26 | 30 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 8.2 | 28.2 | 30 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 8.2 | 30.5 | 35 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 8.2 | 32.9 | 35 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 8.2 | 35.1 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 8.2 | 37.4 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 8.2 | 39.6 | 40 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 8.2 | 41.9 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 8.2 | 44.1 | 45 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 8.2 | 46.4 | 50 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 8.2 | 48.6 | 50 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 8.2 | 50.9 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 8.2 | 53.1 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 8.2 | 55.4 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 11 | 39.7 | 277/1 | 8.2 | 59.9 | 60 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 11 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 12 | 43.3 | 277/1 | 8.2 | 64.4 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 12 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | ELECTRIC | - | - | - | 13 | 46.9 | 277/1 | 8.2 | 68.9 | 70 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 13 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | 1-ROW HW | 56 | 5.7 | 5.4 | - | - | 277/1 | 8.2 | 10.2 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | CDV-20 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | NO | 2000 | ECM (3-SPEED) | 1 | 4 | 66400 | 45700 | 13.3 | 4.3 | 2-ROW HW | 100.9 | 10.3 | 15.7 | - | - | 277/1 | 8.2 | 10.2 | 15 | 134 | CDV HIGH-PERFORMANCE VERTICAL | CONCEALED | 20 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec CDV Fan Coil Catalog ET115.26-EG8
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | PSC | 1/50 | 3 | 5700 | 4400 | 1.3 | 2.6 | NONE | - | - | - | - | - | 115/1 | 0.4 | 0.5 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | PSC | 1/50 | 3 | 5700 | 4400 | 1.3 | 2.6 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.4 | 10.9 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | PSC | 1/50 | 3 | 5700 | 4400 | 1.3 | 2.6 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 0.4 | 0.5 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | PSC | 1/50 | 3 | 5700 | 4400 | 1.3 | 2.6 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 0.4 | 0.5 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | PSC | 1/50 | 3 | 5700 | 4400 | 1.3 | 2.6 | NONE | - | - | - | - | - | 277/1 | 0.21 | 0.3 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | PSC | 1/50 | 3 | 5700 | 4400 | 1.3 | 2.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.21 | 4.8 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | PSC | 1/50 | 3 | 5700 | 4400 | 1.3 | 2.6 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.21 | 0.3 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | PSC | 1/50 | 3 | 5700 | 4400 | 1.3 | 2.6 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.21 | 0.3 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | NONE | - | - | - | - | - | 115/1 | 1 | 1.2 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1 | 11.6 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 1 | 1.2 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 1 | 1.2 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 231 | ECM (3-SPEED) | 1/4 | 3 | 5700 | 4400 | 1.3 | 2.6 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | PSC | 1/50 | 4 | 7800 | 5500 | 1.8 | 6.16 | NONE | - | - | - | - | - | 115/1 | 0.4 | 0.5 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | PSC | 1/50 | 4 | 7800 | 5500 | 1.8 | 6.16 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.4 | 10.9 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | PSC | 1/50 | 4 | 7800 | 5500 | 1.8 | 6.16 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 0.4 | 0.5 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | PSC | 1/50 | 4 | 7800 | 5500 | 1.8 | 6.16 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 0.4 | 0.5 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | PSC | 1/50 | 4 | 7800 | 5500 | 1.8 | 6.16 | NONE | - | - | - | - | - | 277/1 | 0.21 | 0.3 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | PSC | 1/50 | 4 | 7800 | 5500 | 1.8 | 6.16 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.21 | 4.8 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | PSC | 1/50 | 4 | 7800 | 5500 | 1.8 | 6.16 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.21 | 0.3 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | PSC | 1/50 | 4 | 7800 | 5500 | 1.8 | 6.16 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.21 | 0.3 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | NONE | - | - | - | - | - | 115/1 | 1 | 1.2 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1 | 11.6 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 1 | 1.2 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 1 | 1.2 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-02 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 210 | ECM (3-SPEED) | 1/4 | 4 | 7800 | 5500 | 1.8 | 6.16 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.5 | 0.6 | 15 | 36 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | NONE | - | - | - | - | - | 115/1 | 0.55 | 0.7 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.55 | 11.1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.55 | 16.3 | 20 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 0.55 | 0.7 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 0.55 | 0.7 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | NONE | - | - | - | - | - | 277/1 | 0.31 | 0.4 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.31 | 4.9 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.31 | 7.1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.31 | 0.4 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | PSC | 1/30 | 3 | 8500 | 6300 | 1.9 | 5.85 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.31 | 0.4 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 1.3 | 1.6 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 1.3 | 1.6 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 208-230/1 | 0.8 | 1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 208-230/1 | 0.8 | 1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.7 | 0.9 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 311 | ECM (3-SPEED) | 1/4 | 3 | 8500 | 6300 | 1.9 | 5.85 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.7 | 0.9 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | NONE | - | - | - | - | - | 115/1 | 0.55 | 0.7 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.55 | 11.1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.55 | 16.3 | 20 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 0.55 | 0.7 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 0.55 | 0.7 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | NONE | - | - | - | - | - | 277/1 | 0.31 | 0.4 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.31 | 4.9 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.31 | 7.1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.31 | 0.4 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | PSC | 1/30 | 4 | 9100 | 6800 | 2.1 | 2.72 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.31 | 0.4 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 1.3 | 1.6 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 1.3 | 1.6 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 208-230/1 | 0.8 | 1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 208-230/1 | 0.8 | 1 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.7 | 0.9 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-03 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 281 | ECM (3-SPEED) | 1/4 | 4 | 9100 | 6800 | 2.1 | 2.72 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.7 | 0.9 | 15 | 45 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | NONE | - | - | - | - | - | 115/1 | 0.62 | 0.8 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.62 | 11.2 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.62 | 16.4 | 20 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.62 | 21.6 | 25 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 0.62 | 0.8 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 0.62 | 0.8 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | NONE | - | - | - | - | - | 277/1 | 0.27 | 0.3 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.27 | 4.8 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.27 | 7.1 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.27 | 9.3 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.27 | 0.3 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | PSC | 1/20 | 3 | 10500 | 8100 | 2.4 | 3.04 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.27 | 0.3 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.3 | 22.5 | 25 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 1.3 | 1.6 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 1.3 | 1.6 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 208-230/1 | 0.8 | 1 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 208-230/1 | 0.8 | 1 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.7 | 9.9 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.7 | 0.9 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 425 | ECM (3-SPEED) | 1/4 | 3 | 10500 | 8100 | 2.4 | 3.04 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.7 | 0.9 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 115/1 | 0.62 | 0.8 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.62 | 11.2 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.62 | 16.4 | 20 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.62 | 21.6 | 25 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 0.62 | 0.8 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 0.62 | 0.8 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 277/1 | 0.27 | 0.3 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.27 | 4.8 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.27 | 7.1 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.27 | 9.3 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.27 | 0.3 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | PSC | 1/20 | 4 | 12200 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.27 | 0.3 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.3 | 22.5 | 25 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 1.3 | 1.6 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 1.3 | 1.6 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 208-230/1 | 0.8 | 1 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 208-230/1 | 0.8 | 1 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.7 | 9.9 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.7 | 0.9 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-04 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 375 | ECM (3-SPEED) | 1/4 | 4 | 12200 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.7 | 0.9 | 15 | 55 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 115/1 | 0.71 | 0.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.71 | 11.3 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.71 | 16.5 | 20 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.71 | 21.8 | 25 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 0.71 | 32.1 | 35 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 0.71 | 0.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 0.71 | 0.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 0.3 | 0.4 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 0.3 | 0.4 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 115/1 | 2.3 | 2.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 2.3 | 13.3 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 2.3 | 18.5 | 20 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 2.3 | 23.8 | 25 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 2.3 | 34.1 | 35 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 2.3 | 2.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 2.3 | 2.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.4 | 7.7 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.4 | 10.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 277/1 | 1.2 | 1.5 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.2 | 6 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.2 | 8.2 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.2 | 10.5 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.2 | 15 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 1.2 | 1.5 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 602 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 1.2 | 1.5 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | NONE | - | - | - | - | - | 115/1 | 0.71 | 0.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.71 | 11.3 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.71 | 16.5 | 20 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.71 | 21.8 | 25 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 0.71 | 32.1 | 35 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 0.71 | 0.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 0.71 | 0.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 0.3 | 0.4 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | PSC | 1/20 | 4 | 21400 | 14700 | 4.9 | 8.58 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 0.3 | 0.4 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | NONE | - | - | - | - | - | 115/1 | 2.3 | 2.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 2.3 | 13.3 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 2.3 | 18.5 | 20 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 2.3 | 23.8 | 25 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 2.3 | 34.1 | 35 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 2.3 | 2.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 2.3 | 2.9 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.4 | 7.7 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.4 | 10.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | NONE | - | - | - | - | - | 277/1 | 1.2 | 1.5 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.2 | 6 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.2 | 8.2 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.2 | 10.5 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.2 | 15 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 1.2 | 1.5 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-06 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21400 | 14700 | 4.9 | 8.58 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 1.2 | 1.5 | 15 | 62 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | NONE | - | - | - | - | - | 115/1 | 1.03 | 1.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.03 | 11.7 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.03 | 16.9 | 20 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.03 | 22.2 | 25 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.03 | 32.5 | 35 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 1.03 | 1.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 1.03 | 1.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | NONE | - | - | - | - | - | 277/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.4 | 5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.4 | 7.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.4 | 9.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.4 | 14 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.4 | 18.5 | 20 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | PSC | 1/10 | 3 | 19800 | 14900 | 4.5 | 5.62 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | NONE | - | - | - | - | - | 115/1 | 3.4 | 4.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.4 | 14.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.4 | 19.9 | 20 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.4 | 25.1 | 30 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.4 | 35.5 | 40 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 3.4 | 4.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 3.4 | 4.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | NONE | - | - | - | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.1 | 8.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.1 | 11.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.1 | 14.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.1 | 20.6 | 25 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.1 | 26.6 | 30 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | NONE | - | - | - | - | - | 277/1 | 1.7 | 2.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.7 | 6.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.7 | 8.9 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.7 | 11.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.7 | 15.6 | 20 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.7 | 20.1 | 25 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 1.7 | 2.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 796 | ECM (3-SPEED) | 1/4 | 3 | 19800 | 14900 | 4.5 | 5.62 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 1.7 | 2.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | NONE | - | - | - | - | - | 115/1 | 1.03 | 1.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.03 | 11.7 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.03 | 16.9 | 20 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.03 | 22.2 | 25 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.03 | 32.5 | 35 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 1.03 | 1.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 1.03 | 1.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | NONE | - | - | - | - | - | 277/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.4 | 5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.4 | 7.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.4 | 9.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.4 | 14 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.4 | 18.5 | 20 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | PSC | 1/10 | 4 | 27400 | 19000 | 6.2 | 14.33 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | NONE | - | - | - | - | - | 115/1 | 3.4 | 4.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.4 | 14.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.4 | 19.9 | 20 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.4 | 25.1 | 30 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.4 | 35.5 | 40 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 3.4 | 4.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 3.4 | 4.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | NONE | - | - | - | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.1 | 8.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.1 | 11.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.1 | 14.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.1 | 20.6 | 25 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.1 | 26.6 | 30 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | NONE | - | - | - | - | - | 277/1 | 1.7 | 2.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.7 | 6.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.7 | 8.9 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.7 | 11.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.7 | 15.6 | 20 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.7 | 20.1 | 25 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 1.7 | 2.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-08 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 722 | ECM (3-SPEED) | 1/4 | 4 | 27400 | 19000 | 6.2 | 14.33 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 1.7 | 2.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 115/1 | 1.18 | 1.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.18 | 11.9 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.18 | 17.1 | 20 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.18 | 22.3 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.18 | 32.7 | 35 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 1.18 | 1.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 1.18 | 1.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 277/1 | 0.53 | 0.7 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.53 | 5.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.53 | 7.4 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.53 | 9.7 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.53 | 14.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.53 | 18.7 | 20 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.53 | 23.3 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 0.53 | 0.7 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | PSC | (2) 1/20 | 3 | 27600 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 0.53 | 0.7 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 115/1 | 3.6 | 4.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.6 | 14.9 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.6 | 20.1 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.6 | 25.4 | 30 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.6 | 35.8 | 40 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 3.6 | 4.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 3.6 | 4.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.2 | 8.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.2 | 11.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.2 | 14.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.2 | 20.8 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.2 | 26.8 | 30 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.2 | 32.8 | 35 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.8 | 6.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.8 | 9 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.8 | 11.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.8 | 15.8 | 20 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.8 | 20.2 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.8 | 24.9 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 1.8 | 2.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 983 | ECM (3-SPEED) | (2) 1/4 | 3 | 27600 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 1.8 | 2.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | NONE | - | - | - | - | - | 115/1 | 1.18 | 1.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.18 | 11.9 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.18 | 17.1 | 20 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.18 | 22.3 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.18 | 32.7 | 35 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 1.18 | 1.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 1.18 | 1.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | NONE | - | - | - | - | - | 277/1 | 0.53 | 0.7 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.53 | 5.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.53 | 7.4 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.53 | 9.7 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.53 | 14.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.53 | 18.7 | 20 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.53 | 23.3 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 0.53 | 0.7 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | PSC | (2) 1/20 | 4 | 35300 | 24300 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 0.53 | 0.7 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | NONE | - | - | - | - | - | 115/1 | 3.6 | 4.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.6 | 14.9 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.6 | 20.1 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.6 | 25.4 | 30 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.6 | 35.8 | 40 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 3.6 | 4.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 3.6 | 4.5 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | NONE | - | - | - | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.2 | 8.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.2 | 11.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.2 | 14.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.2 | 20.8 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.2 | 26.8 | 30 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.2 | 32.8 | 35 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.8 | 6.8 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.8 | 9 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.8 | 11.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.8 | 15.8 | 20 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.8 | 20.2 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.8 | 24.9 | 25 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 1.8 | 2.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-10 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 901 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24300 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 1.8 | 2.2 | 15 | 92 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 115/1 | 1.26 | 1.6 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.26 | 12 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.26 | 17.2 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.26 | 22.5 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.26 | 32.8 | 35 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 277/1 | 0.57 | 0.7 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.57 | 5.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.57 | 7.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.57 | 9.7 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.57 | 14.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.57 | 18.7 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.57 | 23.3 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.57 | 27.8 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | PSC | (2) 1/20 | 3 | 28100 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 115/1 | 4.4 | 5.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 4.4 | 15.9 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 4.4 | 21.1 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 4.4 | 26.4 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 4.4 | 36.8 | 40 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.6 | 9.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.6 | 12.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.6 | 15.2 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.6 | 21.2 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.6 | 27.2 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.6 | 33.2 | 35 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 28.9 | 208-230/1 | 2.6 | 39.4 | 40 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 277/1 | 2.2 | 2.8 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.2 | 7.3 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.2 | 9.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.2 | 11.8 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.2 | 16.2 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.2 | 20.8 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.2 | 25.4 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.2 | 29.9 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1192 | ECM (3-SPEED) | (2) 1/4 | 3 | 28100 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | NONE | - | - | - | - | - | 115/1 | 1.26 | 1.6 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.26 | 12 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.26 | 17.2 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.26 | 22.5 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.26 | 32.8 | 35 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | NONE | - | - | - | - | - | 277/1 | 0.57 | 0.7 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.57 | 5.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.57 | 7.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.57 | 9.7 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.57 | 14.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.57 | 18.7 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.57 | 23.3 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.57 | 27.8 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | PSC | (2) 1/20 | 4 | 35100 | 26200 | 7.9 | 2.16 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | NONE | - | - | - | - | - | 115/1 | 4.4 | 5.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 4.4 | 15.9 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 4.4 | 21.1 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 4.4 | 26.4 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 4.4 | 36.8 | 40 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | NONE | - | - | - | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.6 | 9.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.6 | 12.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.6 | 15.2 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.6 | 21.2 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.6 | 27.2 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.6 | 33.2 | 35 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 6 | 28.9 | 208-230/1 | 2.6 | 39.4 | 40 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | NONE | - | - | - | - | - | 277/1 | 2.2 | 2.8 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.2 | 7.3 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.2 | 9.5 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.2 | 11.8 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.2 | 16.2 | 20 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.2 | 20.8 | 25 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.2 | 25.4 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.2 | 29.9 | 30 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFC-12 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 1098 | ECM (3-SPEED) | (2) 1/4 | 4 | 35100 | 26200 | 7.9 | 2.16 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 105 | VF FLOOR-MOUNTED VERTICAL | CONCEALED | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 115/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.4 | 10.9 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 277/1 | 0.21 | 0.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.21 | 4.8 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.21 | 0.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.21 | 0.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 115/1 | 1 | 1.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1 | 11.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 1 | 1.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 1 | 1.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.5 | 0.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.5 | 0.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 115/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.4 | 10.9 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 0.4 | 0.5 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 277/1 | 0.21 | 0.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.21 | 4.8 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.21 | 0.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.21 | 0.3 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 115/1 | 1 | 1.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1 | 11.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 1 | 1.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 1 | 1.2 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.5 | 0.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.5 | 0.6 | 15 | 66 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 115/1 | 0.55 | 0.7 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.55 | 11.1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.55 | 16.3 | 20 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 0.55 | 0.7 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 0.55 | 0.7 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 277/1 | 0.31 | 0.4 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.31 | 4.9 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.31 | 7.1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.31 | 0.4 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.31 | 0.4 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 1.3 | 1.6 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 1.3 | 1.6 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 208-230/1 | 0.8 | 1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 208-230/1 | 0.8 | 1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.7 | 0.9 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.7 | 0.9 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 115/1 | 0.55 | 0.7 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.55 | 11.1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.55 | 16.3 | 20 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 0.55 | 0.7 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 0.55 | 0.7 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 277/1 | 0.31 | 0.4 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.31 | 4.9 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.31 | 7.1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.31 | 0.4 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.31 | 0.4 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 1.3 | 1.6 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 1.3 | 1.6 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 208-230/1 | 0.8 | 1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 208-230/1 | 0.8 | 1 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.7 | 0.9 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.7 | 0.9 | 15 | 74 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 115/1 | 0.62 | 0.8 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.62 | 11.2 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.62 | 16.4 | 20 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.62 | 21.6 | 25 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 0.62 | 0.8 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 0.62 | 0.8 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 277/1 | 0.27 | 0.3 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.27 | 4.8 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.27 | 7.1 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.27 | 9.3 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.27 | 0.3 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.27 | 0.3 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.3 | 22.5 | 25 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 1.3 | 1.6 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 1.3 | 1.6 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 208-230/1 | 0.8 | 1 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 208-230/1 | 0.8 | 1 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.7 | 9.9 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.7 | 0.9 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.7 | 0.9 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 115/1 | 0.62 | 0.8 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.62 | 11.2 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.62 | 16.4 | 20 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.62 | 21.6 | 25 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 0.62 | 0.8 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 0.62 | 0.8 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 277/1 | 0.27 | 0.3 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.27 | 4.8 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.27 | 7.1 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.27 | 9.3 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.27 | 0.3 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.27 | 0.3 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.3 | 22.5 | 25 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 1.3 | 1.6 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 1.3 | 1.6 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 208-230/1 | 0.8 | 1 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 208-230/1 | 0.8 | 1 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.7 | 9.9 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.7 | 0.9 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.7 | 0.9 | 15 | 87 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 115/1 | 0.71 | 0.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.71 | 11.3 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.71 | 16.5 | 20 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.71 | 21.8 | 25 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 0.71 | 32.1 | 35 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 0.71 | 0.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 0.71 | 0.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 0.3 | 0.4 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 0.3 | 0.4 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 115/1 | 2.3 | 2.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 2.3 | 13.3 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 2.3 | 18.5 | 20 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 2.3 | 23.8 | 25 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 2.3 | 34.1 | 35 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 2.3 | 2.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 2.3 | 2.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.4 | 7.7 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.4 | 10.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 277/1 | 1.2 | 1.5 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.2 | 6 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.2 | 8.2 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.2 | 10.5 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.2 | 15 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 1.2 | 1.5 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 1.2 | 1.5 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 115/1 | 0.71 | 0.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.71 | 11.3 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.71 | 16.5 | 20 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.71 | 21.8 | 25 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 0.71 | 32.1 | 35 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 0.71 | 0.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 0.71 | 0.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 0.3 | 0.4 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 0.3 | 0.4 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 115/1 | 2.3 | 2.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 2.3 | 13.3 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 2.3 | 18.5 | 20 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 2.3 | 23.8 | 25 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 2.3 | 34.1 | 35 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 2.3 | 2.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 2.3 | 2.9 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.4 | 7.7 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.4 | 10.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 277/1 | 1.2 | 1.5 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.2 | 6 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.2 | 8.2 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.2 | 10.5 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.2 | 15 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 1.2 | 1.5 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 1.2 | 1.5 | 15 | 96 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.03 | 11.7 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.03 | 16.9 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.03 | 22.2 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.03 | 32.5 | 35 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.4 | 5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.4 | 7.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.4 | 9.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.4 | 14 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.4 | 18.5 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.4 | 14.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.4 | 19.9 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.4 | 25.1 | 30 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.4 | 35.5 | 40 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.1 | 8.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.1 | 11.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.1 | 14.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.1 | 20.6 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.1 | 26.6 | 30 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.7 | 6.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.7 | 8.9 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.7 | 11.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.7 | 15.6 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.7 | 20.1 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.03 | 11.7 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.03 | 16.9 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.03 | 22.2 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.03 | 32.5 | 35 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.4 | 5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.4 | 7.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.4 | 9.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.4 | 14 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.4 | 18.5 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.4 | 14.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.4 | 19.9 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.4 | 25.1 | 30 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.4 | 35.5 | 40 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.1 | 8.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.1 | 11.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.1 | 14.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.1 | 20.6 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.1 | 26.6 | 30 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.7 | 6.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.7 | 8.9 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.7 | 11.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.7 | 15.6 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.7 | 20.1 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 115/1 | 1.18 | 1.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.18 | 11.9 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.18 | 17.1 | 20 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.18 | 22.3 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.18 | 32.7 | 35 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 1.18 | 1.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 1.18 | 1.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 277/1 | 0.53 | 0.7 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.53 | 5.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.53 | 7.4 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.53 | 9.7 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.53 | 14.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.53 | 18.7 | 20 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.53 | 23.3 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 0.53 | 0.7 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 0.53 | 0.7 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 115/1 | 3.6 | 4.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.6 | 14.9 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.6 | 20.1 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.6 | 25.4 | 30 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.6 | 35.8 | 40 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 3.6 | 4.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 3.6 | 4.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.2 | 8.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.2 | 11.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.2 | 14.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.2 | 20.8 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.2 | 26.8 | 30 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.2 | 32.8 | 35 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.8 | 6.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.8 | 9 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.8 | 11.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.8 | 15.8 | 20 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.8 | 20.2 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.8 | 24.9 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 1.8 | 2.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 1.8 | 2.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 115/1 | 1.18 | 1.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.18 | 11.9 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.18 | 17.1 | 20 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.18 | 22.3 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.18 | 32.7 | 35 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 1.18 | 1.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 1.18 | 1.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 277/1 | 0.53 | 0.7 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.53 | 5.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.53 | 7.4 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.53 | 9.7 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.53 | 14.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.53 | 18.7 | 20 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.53 | 23.3 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 0.53 | 0.7 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 0.53 | 0.7 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 115/1 | 3.6 | 4.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.6 | 14.9 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.6 | 20.1 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.6 | 25.4 | 30 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.6 | 35.8 | 40 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 3.6 | 4.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 3.6 | 4.5 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.2 | 8.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.2 | 11.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.2 | 14.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.2 | 20.8 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.2 | 26.8 | 30 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.2 | 32.8 | 35 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.8 | 6.8 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.8 | 9 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.8 | 11.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.8 | 15.8 | 20 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.8 | 20.2 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.8 | 24.9 | 25 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 1.8 | 2.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 1.8 | 2.2 | 15 | 131 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 115/1 | 1.26 | 1.6 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.26 | 12 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.26 | 17.2 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.26 | 22.5 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.26 | 32.8 | 35 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 277/1 | 0.57 | 0.7 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.57 | 5.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.57 | 7.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.57 | 9.7 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.57 | 14.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.57 | 18.7 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.57 | 23.3 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.57 | 27.8 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 115/1 | 4.4 | 5.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 4.4 | 15.9 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 4.4 | 21.1 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 4.4 | 26.4 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 4.4 | 36.8 | 40 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.6 | 9.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.6 | 12.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.6 | 15.2 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.6 | 21.2 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.6 | 27.2 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.6 | 33.2 | 35 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 28.9 | 208-230/1 | 2.6 | 39.4 | 40 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 277/1 | 2.2 | 2.8 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.2 | 7.3 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.2 | 9.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.2 | 11.8 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.2 | 16.2 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.2 | 20.8 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.2 | 25.4 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.2 | 29.9 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 115/1 | 1.26 | 1.6 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.26 | 12 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.26 | 17.2 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.26 | 22.5 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.26 | 32.8 | 35 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 277/1 | 0.57 | 0.7 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.57 | 5.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.57 | 7.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.57 | 9.7 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.57 | 14.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.57 | 18.7 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.57 | 23.3 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.57 | 27.8 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 115/1 | 4.4 | 5.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 4.4 | 15.9 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 4.4 | 21.1 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 4.4 | 26.4 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 4.4 | 36.8 | 40 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.6 | 9.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.6 | 12.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.6 | 15.2 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.6 | 21.2 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.6 | 27.2 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.6 | 33.2 | 35 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 6 | 28.9 | 208-230/1 | 2.6 | 39.4 | 40 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 277/1 | 2.2 | 2.8 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.2 | 7.3 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.2 | 9.5 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.2 | 11.8 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.2 | 16.2 | 20 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.2 | 20.8 | 25 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.2 | 25.4 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.2 | 29.9 | 30 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFE-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 149 | VF FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 115/1 | 0.4 | 0.5 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.4 | 10.9 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 0.4 | 0.5 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 0.4 | 0.5 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 277/1 | 0.21 | 0.3 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.21 | 4.8 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.21 | 0.3 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | PSC | 1/50 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.21 | 0.3 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 115/1 | 1 | 1.2 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1 | 11.6 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 1 | 1.2 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 1 | 1.2 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.5 | 0.6 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 221 | ECM (3-SPEED) | 1/4 | 3 | 5500 | 4300 | 1.3 | 2.44 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.5 | 0.6 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 115/1 | 0.4 | 0.5 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.4 | 10.9 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 0.4 | 0.5 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 0.4 | 0.5 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 277/1 | 0.21 | 0.3 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.21 | 4.8 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.21 | 0.3 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | PSC | 1/50 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.21 | 0.3 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 115/1 | 1 | 1.2 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1 | 11.6 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 115/1 | 1 | 1.2 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 115/1 | 1 | 1.2 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 1-ROW HW | 7.86 | 0.4 | 0.2 | - | - | 277/1 | 0.5 | 0.6 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-02 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 200 | ECM (3-SPEED) | 1/4 | 4 | 7500 | 5300 | 1.7 | 5.91 | 2-ROW HW | 14.27 | 0.7 | 1 | - | - | 277/1 | 0.5 | 0.6 | 15 | 68 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 02 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 115/1 | 0.55 | 0.7 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.55 | 11.1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.55 | 16.3 | 20 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 0.55 | 0.7 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 0.55 | 0.7 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 277/1 | 0.31 | 0.4 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.31 | 4.9 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.31 | 7.1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.31 | 0.4 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | PSC | 1/30 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.31 | 0.4 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 1.3 | 1.6 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 1.3 | 1.6 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 208-230/1 | 0.8 | 1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 208-230/1 | 0.8 | 1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.7 | 0.9 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 301 | ECM (3-SPEED) | 1/4 | 3 | 8300 | 6200 | 1.9 | 5.63 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.7 | 0.9 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 115/1 | 0.55 | 0.7 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.55 | 11.1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.55 | 16.3 | 20 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 0.55 | 0.7 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 0.55 | 0.7 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 277/1 | 0.31 | 0.4 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.31 | 4.9 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.31 | 7.1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.31 | 0.4 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | PSC | 1/30 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.31 | 0.4 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 115/1 | 1.3 | 1.6 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 115/1 | 1.3 | 1.6 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 208-230/1 | 0.8 | 1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 208-230/1 | 0.8 | 1 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 1-ROW HW | 10.98 | 0.6 | 0.4 | - | - | 277/1 | 0.7 | 0.9 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-03 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 269 | ECM (3-SPEED) | 1/4 | 4 | 8700 | 6500 | 1.9 | 2.4 | 2-ROW HW | 19.15 | 1 | 1.9 | - | - | 277/1 | 0.7 | 0.9 | 15 | 76 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 03 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 115/1 | 0.62 | 0.8 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.62 | 11.2 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.62 | 16.4 | 20 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.62 | 21.6 | 25 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 0.62 | 0.8 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 0.62 | 0.8 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 277/1 | 0.27 | 0.3 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.27 | 4.8 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.27 | 7.1 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.27 | 9.3 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.27 | 0.3 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | PSC | 1/20 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.27 | 0.3 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.3 | 22.5 | 25 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 1.3 | 1.6 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 1.3 | 1.6 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 208-230/1 | 0.8 | 1 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 208-230/1 | 0.8 | 1 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.7 | 9.9 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.7 | 0.9 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 423 | ECM (3-SPEED) | 1/4 | 3 | 10600 | 8100 | 2.4 | 3.05 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.7 | 0.9 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 115/1 | 0.62 | 0.8 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.62 | 11.2 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.62 | 16.4 | 20 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.62 | 21.6 | 25 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 0.62 | 0.8 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 0.62 | 0.8 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 277/1 | 0.27 | 0.3 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.27 | 4.8 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.27 | 7.1 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.27 | 9.3 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.27 | 0.3 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | PSC | 1/20 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.27 | 0.3 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.3 | 12 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.3 | 17.2 | 20 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.3 | 22.5 | 25 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 115/1 | 1.3 | 1.6 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 115/1 | 1.3 | 1.6 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 208-230/1 | 0.8 | 1 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 208-230/1 | 0.8 | 1 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | NONE | - | - | - | - | - | 277/1 | 0.7 | 0.9 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.7 | 5.4 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.7 | 7.6 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.7 | 9.9 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 1-ROW HW | 15.95 | 0.8 | 0.8 | - | - | 277/1 | 0.7 | 0.9 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-04 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 379 | ECM (3-SPEED) | 1/4 | 4 | 12300 | 9100 | 2.8 | 2.3 | 2-ROW HW | 27.48 | 1.4 | 4.2 | - | - | 277/1 | 0.7 | 0.9 | 15 | 89 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 04 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 115/1 | 0.71 | 0.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.71 | 11.3 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.71 | 16.5 | 20 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.71 | 21.8 | 25 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 0.71 | 32.1 | 35 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 0.71 | 0.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 0.71 | 0.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 0.3 | 0.4 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | PSC | 1/20 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 0.3 | 0.4 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 115/1 | 2.3 | 2.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 2.3 | 13.3 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 2.3 | 18.5 | 20 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 2.3 | 23.8 | 25 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 2.3 | 34.1 | 35 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 2.3 | 2.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 2.3 | 2.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.4 | 7.7 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.4 | 10.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | NONE | - | - | - | - | - | 277/1 | 1.2 | 1.5 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.2 | 6 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.2 | 8.2 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.2 | 10.5 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.2 | 15 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 1.2 | 1.5 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 599 | ECM (3-SPEED) | 1/4 | 3 | 14900 | 11400 | 3.3 | 2.88 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 1.2 | 1.5 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 115/1 | 0.71 | 0.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 0.71 | 11.3 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 0.71 | 16.5 | 20 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 0.71 | 21.8 | 25 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 0.71 | 32.1 | 35 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 0.71 | 0.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 0.71 | 0.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 0.3 | 0.4 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | PSC | 1/20 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 0.3 | 0.4 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 115/1 | 2.3 | 2.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 2.3 | 13.3 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 2.3 | 18.5 | 20 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 2.3 | 23.8 | 25 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 2.3 | 34.1 | 35 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 115/1 | 2.3 | 2.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 115/1 | 2.3 | 2.9 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1.4 | 7.7 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1.4 | 10.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1.4 | 13.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1.4 | 19.8 | 20 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 208-230/1 | 1.4 | 1.8 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | NONE | - | - | - | - | - | 277/1 | 1.2 | 1.5 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.2 | 6 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.2 | 8.2 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.2 | 10.5 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.2 | 15 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 1-ROW HW | 21.79 | 1.1 | 1.7 | - | - | 277/1 | 1.2 | 1.5 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-06 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 546 | ECM (3-SPEED) | 1/4 | 4 | 21300 | 14700 | 4.8 | 8.3 | 2-ROW HW | 36.75 | 1.9 | 8.8 | - | - | 277/1 | 1.2 | 1.5 | 15 | 99 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 06 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.03 | 11.7 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.03 | 16.9 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.03 | 22.2 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.03 | 32.5 | 35 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.4 | 5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.4 | 7.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.4 | 9.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.4 | 14 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.4 | 18.5 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | PSC | 1/10 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.4 | 14.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.4 | 19.9 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.4 | 25.1 | 30 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.4 | 35.5 | 40 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.1 | 8.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.1 | 11.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.1 | 14.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.1 | 20.6 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.1 | 26.6 | 30 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | NONE | - | - | - | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.7 | 6.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.7 | 8.9 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.7 | 11.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.7 | 15.6 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.7 | 20.1 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 823 | ECM (3-SPEED) | 1/4 | 3 | 20400 | 15400 | 4.7 | 6.04 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.03 | 11.7 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.03 | 16.9 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.03 | 22.2 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.03 | 32.5 | 35 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 1.03 | 1.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.4 | 5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.4 | 7.3 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.4 | 9.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.4 | 14 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.4 | 18.5 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | PSC | 1/10 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 0.4 | 0.5 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.4 | 14.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.4 | 19.9 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.4 | 25.1 | 30 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.4 | 35.5 | 40 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 115/1 | 3.4 | 4.2 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.1 | 8.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.1 | 11.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.1 | 14.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.1 | 20.6 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.1 | 26.6 | 30 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 208-230/1 | 2.1 | 2.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | NONE | - | - | - | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.7 | 6.6 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.7 | 8.9 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.7 | 11.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.7 | 15.6 | 20 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.7 | 20.1 | 25 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 1-ROW HW | 23.85 | 1.2 | 2.1 | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-08 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 748 | ECM (3-SPEED) | 1/4 | 4 | 28200 | 19600 | 6.4 | 15.19 | 2-ROW HW | 40.07 | 2.1 | 10.7 | - | - | 277/1 | 1.7 | 2.1 | 15 | 102 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 08 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 115/1 | 1.18 | 1.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.18 | 11.9 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.18 | 17.1 | 20 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.18 | 22.3 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.18 | 32.7 | 35 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 1.18 | 1.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 1.18 | 1.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 277/1 | 0.53 | 0.7 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.53 | 5.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.53 | 7.4 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.53 | 9.7 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.53 | 14.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.53 | 18.7 | 20 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.53 | 23.3 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 0.53 | 0.7 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | PSC | (2) 1/20 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 0.53 | 0.7 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 115/1 | 3.6 | 4.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.6 | 14.9 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.6 | 20.1 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.6 | 25.4 | 30 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.6 | 35.8 | 40 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 3.6 | 4.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 3.6 | 4.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.2 | 8.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.2 | 11.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.2 | 14.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.2 | 20.8 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.2 | 26.8 | 30 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.2 | 32.8 | 35 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.8 | 6.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.8 | 9 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.8 | 11.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.8 | 15.8 | 20 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.8 | 20.2 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.8 | 24.9 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 1.8 | 2.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 981 | ECM (3-SPEED) | (2) 1/4 | 3 | 27700 | 20100 | 6.3 | 7.42 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 1.8 | 2.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 115/1 | 1.18 | 1.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.18 | 11.9 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.18 | 17.1 | 20 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.18 | 22.3 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.18 | 32.7 | 35 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 1.18 | 1.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 1.18 | 1.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 277/1 | 0.53 | 0.7 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.53 | 5.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.53 | 7.4 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.53 | 9.7 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.53 | 14.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.53 | 18.7 | 20 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.53 | 23.3 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 0.53 | 0.7 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | PSC | (2) 1/20 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 0.53 | 0.7 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 115/1 | 3.6 | 4.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 3.6 | 14.9 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 3.6 | 20.1 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 3.6 | 25.4 | 30 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 3.6 | 35.8 | 40 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 115/1 | 3.6 | 4.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 115/1 | 3.6 | 4.5 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.2 | 8.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.2 | 11.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.2 | 14.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.2 | 20.8 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.2 | 26.8 | 30 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.2 | 32.8 | 35 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 208-230/1 | 2.2 | 2.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | NONE | - | - | - | - | - | 277/1 | 1.8 | 2.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.8 | 6.8 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.8 | 9 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.8 | 11.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.8 | 15.8 | 20 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.8 | 20.2 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.8 | 24.9 | 25 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 1-ROW HW | 34.28 | 1.8 | 5.1 | - | - | 277/1 | 1.8 | 2.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-10 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 893 | ECM (3-SPEED) | (2) 1/4 | 4 | 35300 | 24200 | 7.9 | 15.57 | 2-ROW HW | 54.72 | 2.8 | 3.4 | - | - | 277/1 | 1.8 | 2.2 | 15 | 135 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 10 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 115/1 | 1.26 | 1.6 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.26 | 12 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.26 | 17.2 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.26 | 22.5 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.26 | 32.8 | 35 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 277/1 | 0.57 | 0.7 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.57 | 5.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.57 | 7.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.57 | 9.7 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.57 | 14.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.57 | 18.7 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.57 | 23.3 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.57 | 27.8 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | PSC | (2) 1/20 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 115/1 | 4.4 | 5.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 4.4 | 15.9 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 4.4 | 21.1 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 4.4 | 26.4 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 4.4 | 36.8 | 40 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.6 | 9.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.6 | 12.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.6 | 15.2 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.6 | 21.2 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.6 | 27.2 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.6 | 33.2 | 35 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 28.9 | 208-230/1 | 2.6 | 39.4 | 40 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | NONE | - | - | - | - | - | 277/1 | 2.2 | 2.8 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.2 | 7.3 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.2 | 9.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.2 | 11.8 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.2 | 16.2 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.2 | 20.8 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.2 | 25.4 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.2 | 29.9 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1178 | ECM (3-SPEED) | (2) 1/4 | 3 | 28200 | 21700 | 6.4 | 2.88 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 115/1 | 1.26 | 1.6 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 1.26 | 12 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 1.26 | 17.2 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 1.26 | 22.5 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 1.26 | 32.8 | 35 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 1.26 | 1.6 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 277/1 | 0.57 | 0.7 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.57 | 5.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.57 | 7.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.57 | 9.7 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.57 | 14.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.57 | 18.7 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.57 | 23.3 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.57 | 27.8 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | PSC | (2) 1/20 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 0.57 | 0.7 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | PSC | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 115/1 | 4.4 | 5.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 8.3 | 115/1 | 4.4 | 15.9 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 12.5 | 115/1 | 4.4 | 21.1 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 16.7 | 115/1 | 4.4 | 26.4 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 25 | 115/1 | 4.4 | 36.8 | 40 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 115/1 | 4.4 | 5.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 115/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.6 | 9.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.6 | 12.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.6 | 15.2 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.6 | 21.2 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.6 | 27.2 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.6 | 33.2 | 35 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 6 | 28.9 | 208-230/1 | 2.6 | 39.4 | 40 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 208-230/1 | 2.6 | 3.2 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 208-230/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | NONE | - | - | - | - | - | 277/1 | 2.2 | 2.8 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.2 | 7.3 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.2 | 9.5 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.2 | 11.8 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.2 | 16.2 | 20 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.2 | 20.8 | 25 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.2 | 25.4 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.2 | 29.9 | 30 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 1-ROW HW | 38.81 | 2 | 7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | 1-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VFS-12 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | YES | 1077 | ECM (3-SPEED) | (2) 1/4 | 4 | 35000 | 25900 | 7.9 | 2.17 | 2-ROW HW | 62.21 | 3.2 | 4.7 | - | - | 277/1 | 2.2 | 2.8 | 15 | 153 | VF FLOOR-MOUNTED VERTICAL | EXPOSED SLOPED TOP | 12 | ECM (3-SPEED) | 277/1 | 2-ROW HW | 4 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 51 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 51 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | 1-ROW HW | 9.2 | 0.6 | 0.6 | - | - | 115/1 | 0.6 | 0.8 | 15 | 51 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | 2-ROW HW | 15.4 | 1.1 | 2.6 | - | - | 115/1 | 0.6 | 0.8 | 15 | 51 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 51 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 51 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | 1-ROW HW | 9.2 | 0.6 | 0.6 | - | - | 277/1 | 0.3 | 0.4 | 15 | 51 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | 2-ROW HW | 15.4 | 1.1 | 2.6 | - | - | 277/1 | 0.3 | 0.4 | 15 | 51 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 02 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | ELECTRIC | - | - | - | 1.5 | 13.1 | 115/1 | 0.6 | 17.1 | 20 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | 1-ROW HW | 13.4 | 0.9 | 1.2 | - | - | 115/1 | 0.6 | 0.8 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | 2-ROW HW | 22.4 | 1.5 | 5.6 | - | - | 115/1 | 0.6 | 0.8 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | 1-ROW HW | 13.4 | 0.9 | 1.2 | - | - | 277/1 | 0.3 | 0.4 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | 2-ROW HW | 22.4 | 1.5 | 5.6 | - | - | 277/1 | 0.3 | 0.4 | 15 | 58 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 03 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13.1 | 115/1 | 0.6 | 17.1 | 20 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | 1-ROW HW | 18.5 | 1.3 | 2.4 | - | - | 115/1 | 0.6 | 0.8 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | 2-ROW HW | 30.4 | 2.1 | 11.1 | - | - | 115/1 | 0.6 | 0.8 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | 1-ROW HW | 18.5 | 1.3 | 2.4 | - | - | 277/1 | 0.3 | 0.4 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | 2-ROW HW | 30.4 | 2.1 | 11.1 | - | - | 277/1 | 0.3 | 0.4 | 15 | 65 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 04 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | NONE | - | - | - | - | - | 115/1 | 1.2 | 1.5 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.2 | 12.4 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 1.5 | 13.1 | 115/1 | 1.2 | 17.9 | 20 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.2 | 23.2 | 25 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.2 | 34.1 | 35 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | 1-ROW HW | 28.2 | 1.9 | 6 | - | - | 115/1 | 1.2 | 1.5 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | 2-ROW HW | 44.8 | 3.1 | 4.7 | - | - | 115/1 | 1.2 | 1.5 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | NONE | - | - | - | - | - | 277/1 | 0.6 | 0.8 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.6 | 5.2 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.6 | 7.5 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.6 | 9.8 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.6 | 14.2 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | 1-ROW HW | 28.2 | 1.9 | 6 | - | - | 277/1 | 0.6 | 0.8 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLC-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | 2-ROW HW | 44.8 | 3.1 | 4.7 | - | - | 277/1 | 0.6 | 0.8 | 15 | 77 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | CONCEALED | 06 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 90 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 90 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | 1-ROW HW | 9.2 | 0.6 | 0.6 | - | - | 115/1 | 0.6 | 0.8 | 15 | 90 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | 2-ROW HW | 15.4 | 1.1 | 2.6 | - | - | 115/1 | 0.6 | 0.8 | 15 | 90 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 90 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 90 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | 1-ROW HW | 9.2 | 0.6 | 0.6 | - | - | 277/1 | 0.3 | 0.4 | 15 | 90 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-02 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 200 | PSC | 1/25 | 3 | 6500 | 4300 | 1.6 | 11.7 | 2-ROW HW | 15.4 | 1.1 | 2.6 | - | - | 277/1 | 0.3 | 0.4 | 15 | 90 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 02 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | ELECTRIC | - | - | - | 1.5 | 13.1 | 115/1 | 0.6 | 17.1 | 20 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | 1-ROW HW | 13.4 | 0.9 | 1.2 | - | - | 115/1 | 0.6 | 0.8 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | 2-ROW HW | 22.4 | 1.5 | 5.6 | - | - | 115/1 | 0.6 | 0.8 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | 1-ROW HW | 13.4 | 0.9 | 1.2 | - | - | 277/1 | 0.3 | 0.4 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-03 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 300 | PSC | 1/25 | 3 | 9500 | 6500 | 2 | 3.4 | 2-ROW HW | 22.4 | 1.5 | 5.6 | - | - | 277/1 | 0.3 | 0.4 | 15 | 97 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13.1 | 115/1 | 0.6 | 17.1 | 20 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | 1-ROW HW | 18.5 | 1.3 | 2.4 | - | - | 115/1 | 0.6 | 0.8 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | 2-ROW HW | 30.4 | 2.1 | 11.1 | - | - | 115/1 | 0.6 | 0.8 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | 1-ROW HW | 18.5 | 1.3 | 2.4 | - | - | 277/1 | 0.3 | 0.4 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-04 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 400 | PSC | 1/25 | 3 | 14000 | 9500 | 2.9 | 7.4 | 2-ROW HW | 30.4 | 2.1 | 11.1 | - | - | 277/1 | 0.3 | 0.4 | 15 | 104 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | NONE | - | - | - | - | - | 115/1 | 1.2 | 1.5 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.2 | 12.4 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 1.5 | 13.1 | 115/1 | 1.2 | 17.9 | 20 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.2 | 23.2 | 25 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.2 | 34.1 | 35 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | 1-ROW HW | 28.2 | 1.9 | 6 | - | - | 115/1 | 1.2 | 1.5 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | 2-ROW HW | 44.8 | 3.1 | 4.7 | - | - | 115/1 | 1.2 | 1.5 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | NONE | - | - | - | - | - | 277/1 | 0.6 | 0.8 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.6 | 5.2 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.6 | 7.5 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.6 | 9.8 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.6 | 14.2 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | 1-ROW HW | 28.2 | 1.9 | 6 | - | - | 277/1 | 0.6 | 0.8 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | 1-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VLE-06 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | YES | 600 | PSC | (2) 1/25 | 3 | 20000 | 15000 | 5.2 | 9.9 | 2-ROW HW | 44.8 | 3.1 | 4.7 | - | - | 277/1 | 0.6 | 0.8 | 15 | 116 | VL LOW-PROFILE FLOOR-MOUNTED VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | 2-ROW HW | 3 | 0 |  | Enviro-Tec VF and VL Fan Coil Catalog ET115.26-EG9
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-03 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-04 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-06 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-08 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-10 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHC-12 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | CONCEALED WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-03 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-04 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-06 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-08 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-10 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHM-12 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | MASTER (A) WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-03 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-04 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-06 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-08 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-10 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHS-12 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | SLAVE (B) WITHOUT RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-03 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-04 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-06 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-08 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-10 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHA/VHB-12 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | TANDEM A/B WITH RISERS | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | PSC | 1/35 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 347 | ECM (3-SPEED) | 1/3 | 3 | 13560 | 9350 | 2.7 | 7.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 0.6 | 0.8 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.6 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.6 | 17 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.6 | 22.5 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.6 | 27.9 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.6 | 33.4 | 35 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.3 | 6.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.3 | 12.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.3 | 15.4 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.3 | 18.4 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 0.3 | 0.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.3 | 4.9 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.3 | 7.1 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.3 | 9.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.3 | 11.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | PSC | 1/35 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.3 | 13.9 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-03 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 337 | ECM (3-SPEED) | 1/3 | 4 | 16390 | 10780 | 3.3 | 12.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 03 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | PSC | 1/25 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 442 | ECM (3-SPEED) | 1/3 | 3 | 16700 | 11580 | 3.3 | 9.5 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 0.9 | 1.1 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 0.9 | 12 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 0.9 | 17.4 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 0.9 | 22.9 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 0.9 | 28.2 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 0.9 | 33.8 | 35 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 0.9 | 39.1 | 40 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 0.9 | 44.6 | 45 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.5 | 6.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.5 | 12.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.5 | 15.6 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.5 | 21.6 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.5 | 24.6 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | PSC | 1/25 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-04 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 427 | ECM (3-SPEED) | 1/3 | 4 | 20250 | 13400 | 4 | 15 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 218 | VH HI-RISE VERTICAL | EXPOSED CABINET | 04 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | PSC | 1/15 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 601 | ECM (3-SPEED) | 1/3 | 3 | 22620 | 15700 | 4.5 | 9 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 1.3 | 1.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 1.3 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 1.3 | 17.9 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 1.3 | 23.4 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 1.3 | 28.8 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 1.3 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 1.3 | 39.6 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 1.3 | 45.1 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 0.6 | 0.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.6 | 6.7 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.6 | 9.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.6 | 12.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.6 | 15.8 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.6 | 18.8 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.6 | 21.8 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.6 | 24.8 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.6 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.6 | 30.8 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 0.5 | 0.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.5 | 5.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.5 | 7.4 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.5 | 9.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.5 | 11.9 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.5 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.5 | 16.4 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.5 | 18.6 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.5 | 20.9 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | PSC | 1/15 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.5 | 23.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-06 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 588 | ECM (3-SPEED) | 1/3 | 4 | 27740 | 18370 | 5.5 | 14.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 06 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | PSC | 1/6 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 800 | ECM (3-SPEED) | 1/3 | 3 | 27760 | 19610 | 5.5 | 10.6 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.6 | 14.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.6 | 19.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.6 | 25 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.6 | 35.9 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.6 | 41.2 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.6 | 46.8 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 1 | 1.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 1 | 7.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 1 | 10.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 1 | 13.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 1 | 16.2 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 1 | 19.2 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 1 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 1 | 25.2 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 1 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 1 | 31.2 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 1 | 34.2 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 1 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 1 | 40.4 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 1 | 43.4 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 1 | 46.4 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 1 | 49.4 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 0.9 | 1.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 0.9 | 5.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 0.9 | 7.9 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 0.9 | 10.1 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 0.9 | 12.4 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 0.9 | 14.6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 0.9 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 0.9 | 19.1 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 0.9 | 21.4 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 0.9 | 23.8 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 0.9 | 26 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 0.9 | 28.2 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 0.9 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 0.9 | 32.8 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 0.9 | 35 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | PSC | 1/6 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 0.9 | 37.2 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-08 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 780 | ECM (3-SPEED) | 1/3 | 4 | 34420 | 23150 | 6.9 | 19.4 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 235 | VH HI-RISE VERTICAL | EXPOSED CABINET | 08 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | PSC | 1/5 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1006 | ECM (3-SPEED) | 1/3 | 3 | 37470 | 26030 | 7.5 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 2.7 | 3.4 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 2.7 | 14.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 2.7 | 19.6 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 2.7 | 25.1 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 2.7 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 2.7 | 36 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 2.7 | 41.4 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 2.7 | 46.9 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 0.8 | 1 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 0.8 | 7 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 0.8 | 10 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 0.8 | 13 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 0.8 | 16 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 0.8 | 19 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 0.8 | 22 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 0.8 | 25 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 0.8 | 28 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 0.8 | 31 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 0.8 | 34 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 0.8 | 37 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 0.8 | 40.1 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 0.8 | 43.1 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 0.8 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 0.8 | 49.1 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 0.8 | 52.1 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 0.8 | 55.1 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 1 | 1.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1 | 5.8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1 | 8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1 | 10.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1 | 14.8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1 | 17 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1 | 19.2 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1 | 23.9 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1 | 26.1 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1 | 28.4 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1 | 30.6 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1 | 32.9 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1 | 35.1 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1 | 37.4 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1 | 39.6 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1 | 41.9 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | PSC | 1/5 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1 | 46.4 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-10 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 990 | ECM (3-SPEED) | 1/3 | 4 | 43350 | 29350 | 8.7 | 7.7 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 10 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | PSC | 1/4 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | NONE | 3 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1238 | ECM (3-SPEED) | 1/3 | 3 | 43120 | 30410 | 8.5 | 10 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 3 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.9 | 6.1 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.9 | 17 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.9 | 22.4 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.9 | 27.9 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.9 | 33.2 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.9 | 38.8 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.9 | 44.1 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.9 | 49.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2 | 2.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2 | 8.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2 | 11.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2 | 17.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2 | 20.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2 | 26.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2 | 32.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2 | 35.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2 | 44.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2 | 47.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2 | 50.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2 | 53.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2 | 56.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 1.9 | 2.4 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 1.9 | 6.9 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 1.9 | 9.1 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 1.9 | 11.4 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 1.9 | 13.6 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 1.9 | 15.9 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 1.9 | 18.1 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 1.9 | 20.4 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 1.9 | 22.6 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 1.9 | 25 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 1.9 | 27.2 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 1.9 | 29.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 1.9 | 31.8 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 1.9 | 34 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 1.9 | 36.2 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 1.9 | 38.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 1.9 | 40.8 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 1.9 | 43 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 1.9 | 45.2 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | PSC | 1/4 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 1.9 | 47.5 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | PSC | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 115/1 | 4.8 | 6 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 8.7 | 115/1 | 4.8 | 16.9 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 13 | 115/1 | 4.8 | 22.2 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 17.4 | 115/1 | 4.8 | 27.8 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 21.7 | 115/1 | 4.8 | 33.1 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 26.1 | 115/1 | 4.8 | 38.6 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 30.4 | 115/1 | 4.8 | 44 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 34.8 | 115/1 | 4.8 | 49.5 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 115/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 208-230/1 | 2.8 | 3.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 4.8 | 208-230/1 | 2.8 | 9.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 7.2 | 208-230/1 | 2.8 | 12.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 9.6 | 208-230/1 | 2.8 | 15.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 12 | 208-230/1 | 2.8 | 18.5 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 14.4 | 208-230/1 | 2.8 | 21.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 16.8 | 208-230/1 | 2.8 | 24.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 19.2 | 208-230/1 | 2.8 | 27.5 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 21.6 | 208-230/1 | 2.8 | 30.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 24 | 208-230/1 | 2.8 | 33.5 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 26.4 | 208-230/1 | 2.8 | 36.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 28.8 | 208-230/1 | 2.8 | 39.5 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 31.3 | 208-230/1 | 2.8 | 42.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 33.7 | 208-230/1 | 2.8 | 45.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 36.1 | 208-230/1 | 2.8 | 48.6 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 38.5 | 208-230/1 | 2.8 | 51.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 40.9 | 208-230/1 | 2.8 | 54.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 43.3 | 208-230/1 | 2.8 | 57.6 | 60 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 208-230/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | NONE | - | - | - | - | - | 277/1 | 2.6 | 3.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | NONE | 4 | 0 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1 | 3.6 | 277/1 | 2.6 | 7.8 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 1.5 | 5.4 | 277/1 | 2.6 | 10 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 1.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2 | 7.2 | 277/1 | 2.6 | 12.2 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 2.5 | 9 | 277/1 | 2.6 | 14.5 | 15 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 2.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3 | 10.8 | 277/1 | 2.6 | 16.8 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 3.5 | 12.6 | 277/1 | 2.6 | 19 | 20 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 3.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4 | 14.4 | 277/1 | 2.6 | 21.2 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 4.5 | 16.2 | 277/1 | 2.6 | 23.5 | 25 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 4.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5 | 18.1 | 277/1 | 2.6 | 25.9 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 5.5 | 19.9 | 277/1 | 2.6 | 28.1 | 30 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 5.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6 | 21.7 | 277/1 | 2.6 | 30.4 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 6.5 | 23.5 | 277/1 | 2.6 | 32.6 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 6.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7 | 25.3 | 277/1 | 2.6 | 34.9 | 35 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 7.5 | 27.1 | 277/1 | 2.6 | 37.1 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 7.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8 | 28.9 | 277/1 | 2.6 | 39.4 | 40 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 8.5 | 30.7 | 277/1 | 2.6 | 41.6 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 8.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9 | 32.5 | 277/1 | 2.6 | 43.9 | 45 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 9.5 | 34.3 | 277/1 | 2.6 | 46.1 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 9.5 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5
ENVIRO-TEC | VHE-12 | VH HI-RISE VERTICAL | EXPOSED CABINET | YES | 1206 | ECM (3-SPEED) | 1/3 | 4 | 50540 | 34600 | 10 | 9.1 | ELECTRIC | - | - | - | 10 | 36.1 | 277/1 | 2.6 | 48.4 | 50 | 277 | VH HI-RISE VERTICAL | EXPOSED CABINET | 12 | ECM (3-SPEED) | 277/1 | ELECTRIC | 4 | 10 |  | Enviro-Tec VH Fan Coil Catalog ET115.26-EG5

## SCHEDULE NOTES
Provide with factory mounted piping package (2-way or 3-way valve, isolation and balancing) as scheduled.
Provide with unit mounted disconnect and main fusing.
Provide with MERV 8 filter.
Electric heat: single point power connection, primary auto-reset and secondary limits; size heater for leaving air below 104F and at least 70 CFM per kW.
MCA / MOP are calculated - verify with the Enviro-Tec MCA/MOP calculator (www.enviro-tec.com) before submittal.

## SOURCES
Enviro-Tec catalogs: HL ET115.26-EG10 (0425), HP ET115.26-EG3 (0825), CDV ET115.26-EG8 (0825), VF/VL ET115.26-EG9 (0222), VH ET115.26-EG5 (0425).
One row per model x size x cooling coil rows x motor (PSC / ECM 3-speed) x voltage x heating option. Electric heat sizes fold into a kW dropdown on the site.
Cooling: AHRI 440 ratings as printed (80/67F EAT, 45F EWT, 10F rise, high speed, dry-coil airflow). Rating motor: PSC 115/1/60 for HL, CDV, VH; ECM 115/1/60 at 0.20" ESP for HP; VF/VL conditions not printed. ECM rows show the same catalog ratings - ECM capacity varies; confirm in ETI Solution Navigator.
CDV cooling capacities are printed as MBH under a BTUH header and were multiplied by 1000. CDV sizes 16 and 20 are not AHRI 440 certified (airflow above the AHRI 440 maximum).
HW heating (1- and 2-row): HL, HP: 70F EAT, 180F EWT, 40F drop; CDV: 70F EAT, 180F EWT, 20F drop; VF: 40F drop; VL: 30F drop; all high fan speed.
Not published, so not offered as rows: HW heating for HPE and for all VH models; electric heat for HLF and HPF; EC motors for HLF and VL.
Electric heat: heater amps from the selection charts for the row motor (PSC / ECM 3-speed chart) and voltage; 208-230 V rows use the 208 V amps and the kW steps offered at 208 V. Only the kW steps the charts show as available are listed.
MCA / MOP calculated: MCA = 1.25 x (motor FLA + heater amps); MOP = next standard fuse size at or above MCA, 15 A minimum. Heaters whose calculated MCA exceeds the 90 A lineblock maximum are left out. Verify with the Enviro-Tec MCA/MOP calculator.
Motor HP / FLA: high-speed nameplate data (VH PSC is listed at medium speed in the catalog); 208-230 V uses the higher of the printed 208 / 230 V values. HL, VF and VL PSC motors are 115 V and 277 V only.
Weights: base unit without coils (coil weights are extra - see the catalogs).
VHM model meaning is inferred (master A unit with risers serving a VHS B unit) - confirm with Enviro-Tec.
Motor FLA blank in the catalog (MCA / MOP shown as -): HP HPE-08 PSC, HP HPE-14 PSC, HP HPF-08 PSC, HP HPF-14 PSC, HP HPP-08 PSC, HP HPP-14 PSC