## SCHEDULE
SCHEDULE RANGE | [24 empty] | FILTERS | [5 empty] | DOCUMENTATION
PACKAGED ROOFTOP UNITS | [24 empty] | SIZE | ELECTRICAL | EFFICIENCY | COOLING STAGES | HIGH/MEDIUM/LOW GAS HEAT | HGRH | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL
MAKE | MODEL NUMBER | NOM TONS | Fan Data |  |  | Cooling Performance | [6 empty] | Heating Performance |  |  |  |  | MODULATING HOT GAS REHEAT | COOLING STAGES | Electrical Data |  |  |  | Weight (lbs)
|  |  | CFM | ESP (IWG) | TESP (IWG) | TOTAL CAPACITY (BTU/h) | SENSIBLE CAPACITY (BTU/h) | EFFICIENCY (AT AHRI) | EDB (°F) | EWB (°F) | LDB (°F) | LWB (°F) | INPUT (MBH) | OUTPUT (MBH) | Stages | EAT (°F) | LAT (°F) |  |  | VOLT/PH | INDOOR MOTOR HP | Unit MCA | Unit MOCP
TEMPMASTER | KJ037N06D2BEAAA5A1 | 3 | 1200 | 1.5 |  | 38000 | 27500 | 14.7 SEER2/12.5 EER2 | 80 | 67 | 58.8 | 57 | 60 | 49 |  | 60 | 97.8 | NO |  | 208/3 | 1.5 | 22.7 | 30 | 925 | 3 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ037N08D2BEAAA5A1 | 3 | 1200 | 1.5 |  | 38000 | 27500 | 14.7 SEER2/12.5 EER2 | 80 | 67 | 58.8 | 57 | 80 | 65 |  | 60 | 110.2 | NO |  | 208/3 | 1.5 | 22.7 | 30 | 925 | 3 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | KJ037N06D4BEAAA5A1 | 3 | 1200 | 1.5 |  | 38000 | 27500 | 14.7 SEER2/12.5 EER2 | 80 | 67 | 58.8 | 57 | 60 | 49 |  | 60 | 97.8 | NO |  | 460/3 | 1.5 | 10 | 15 | 925 | 3 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ037N08D4BEAAA5A1 | 3 | 1200 | 1.5 |  | 38000 | 27500 | 14.7 SEER2/12.5 EER2 | 80 | 67 | 58.8 | 57 | 80 | 65 |  | 60 | 110.2 | NO |  | 460/3 | 1.5 | 10 | 15 | 925 | 3 | 460/3 | STANDARD |  | HIGH | NO
TEMPMASTER | KJ049N06D2BEAAA5A1 | 4 | 1600 | 1.5 |  | 51400 | 36900 | 14.7 SEER2/12.3 EER2 | 80 | 67 | 58.6 | 56.7 | 60 | 49 |  | 60 | 88.4 | NO |  | 208/3 | 1.5 | 22 | 30 | 960 | 4 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ049N08D2BEAAA5A1 | 4 | 1600 | 1.5 |  | 51400 | 36900 | 14.7 SEER2/12.3 EER2 | 80 | 67 | 58.6 | 56.7 | 80 | 65 |  | 60 | 97.6 | NO |  | 208/3 | 1.5 | 22 | 30 | 960 | 4 | 208/3 | STANDARD |  | MEDIUM | NO
TEMPMASTER | KJ049N12D2BEAAA5A1 | 4 | 1600 | 1.5 |  | 51400 | 36900 | 14.7 SEER2/12.3 EER2 | 80 | 67 | 58.6 | 56.7 | 120 | 97 |  | 60 | 116.1 | NO |  | 208/3 | 1.5 | 22 | 30 | 960 | 4 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | KJ049N06D4BEAAA5A1 | 4 | 1600 | 1.5 |  | 51400 | 36900 | 14.7 SEER2/12.3 EER2 | 80 | 67 | 58.6 | 56.7 | 60 | 49 |  | 60 | 88.4 | NO |  | 460/3 | 1.5 | 11.6 | 15 | 960 | 4 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ049N08D4BEAAA5A1 | 4 | 1600 | 1.5 |  | 51400 | 36900 | 14.7 SEER2/12.3 EER2 | 80 | 67 | 58.6 | 56.7 | 80 | 65 |  | 60 | 97.6 | NO |  | 460/3 | 1.5 | 11.6 | 15 | 960 | 4 | 460/3 | STANDARD |  | MEDIUM | NO
TEMPMASTER | KJ061N08D2BEAAA5A1 | 5 | 2000 | 1.5 |  | 65300 | 46700 | 14.7 SEER2/12.5 EER2 | 80 | 67 | 58.4 | 56.6 | 80 | 65 |  | 60 | 90.1 | NO |  | 208/3 | 2 | 29.6 | 40 | 955 | 5 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ061N12D2BEAAA5A1 | 5 | 2000 | 1.5 |  | 65300 | 46700 | 14.7 SEER2/12.5 EER2 | 80 | 67 | 58.4 | 56.6 | 120 | 97 |  | 60 | 104.9 | NO |  | 208/3 | 2 | 29.6 | 40 | 955 | 5 | 208/3 | STANDARD |  | MEDIUM | NO
TEMPMASTER | KJ061N16D2BEAAA5A1 | 5 | 2000 | 1.5 |  | 65300 | 46700 | 14.7 SEER2/12.5 EER2 | 80 | 67 | 58.4 | 56.6 | 160 | 130 |  | 60 | 120.2 | NO |  | 208/3 | 2 | 29.6 | 40 | 975 | 5 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | KJ078N12R2BEAAA5A1 | 6.5 | 2600 | 1.5 |  | 79800 | 56500 | 15.8 IEER/12 EER | 80 | 67 | 59.9 | 57.3 | 120 | 97 |  | 60 | 94.5 | NO |  | 208/3 | 2 | 32.6 | 40 | 1225 | 6.5 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ078N18R2BEAAA5A1 | 6.5 | 2600 | 1.5 |  | 79800 | 56500 | 15.8 IEER/12 EER | 80 | 67 | 59.9 | 57.3 | 180 | 146 |  | 60 | 112 | NO |  | 208/3 | 2 | 32.6 | 40 | 1225 | 6.5 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | KJ090N12R2BEAAA5A1 | 7.5 | 3000 | 1.5 |  | 94500 | 67700 | 15.8 IEER/12.2 EER | 80 | 67 | 59.1 | 56.9 | 120 | 97 |  | 60 | 89.9 | NO |  | 208/3 | 3 | 47.7 | 60 | 1245 | 7.5 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ090N18R2BEAAA5A1 | 7.5 | 3000 | 1.5 |  | 94500 | 67700 | 15.8 IEER/12.2 EER | 80 | 67 | 59.1 | 56.9 | 180 | 146 |  | 60 | 105.1 | NO |  | 208/3 | 3 | 47.7 | 60 | 1245 | 7.5 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | KJ102N12R2BEAAA5A1 | 8.5 | 3400 | 1.37 |  | 103900 | 75800 | 14.6 IEER/12 EER | 80 | 67 | 59.4 | 57.3 | 120 | 97 |  | 60 | 86.4 | NO |  | 208/3 | 3 | 46.1 | 50 | 1245 | 8.5 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ102N18R2BEAAA5A1 | 8.5 | 3400 | 1.37 |  | 103900 | 75800 | 14.6 IEER/12 EER | 80 | 67 | 59.4 | 57.3 | 180 | 146 |  | 60 | 99.8 | NO |  | 208/3 | 3 | 46.1 | 50 | 1245 | 8.5 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | KJ120N18R2BEAAA5A1 | 10 | 4000 | 1.42 |  | 126700 | 89500 | 15 IEER/12.2 EER | 80 | 67 | 59.3 | 56.9 | 180 | 146 |  | 60 | 93.8 | NO |  | 208/3 | 3 | 54.8 | 70 | 1265 | 10 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ120N24R2BEAAA5A1 | 10 | 4000 | 1.42 |  | 126700 | 89500 | 15 IEER/12.2 EER | 80 | 67 | 59.3 | 56.9 | 240 | 194 |  | 60 | 104.9 | NO |  | 208/3 | 3 | 54.8 | 70 | 1275 | 10 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | KJ150N18R2BEAAA5A1 | 12.5 | 5000 | 1.18 |  | 168000 | 114900 | 15.2 IEER/12 EER | 80 | 67 | 58.7 | 56.3 | 180 | 146 |  | 60 | 87 | NO |  | 208/3 | 5 | 77.4 | 90 | 1475 | 12.5 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | KJ150N24R2BEAAA5A1 | 12.5 | 5000 | 1.18 |  | 168000 | 114900 | 15.2 IEER/12 EER | 80 | 67 | 58.7 | 56.3 | 240 | 194 |  | 60 | 95.9 | NO |  | 208/3 | 5 | 77.4 | 90 | 1485 | 12.5 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV15N1DP2E1AAN82A1 | 15 | 6000 | 1.5 |  | 182000 | 136500 | 14 IEER/10.9 EER | 80 | 67 | 58.9 | 57.4 | 220 | 178.2 |  | 60 | 87.5 | NO |  | 208/3 | 5 | 80.9 | 100 | 2115 | 15 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV15N3DP2E1AAN82A1 | 15 | 6000 | 1.5 |  | 182000 | 136500 | 14 IEER/10.9 EER | 80 | 67 | 58.9 | 57.4 | 400 | 324 |  | 60 | 110 | NO |  | 208/3 | 5 | 80.9 | 100 | 2115 | 15 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV15N3DP4E1AAN82A1 | 15 | 6000 | 1.5 |  | 182000 | 136500 | 14 IEER/10.9 EER | 80 | 67 | 58.9 | 57.4 | 400 | 324 |  | 60 | 110 | NO |  | 460/3 | 5 | 39.6 | 50 | 2115 | 15 | 460/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV18N1DP2E1AAN82A1 | 17.5 | 7000 | 1.5 |  | 214500 | 158300 | 14 IEER/10.8 EER | 80 | 67 | 59.1 | 57.3 | 220 | 178.2 |  | 60 | 83.6 | NO |  | 208/3 | 7.5 | 102.7 | 125 | 2200 | 17.5 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV18N3DP2E1AAN82A1 | 17.5 | 7000 | 1.5 |  | 214500 | 158300 | 14 IEER/10.8 EER | 80 | 67 | 59.1 | 57.3 | 400 | 324 |  | 60 | 102.9 | NO |  | 208/3 | 7.5 | 102.7 | 125 | 2200 | 17.5 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV18N1DP4E1AAN82A1 | 17.5 | 7000 | 1.5 |  | 214500 | 158300 | 14 IEER/10.8 EER | 80 | 67 | 59.1 | 57.3 | 220 | 178.2 |  | 60 | 83.6 | NO |  | 460/3 | 7.5 | 50.6 | 60 | 2200 | 17.5 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV18N3DP4E1AAN82A1 | 17.5 | 7000 | 1.5 |  | 214500 | 158300 | 14 IEER/10.8 EER | 80 | 67 | 59.1 | 57.3 | 400 | 324 |  | 60 | 102.9 | NO |  | 460/3 | 7.5 | 50.6 | 60 | 2200 | 17.5 | 460/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV20N1DP2E1AAN82A1 | 20 | 8000 | 1.5 |  | 255400 | 171000 | 14 IEER/10.8 EER | 80 | 67 | 60.2 | 56.8 | 220 | 178.2 |  | 60 | 80.6 | NO |  | 208/3 | 7.5 | 119.6 | 150 | 2300 | 20 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV20N3DP2E1AAN82A1 | 20 | 8000 | 1.5 |  | 255400 | 171000 | 14 IEER/10.8 EER | 80 | 67 | 60.2 | 56.8 | 400 | 324 |  | 60 | 97.5 | NO |  | 208/3 | 7.5 | 119.6 | 150 | 2300 | 20 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV20N1DP4E1AAN82A1 | 20 | 8000 | 1.5 |  | 255400 | 171000 | 14 IEER/10.8 EER | 80 | 67 | 60.2 | 56.8 | 220 | 178.2 |  | 60 | 80.6 | NO |  | 460/3 | 7.5 | 58.8 | 70 | 2300 | 20 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV20N3DP4E1AAN82A1 | 20 | 8000 | 1.5 |  | 255400 | 171000 | 14 IEER/10.8 EER | 80 | 67 | 60.2 | 56.8 | 400 | 324 |  | 60 | 97.5 | NO |  | 460/3 | 7.5 | 58.8 | 70 | 2300 | 20 | 460/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV25N1DP2E1AAN82A1 | 25 | 10000 | 1.5 |  | 309600 | 218800 | 13.8 IEER/10 EER | 80 | 67 | 59.7 | 57.2 | 220 | 178.2 |  | 60 | 76.5 | NO |  | 208/3 | 10 | 139.9 | 175 | 2485 | 25 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV25N3DP2E1AAN82A1 | 25 | 10000 | 1.5 |  | 309600 | 218800 | 13.8 IEER/10 EER | 80 | 67 | 59.7 | 57.2 | 400 | 324 |  | 60 | 90 | NO |  | 208/3 | 10 | 139.9 | 175 | 2485 | 25 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV25N1DP4E1AAN82A1 | 25 | 10000 | 1.5 |  | 309600 | 218800 | 13.8 IEER/10 EER | 80 | 67 | 59.7 | 57.2 | 220 | 178.2 |  | 60 | 76.5 | NO |  | 460/3 | 10 | 67.1 | 80 | 2480 | 25 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV25N3DP4E1AAN82A1 | 25 | 10000 | 1.5 |  | 309600 | 218800 | 13.8 IEER/10 EER | 80 | 67 | 59.7 | 57.2 | 400 | 324 |  | 60 | 90 | NO |  | 460/3 | 10 | 67.1 | 80 | 2480 | 25 | 460/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV28N1DP2E1AAN82A1 | 27.5 | 11000 | 1.5 |  | 346400 | 248000 | 13.2 IEER/10.2 EER | 80 | 67 | 59.1 | 57 | 220 | 178.2 |  | 60 | 75 | NO |  | 208/3 | 12 | 147.5 | 175 | 2565 | 27.5 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV28N3DP2E1AAN82A1 | 27.5 | 11000 | 1.5 |  | 346400 | 248000 | 13.2 IEER/10.2 EER | 80 | 67 | 59.1 | 57 | 400 | 324 |  | 60 | 87.3 | NO |  | 208/3 | 12 | 147.5 | 175 | 2565 | 27.5 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | LV28N1DP4E1AAN82A1 | 27.5 | 11000 | 1.5 |  | 346400 | 248000 | 13.2 IEER/10.2 EER | 80 | 67 | 59.1 | 57 | 220 | 178.2 |  | 60 | 75 | NO |  | 460/3 | 12 | 73.5 | 90 | 2565 | 27.5 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | LV28N3DP4E1AAN82A1 | 27.5 | 11000 | 1.5 |  | 346400 | 248000 | 13.2 IEER/10.2 EER | 80 | 67 | 59.1 | 57 | 400 | 324 |  | 60 | 87.3 | NO |  | 460/3 | 12 | 73.5 | 90 | 2565 | 27.5 | 460/3 | STANDARD |  | HIGH | NO
TEMPMASTER | RV30N1DP2C1AAN12A1 | 30 | 12000 | 1.5 |  | 351300 | 266300 | 14 IEER/10.6 EER | 80 | 67 | 59.5 | 57.8 | 400 | 324 |  | 60 | 85 | NO |  | 208/3 | 15 | 168.9 | 200 | 4942 | 30 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | RV30N3DP2C1AAN12A1 | 30 | 12000 | 1.5 |  | 351300 | 266300 | 14 IEER/10.6 EER | 80 | 67 | 59.5 | 57.8 | 620 | 502.2 |  | 60 | 98.8 | NO |  | 208/3 | 15 | 168.9 | 200 | 4942 | 30 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | RV30N1DP4C1AAN12A1 | 30 | 12000 | 1.5 |  | 351300 | 266300 | 14 IEER/10.6 EER | 80 | 67 | 59.5 | 57.8 | 400 | 324 |  | 60 | 85 | NO |  | 460/3 | 15 | 82.5 | 100 | 4938 | 30 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | RV30N3DP4C1AAN12A1 | 30 | 12000 | 1.5 |  | 351300 | 266300 | 14 IEER/10.6 EER | 80 | 67 | 59.5 | 57.8 | 620 | 502.2 |  | 60 | 98.8 | NO |  | 460/3 | 15 | 82.5 | 100 | 4938 | 30 | 460/3 | STANDARD |  | HIGH | NO
TEMPMASTER | RV35N1DP2C1AAN12A1 | 35 | 14000 | 1.5 |  | 432000 | 335300 | 14.8 IEER/11 EER | 80 | 67 | 57.8 | 57.2 | 400 | 324 |  | 60 | 81.4 | NO |  | 208/3 | 15 | 178.6 | 225 | 5090 | 35 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | RV35N3DP2C1AAN12A1 | 35 | 14000 | 1.5 |  | 432000 | 335300 | 14.8 IEER/11 EER | 80 | 67 | 57.8 | 57.2 | 800 | 648 |  | 60 | 102.9 | NO |  | 208/3 | 15 | 178.6 | 225 | 5090 | 35 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | RV35N1DP4C1AAN12A1 | 35 | 14000 | 1.5 |  | 432000 | 335300 | 14.8 IEER/11 EER | 80 | 67 | 57.8 | 57.2 | 400 | 324 |  | 60 | 81.4 | NO |  | 460/3 | 15 | 91.5 | 110 | 5086 | 35 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | RV35N3DP4C1AAN12A1 | 35 | 14000 | 1.5 |  | 432000 | 335300 | 14.8 IEER/11 EER | 80 | 67 | 57.8 | 57.2 | 800 | 648 |  | 60 | 102.9 | NO |  | 460/3 | 15 | 91.5 | 110 | 5086 | 35 | 460/3 | STANDARD |  | HIGH | NO
TEMPMASTER | RV40N1DP2C1AAN12A1 | 40 | 16000 | 1.5 |  | 449700 | 373300 | 15.2 IEER/10.5 EER | 80 | 67 | 58.4 | 58.1 | 400 | 324 |  | 60 | 78.8 | NO |  | 208/3 | 20 | 197.5 | 250 | 6779 | 40 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | RV40N3DP2C1AAN12A1 | 40 | 16000 | 1.5 |  | 449700 | 373300 | 15.2 IEER/10.5 EER | 80 | 67 | 58.4 | 58.1 | 800 | 648 |  | 60 | 97.5 | NO |  | 208/3 | 20 | 197.5 | 250 | 6779 | 40 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | RV40N1DP4C1AAN12A1 | 40 | 16000 | 1.5 |  | 449700 | 373300 | 15.2 IEER/10.5 EER | 80 | 67 | 58.4 | 58.1 | 400 | 324 |  | 60 | 78.8 | NO |  | 460/3 | 20 | 97.5 | 125 | 6775 | 40 | 460/3 | STANDARD |  | LOW | NO
TEMPMASTER | RV50N1DP2C1AAN12A1 | 50 | 20000 | 1.1 |  | 603700 | 454400 | 15.1 IEER/10.4 EER | 80 | 67 | 59 | 57.4 | 400 | 324 |  | 60 | 75 | NO |  | 208/3 | 20 | 272.4 | 325 | 7045 | 50 | 208/3 | STANDARD |  | LOW | NO
TEMPMASTER | RV50N3DP2C1AAN12A1 | 50 | 20000 | 1.1 |  | 603700 | 454400 | 15.1 IEER/10.4 EER | 80 | 67 | 59 | 57.4 | 800 | 648 |  | 60 | 90 | NO |  | 208/3 | 20 | 272.4 | 325 | 7045 | 50 | 208/3 | STANDARD |  | HIGH | NO
TEMPMASTER | RV50N1DP4C1AAN12A1 | 50 | 20000 | 1.1 |  | 603700 | 454400 | 15.1 IEER/10.4 EER | 80 | 67 | 59 | 57.4 | 400 | 324 |  | 60 | 75 | NO |  | 460/3 | 20 | 121.6 | 150 | 7041 | 50 | 460/3 | STANDARD |  | LOW | NO

## SCHEDULE NOTES
Provide with economizer with enthalpy sensor
Provide with factory installed disconnect
Provide with factory installed, field powered 115V GFCI outlet
Provide with 7-day programmable thermostat
Provide with 7-day programmable BACnet thermostat
Provide with factory installed DDC controller with BAS input and 7-day programmable thermostat
Provide with 24" factory roofcurb