## SCHEDULE
SCHEDULE RANGE | [25 empty] | FILTERS | [5 empty] | DOCUMENTATION
VERTICAL WALL MOUNTED CLASSROOM HEAT PUMPS | [25 empty] | SERIES | SIZE | ELECTRICAL | HEAT EXCHANGER | VENTILATION | ELECTRIC HEAT | SUBMITTAL | ENGINEERING MANUAL | PRODUCT DATA SHEET
MAKE | MODEL NUMBER | SERIES | NOM TONS | HEAT EXCHANGER | SUPPLY CFM | Ventilation |  | Cooling (95°F OA, 80/67°F RA) |  |  |  |  | Heat Pump Heating (70°F RA) |  |  |  | PTC HEATER (KW) | Electrical Data |  |  | SOUND (dBA) | REFRIGERANT | CHARGE (LBS) | Weight (lbs) | W x D x H (IN)
[6 empty] | OPTION | FRESH AIR (CFM) | TOTAL CAPACITY (BTU/h) | SENSIBLE CAPACITY (BTU/h) | EER | IEER | VARIABLE CAPACITY RANGE (BTU/h) | CAPACITY @ 47°F (BTU/h) | COP @ 47°F | MAX CAPACITY @ 20°F (BTU/h) | MAX CAPACITY @ 0°F (BTU/h) |  | VOLT/PH | Unit MCA | Unit MOCP
AIRSYS | CV36N3C-AEWBXG-C00XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 0 | 208-230/1 | 30 | 45 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-AEWBXG-C05XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 5 | 208-230/1 | 57 | 70 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-AEWBXG-C10XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 10 | 208-230/1 | 84 | 90 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-AEWBXG-R00XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 0 | 208-230/1 | 30 | 45 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-AEWBXG-R05XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 5 | 208-230/1 | 57 | 70 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-AEWBXG-R10XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 10 | 208-230/1 | 84 | 90 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-ADWBXG-C00XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 208-230/1 | 30 | 45 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-ADWBXG-C05XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 208-230/1 | 57 | 70 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-ADWBXG-C10XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 208-230/1 | 84 | 90 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-ADWBXG-R00XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 208-230/1 | 30 | 45 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-ADWBXG-R05XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 208-230/1 | 57 | 70 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-ADWBXG-R10XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 208-230/1 | 84 | 90 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BEWBXG-C00XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 0 | 208-230/3 | 20 | 30 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BEWBXG-C05XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 5 | 208-230/3 | 35 | 40 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BEWBXG-C10XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 10 | 208-230/3 | 51 | 60 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BEWBXG-R00XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 0 | 208-230/3 | 20 | 30 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BEWBXG-R05XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 5 | 208-230/3 | 35 | 40 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BEWBXG-R10XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 10 | 208-230/3 | 51 | 60 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BDWBXG-C00XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 208-230/3 | 20 | 30 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BDWBXG-C05XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 208-230/3 | 35 | 40 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BDWBXG-C10XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 208-230/3 | 51 | 60 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BDWBXG-R00XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 208-230/3 | 20 | 30 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BDWBXG-R05XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 208-230/3 | 35 | 40 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-BDWBXG-R10XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 33000 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 208-230/3 | 51 | 60 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CEWBXG-C00XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 0 | 460/3 | 10 | 15 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CEWBXG-C05XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 5 | 460/3 | 18 | 20 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CEWBXG-C10XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 10 | 460/3 | 26 | 30 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CEWBXG-R00XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 0 | 460/3 | 10 | 15 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CEWBXG-R05XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 5 | 460/3 | 18 | 20 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CEWBXG-R10XX | FOCUS IQ (INDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 29000 | 21500 | 10 | 460/3 | 26 | 30 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CDWBXG-C00XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 460/3 | 10 | 15 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CDWBXG-C05XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 460/3 | 18 | 20 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CDWBXG-C10XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | COMMERCIAL ROOM VENTILATOR | 360-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 460/3 | 26 | 30 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CDWBXG-R00XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 460/3 | 10 | 15 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CDWBXG-R05XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 460/3 | 18 | 20 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36N3C-CDWBXG-R10XX | FOCUS IQ (INDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1080 | ENERGY RECOVERY VENTILATOR | 80-450 | 32400 | 24900 | 11 | 20 | 16,200-40,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 460/3 | 26 | 30 | 41 | R-454B | 9.5 | 978 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-AEWBXG-C00XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 0 | 208-230/1 | 41 | 60 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-AEWBXG-C06XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 6 | 208-230/1 | 74 | 90 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-AEWBXG-C12XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 12 | 208-230/1 | 106 | 110 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-AEWBXG-R00XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 0 | 208-230/1 | 41 | 60 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-AEWBXG-R06XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 6 | 208-230/1 | 74 | 90 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-AEWBXG-R12XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 12 | 208-230/1 | 106 | 110 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-ADWBXG-C00XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 208-230/1 | 41 | 60 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-ADWBXG-C06XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 208-230/1 | 74 | 90 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-ADWBXG-C12XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 208-230/1 | 106 | 110 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-ADWBXG-R00XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 208-230/1 | 41 | 60 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-ADWBXG-R06XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 208-230/1 | 74 | 90 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-ADWBXG-R12XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 208-230/1 | 106 | 110 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BEWBXG-C00XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 0 | 208-230/3 | 27 | 40 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BEWBXG-C06XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 6 | 208-230/3 | 46 | 50 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BEWBXG-C12XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 12 | 208-230/3 | 65 | 70 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BEWBXG-R00XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 0 | 208-230/3 | 27 | 40 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BEWBXG-R06XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 6 | 208-230/3 | 46 | 50 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BEWBXG-R12XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 12 | 208-230/3 | 65 | 70 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BDWBXG-C00XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 208-230/3 | 27 | 40 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BDWBXG-C06XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 208-230/3 | 46 | 50 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BDWBXG-C12XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 208-230/3 | 65 | 70 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BDWBXG-R00XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 208-230/3 | 27 | 40 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BDWBXG-R06XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 208-230/3 | 46 | 50 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-BDWBXG-R12XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 208-230/3 | 65 | 70 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CEWBXG-C00XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 0 | 460/3 | 15 | 20 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CEWBXG-C06XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 6 | 460/3 | 24 | 30 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CEWBXG-C12XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 12 | 460/3 | 34 | 35 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CEWBXG-R00XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 0 | 460/3 | 15 | 20 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CEWBXG-R06XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 6 | 460/3 | 24 | 30 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CEWBXG-R12XX | FOCUS IQ (INDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 50800 | 35300 | 12 | 460/3 | 34 | 35 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CDWBXG-C00XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 460/3 | 15 | 20 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CDWBXG-C06XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 460/3 | 24 | 30 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CDWBXG-C12XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 360-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 460/3 | 34 | 35 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CDWBXG-R00XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 460/3 | 15 | 20 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CDWBXG-R06XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 460/3 | 24 | 30 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV60N3C-CDWBXG-R12XX | FOCUS IQ (INDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 80-450 | 52500 | 39600 | 11 | 20 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 460/3 | 34 | 35 | 44 | R-454B | 12.8 | 1072 | 48-1/16 x 29-1/2 x 94-1/2 | FOCUS IQ (INDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys Focus IQ Indoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-C00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 0 | 208-230/1 | 28 | 45 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-C05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 5 | 208-230/1 | 54 | 60 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-C10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 10 | 208-230/1 | 82 | 90 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-R00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 0 | 208-230/1 | 28 | 45 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-R05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 5 | 208-230/1 | 54 | 60 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-R10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 10 | 208-230/1 | 82 | 90 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-E00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 0 | 208-230/1 | 28 | 45 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-E05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 5 | 208-230/1 | 54 | 60 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-AEWBXX-E10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 10 | 208-230/1 | 82 | 90 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-C00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 0 | 208-230/1 | 28 | 45 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-C05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 5 | 208-230/1 | 54 | 60 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-C10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 10 | 208-230/1 | 82 | 90 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-R00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 0 | 208-230/1 | 28 | 45 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-R05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 5 | 208-230/1 | 54 | 60 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-R10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 10 | 208-230/1 | 82 | 90 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-E00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 0 | 208-230/1 | 28 | 45 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-E05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 5 | 208-230/1 | 54 | 60 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-ADWBXX-E10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 10 | 208-230/1 | 82 | 90 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-C00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 0 | 208-230/3 | 18 | 25 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-C05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 5 | 208-230/3 | 33 | 40 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-C10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 10 | 208-230/3 | 49 | 50 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-R00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 0 | 208-230/3 | 18 | 25 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-R05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 5 | 208-230/3 | 33 | 40 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-R10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 10 | 208-230/3 | 49 | 50 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-E00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 0 | 208-230/3 | 18 | 25 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-E05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 5 | 208-230/3 | 33 | 40 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BEWBXX-E10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 29000 | 20700 | 10 | 208-230/3 | 49 | 50 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-C00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 0 | 208-230/3 | 18 | 25 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-C05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 5 | 208-230/3 | 33 | 40 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-C10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 10 | 208-230/3 | 49 | 50 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-R00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 0 | 208-230/3 | 18 | 25 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-R05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 5 | 208-230/3 | 33 | 40 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-R10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 10 | 208-230/3 | 49 | 50 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-E00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 0 | 208-230/3 | 18 | 25 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-E05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 5 | 208-230/3 | 33 | 40 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-BDWBXX-E10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 33000 | 24900 | 11 | 21.5 | 16,200-39,900 | 34000 | 3.5 | 21200 | 11000 | 10 | 208-230/3 | 49 | 50 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-C00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 0 | 460/3 | 9 | 10 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-C05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 5 | 460/3 | 18 | 20 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-C10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 10 | 460/3 | 26 | 30 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-R00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 0 | 460/3 | 9 | 10 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-R05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 5 | 460/3 | 18 | 20 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-R10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 10 | 460/3 | 26 | 30 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-E00XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 0 | 460/3 | 9 | 10 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-E05XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 5 | 460/3 | 18 | 20 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CEWBXX-E10XX | BACKPACK (OUTDOOR) | 3 | EVI (ENHANCED WINTER HEATING) | 1150 | ECONOMIZER | 0-830 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 29000 | 20700 | 10 | 460/3 | 26 | 30 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-C00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 460/3 | 9 | 10 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-C05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 460/3 | 18 | 20 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-C10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | COMMERCIAL ROOM VENTILATOR | 100-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 460/3 | 26 | 30 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-R00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 460/3 | 9 | 10 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-R05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 460/3 | 18 | 20 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-R10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ENERGY RECOVERY VENTILATOR | 200-450 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 460/3 | 26 | 30 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-E00XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 0 | 460/3 | 9 | 10 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-E05XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 5 | 460/3 | 18 | 20 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 5 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV36H2C-CDWBXX-E10XX | BACKPACK (OUTDOOR) | 3 | DEHUM (HOT GAS REHEAT) | 1150 | ECONOMIZER | 0-830 | 32400 | 24900 | 11 | 20 | 16,200-39,900 | 34000 | 3.3 | 21200 | 11000 | 10 | 460/3 | 26 | 30 | 44 | R-454B | 8.8 | 730 | 45-5/8 x 27-9/16 x 85-7/8 | BACKPACK (OUTDOOR) | 3 | 460/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 10 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-C00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 0 | 208-230/1 | 42 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-C06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 6 | 208-230/1 | 74 | 90 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-C12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 12 | 208-230/1 | 108 | 120 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-R00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 0 | 208-230/1 | 42 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-R06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 6 | 208-230/1 | 74 | 90 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-R12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 12 | 208-230/1 | 108 | 120 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-E00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 0 | 208-230/1 | 42 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-E06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 6 | 208-230/1 | 74 | 90 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-AEWBXX-E12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 12 | 208-230/1 | 108 | 120 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-C00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 0 | 208-230/1 | 42 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-C06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 6 | 208-230/1 | 74 | 90 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-C12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 12 | 208-230/1 | 108 | 120 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-R00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 0 | 208-230/1 | 42 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-R06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 6 | 208-230/1 | 74 | 90 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-R12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 12 | 208-230/1 | 108 | 120 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-E00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 0 | 208-230/1 | 42 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-E06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 6 | 208-230/1 | 74 | 90 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-ADWBXX-E12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 12 | 208-230/1 | 108 | 120 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/1 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-C00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 0 | 208-230/3 | 27 | 40 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-C06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 6 | 208-230/3 | 45 | 50 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-C12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 12 | 208-230/3 | 65 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-R00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 0 | 208-230/3 | 27 | 40 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-R06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 6 | 208-230/3 | 45 | 50 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-R12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 12 | 208-230/3 | 65 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-E00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 0 | 208-230/3 | 27 | 40 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-E06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 6 | 208-230/3 | 45 | 50 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BEWBXX-E12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 50900 | 35300 | 12 | 208-230/3 | 65 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-C00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 0 | 208-230/3 | 27 | 40 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-C06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 6 | 208-230/3 | 45 | 50 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-C12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 12 | 208-230/3 | 65 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-R00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 0 | 208-230/3 | 27 | 40 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-R06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 6 | 208-230/3 | 45 | 50 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-R12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 12 | 208-230/3 | 65 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-E00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 0 | 208-230/3 | 27 | 40 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-E06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 6 | 208-230/3 | 45 | 50 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-BDWBXX-E12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 53000 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.5 | 33800 | 17500 | 12 | 208-230/3 | 65 | 70 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 208-230/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-C00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 0 | 460/3 | 14 | 20 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-C06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 6 | 460/3 | 23 | 25 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-C12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 12 | 460/3 | 33 | 35 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-R00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 0 | 460/3 | 14 | 20 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-R06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 6 | 460/3 | 23 | 25 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-R12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 12 | 460/3 | 33 | 35 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-E00XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 0 | 460/3 | 14 | 20 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-E06XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 6 | 460/3 | 23 | 25 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CEWBXX-E12XX | BACKPACK (OUTDOOR) | 5 | EVI (ENHANCED WINTER HEATING) | 1600 | ECONOMIZER | 0-1215 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 50900 | 35300 | 12 | 460/3 | 33 | 35 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | EVI (ENHANCED WINTER HEATING) | ECONOMIZER | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-C00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 460/3 | 14 | 20 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-C06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 460/3 | 23 | 25 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-C12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | COMMERCIAL ROOM VENTILATOR | 165-700 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 460/3 | 33 | 35 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | COMMERCIAL ROOM VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-R00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 460/3 | 14 | 20 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-R06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 460/3 | 23 | 25 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-R12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ENERGY RECOVERY VENTILATOR | 200-450 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 460/3 | 33 | 35 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ENERGY RECOVERY VENTILATOR | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-E00XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 0 | 460/3 | 14 | 20 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 0 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-E06XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 6 | 460/3 | 23 | 25 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 6 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet
AIRSYS | CV60H3C-CDWBXX-E12XX | BACKPACK (OUTDOOR) | 5 | DEHUM (HOT GAS REHEAT) | 1600 | ECONOMIZER | 0-1215 | 52500 | 39800 | 11 | 21.5 | 29,500-62,700 | 54500 | 3.3 | 33800 | 17500 | 12 | 460/3 | 33 | 35 | 45 | R-454B | 12.1 | 794 | 45-5/8 x 27-9/16 x 92-7/8 | BACKPACK (OUTDOOR) | 5 | 460/3 | DEHUM (HOT GAS REHEAT) | ECONOMIZER | 12 |  | Airsys School Air Solutions Specification Sheet Rev 3.3.4 | Airsys BackPack Outdoor Data Sheet

## SCHEDULE NOTES
Variable speed inverter heat pump with EC condenser and supply fans; R-454B refrigerant with refrigerant detection.
Provide with factory coastal protection coated outdoor coil and stainless steel fasteners (coil option C).
Provide with stainless steel body and frame, coastal protection coated coils and stainless steel fasteners (coil option E - BackPack only).
Provide with MERV-13 filters (filter option 3).
Cabinet color: gray (G, Focus IQ default), tan (X, BackPack default), white (W) or bronze (Z).
Provide with dual point power (separate heater circuit) - available on 208/230 V units with electric heat.
Provide with AIRSYS 5-year comprehensive warranty (R-454B School Air Solutions units; registration required).

## SOURCES
AIRSYS R-454B School Air Solutions Specification Sheet Rev 3.3.4 (engineering data); Focus IQ (ASCT-P-DS-Focus IQ-E2507V1.2) and BackPack (ASCT-P-DS-BackPack-E2507V1.2) data sheets; model number nomenclature from the 2025 School Air price sheets (option structure only - no pricing used).
Model numbers: base - power source (A 208/230V 1PH, B 208/230V 3PH, C 460V 3PH), heat exchanger (E EVI, D dehum hot gas reheat), W wire control, B R-454B, coil X standard, default color (G gray Focus IQ / X tan BackPack) - ventilation (C CRV, R ERV, E economizer), heater kW, filter X MERV-8, custom X. Coil, color and filter upgrades are schedule notes.
One row per model x power source x heat exchanger x ventilation option x PTC heater; the site folds the heater sizes into a kW dropdown.
Nominal tons, cooling total, EER, IEER, heating at 47F and COP: spec p.5 nominal ratings, by model and power source.
Sensible: spec p.7 standard-mode sensible at 80/67F (50% RH) return, 95F outdoor (does not vary by power source). Variable capacity range: spec p.5 min-max total at 80/67F.
Max heating capacity at 20F / 0F: spec p.6 - EVI rows use the "Max (EVI)" line, dehum rows the standard "Max Speed" line (EVI and dehum are alternative heat exchanger options).
Supply CFM: spec p.9 evaporator fan air volume. Sound: spec p.9 nominal dB. Charge: spec p.9 refrigerant lbs.
MCA / MOCP: spec p.10 single circuit MCA and MFS. Dual circuit values (208/230V with heater) are in the spec sheet.
Fresh air CFM: data sheets, range for each ventilation option. Weights and dimensions: data sheets.
Not modeled: dehumidification-mode capacities (spec p.7), ERV / economizer performance (p.8, p.11), field accessories (p.12; includes an economizer accessory for Focus IQ).