## SCHEDULE
SCHEDULE RANGE | [23 empty] | FILTERS | [13 empty] | DOCUMENTATION | [17 empty] | REFRIGERANT CALCULATIONS
SPLIT SYSTEM SCHEDULE | [23 empty] | SIZE (OUTDOOR UNIT) | COOLING ONLY OR HEAT PUMP | ELECTRICAL | NUMBER OF INDOOR UNITS | SIZE (INDOOR UNIT #1) | SIZE (INDOOR UNIT #2) | SIZE (INDOOR UNIT #3) | SIZE (INDOOR UNIT #4) | SIZE (INDOOR UNIT #5) | TYPE (INDOOR UNIT #1) | TYPE (INDOOR UNIT #2) | TYPE (INDOOR UNIT #3) | TYPE (INDOOR UNIT #4) | TYPE (INDOOR UNIT #5) | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL | REFRIGERANT | MAX VERTICAL SEPARATION (ODU TO IDU) (FT) | MAX VERTICAL SEPARATION (IDU TO IDU) (FT) | MAX TOTAL LINE SET (FT) | LIQUID LINE CONNECTION (IN) | SUCTION LINE CONNECTION (IN) | PRE-CHARGE PIPING LENGTH (FT) | FACTORY CHARGE (LBS) | FACTORY CHARGE (OZ) | ADDITIONAL CHARGE (OZ/FT)
INDOOR UNIT | [12 empty] | OUTDOOR UNIT | [8 empty] | Refrigerant | MAX ALLOWABLE LINE-SET LENGTHS
CFM | COOLING CAPACITY |  |  | HEAT PUMP HEATING CAPACITY |  | OPERATING WEIGHT | INDOOR UNIT TYPE | ELECTRICAL |  |  | MAKE & MODEL |  | OA AMBIENT (COOLING) | OA AMBIENT (HEATING) | OPERATING WEIGHT | SEER2/EER2/HSPF2 | ELECTRICAL |  |  | MAKE & MODEL
| EDB | EWB | TOTAL CAPACITY | EDB | TOTAL CAPACITY |  |  | Voltage | MCA | MOP | MAKE | MODEL |  |  |  |  | Voltage | MCA | MOP | MAKE | MODEL
235 | 80 | 67 | 9000 | 70 | 10000 | 18 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSBNS-H09B-1A | 95 | 47 | 57 | 19.5 / 12 / 9 | 115/60/1 | 18 | 20 | MIDEA | MO1CS-H09B-1A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 115/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 1.38 | 22 | 0.16
247 | 80 | 67 | 9000 | 70 | 10000 | 18 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSBNS-H09B-2A | 95 | 47 | 54 | 19.5 / 12 / 9 | 208-230/60/1 | 12 | 15 | MIDEA | MO1CS-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 1.38 | 22 | 0.16
294 | 80 | 67 | 12000 | 70 | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSBNS-H12B-1A | 95 | 47 | 61 | 19.5 / 10 / 8.7 | 115/60/1 | 19 | 20 | MIDEA | MO1CS-H12B-1A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 115/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 1.5 | 24 | 0.16
294 | 80 | 67 | 12000 | 70 | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSBNS-H12B-2A | 95 | 47 | 59 | 19.5 / 10.5 / 9 | 208-230/60/1 | 13 | 15 | MIDEA | MO1CS-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 1.56 | 25 | 0.16
400 | 80 | 67 | 18000 | 70 | 18800 | 25 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSBNS-H18B-2A | 95 | 47 | 72 | 19 / 11 / 9 | 208-230/60/1 | 15 | 20 | MIDEA | MO1CS-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 2.56 | 41 | 0.16
547 | 80 | 67 | 24000 | 70 | 24000 | 31 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSBNS-H24B-2A | 95 | 47 | 95 | 18 / 9.5 / 9 | 208-230/60/1 | 19 | 20 | MIDEA | MO1CS-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 3.38 | 54 | 0.32
648 | 80 | 67 | 30000 | 70 | 30000 | 43 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSBNS-H30B-2A | 95 | 47 | 143 | 19 / 11 / 8.9 | 208-230/60/1 | 28 | 30 | MIDEA | MO1CS-H30B-2A | R454B | 82' Vertical / 164' Total | 2.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 5.31 | 85 | 0.32
677 | 80 | 67 | 36000 | 70 | 36000 | 43 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSBNS-H36B-2A | 95 | 47 | 150 | 18 / 9 / 8.5 | 208-230/60/1 | 33 | 35 | MIDEA | MO1CS-H36B-2A | R454B | 98' Vertical / 213' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 98 | - | 213 | 0.375 | 0.625 | 25 | 7.06 | 113 | 0.32
324 | 80 | 67 | 6000 | 70 | 7000 | 23 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H06B-2A | 95 | 47 | 62 | 25.5 / 18 / 14.8 | 208-230/60/1 | 12 | 15 | MIDEA | MO1HS-H06B-2A | R454B | 49' Vertical / 82' Total | 0.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
324 | 80 | 67 | 9000 | 70 | 12000 | 23 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H09B-2A | 95 | 47 | 73 | 27.4 / 15.4 / 12.5 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
324 | 80 | 67 | 12000 | 70 | 12000 | 23 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H12B-2A | 95 | 47 | 73 | 25.4 / 13.4 / 10.5 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
500 | 80 | 67 | 15400 | 70 | 15400 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H15B-2A | 95 | 47 | 100 | 22.2 / 13.5 / 11.5 | 208-230/60/1 | 19 | 20 | MIDEA | MO1HS-H15B-2A | R454B | 66' Vertical / 98' Total | 1.25 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.25 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3.44 | 55 | 0.16
500 | 80 | 67 | 18000 | 70 | 18000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H18B-2A | 95 | 47 | 100 | 21.4 / 12.5 / 11 | 208-230/60/1 | 19 | 20 | MIDEA | MO1HS-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3.44 | 55 | 0.16
618 | 80 | 67 | 24000 | 70 | 29000 | 44 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H24B-2A | 95 | 47 | 130 | 21 / 13 / 13.5 | 208-230/60/1 | 24.9 | 25 | MIDEA | MO1HS-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 3.94 | 63 | 0.32
736 | 80 | 67 | 33000 | 70 | 36000 | 43 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H33B-2A | 95 | 47 | 157 | 19.5 / 12 / 10.5 | 208-230/60/1 | 34 | 35 | MIDEA | MO1HS-H33B-2A | R454B | 82' Vertical / 164' Total | 2.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.75 | 25 | 5.44 | 87 | 0.32
324 | 80 | 67 | 9000 | 70 | 10000 | 23 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEES-H09B-1A | 95 | 47 | 65 | 25.4 / 14.5 / 10 | 115/60/1 | 18 | 20 | MIDEA | MO1ES-H09B-1A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 115/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.12 | 34 | 0.16
324 | 80 | 67 | 9000 | 70 | 10000 | 23 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H09B-2A | 95 | 47 | 63 | 25.8 / 14.9 / 12.5 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
324 | 80 | 67 | 12000 | 70 | 12000 | 23 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEES-H12B-1A | 95 | 47 | 65 | 23.4 / 13 / 9.5 | 115/60/1 | 18 | 20 | MIDEA | MO1ES-H12B-1A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 115/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.12 | 34 | 0.16
324 | 80 | 67 | 12000 | 70 | 12000 | 23 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H12B-2A | 95 | 47 | 63 | 25.5 / 13 / 10.6 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
324 | 80 | 67 | 15000 | 70 | 15000 | 23 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEEU-H15B-2A | 95 | 47 | 63 | 23.5 / 11.7 / 9.9 | 208-230/60/1 | 15 | 15 | MIDEA | MO1ES-H15B-2A | R454B | 49' Vertical / 82' Total | 1.25 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.25 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
500 | 80 | 67 | 18000 | 70 | 18000 | 27 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H18B-2A | 95 | 47 | 93 | 23.5 / 12.7 / 10.8 | 208-230/60/1 | 18 | 20 | MIDEA | MO1ES-H18B-2A | R454B | 65' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 65 | - | 98 | 0.25 | 0.5 | 25 | 3 | 48 | 0.16
618 | 80 | 67 | 24000 | 70 | 25000 | 44 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEHU-H24B-2A | 95 | 47 | 122 | 23 / 14 / 11.7 | 208-230/60/1 | 24 | 25 | MIDEA | MO1ES-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 4.44 | 71 | 0.32
636 | 80 | 67 | 30000 | 70 | 30000 | 43 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEEU-H30B-2A | 95 | 47 | 143 | 20.5 / 12 / 9.5 | 208-230/60/1 | 28 | 30 | MIDEA | MO1BS-H30B-2A | R454B | 82' Vertical / 164' Total | 2.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 5.31 | 85 | 0.32
636 | 80 | 67 | 36000 | 70 | 36000 | 43 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSEEU-H36B-2A | 95 | 47 | 150 | 19 / 8.6 / 8.5 | 208-230/60/1 | 33 | 35 | MIDEA | MO1BS-H36B-2A | R454B | 98' Vertical / 213' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 98 | - | 213 | 0.375 | 0.625 | 25 | 7.06 | 113 | 0.32
424 | 80 | 67 | 6000 | 70 | 9000 | 28 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSESU-H06B-2A | 95 | 47 | 100 | 35 / 17.4 / 15.6 | 208-230/60/1 | 16 | 20 | MIDEA | MO1SS-H06B-2A | R454B | 49' Vertical / 82' Total | 0.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.75 | 44 | 0.16
424 | 80 | 67 | 9000 | 70 | 12000 | 28 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSESU-H09B-2A | 95 | 47 | 100 | 33.3 / 17 / 14.6 | 208-230/60/1 | 16 | 20 | MIDEA | MO1SS-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.75 | 44 | 0.16
424 | 80 | 67 | 12000 | 70 | 12000 | 28 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSESU-H12B-2A | 95 | 47 | 100 | 29.4 / 14.2 / 12.7 | 208-230/60/1 | 16 | 20 | MIDEA | MO1SS-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.75 | 44 | 0.16
618 | 80 | 67 | 18000 | 70 | 20000 | 44 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSESU-H18B-2A | 95 | 47 | 130 | 25.6 / 15 / 16.2 | 208-230/60/1 | 24.9 | 25 | MIDEA | MO1SS-H18B-2A | R454B | 82' Vertical / 164' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 3.94 | 63 | 0.32
235 | 80 | 67 | 9000 | 70 | 10000 | 18 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSGNS-H09B-1A | 95 | 47 | 57 | 21.5 / 12.5 / 9 | 115/60/1 | 18 | 20 | MIDEA | MO1BS-H09B-1A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 115/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 1.38 | 22 | 0.16
247 | 80 | 67 | 9000 | 70 | 10000 | 18 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSGNS-H09B-2A | 95 | 47 | 54 | 21.6 / 12.6 / 9.4 | 208-230/60/1 | 12 | 15 | MIDEA | MO1BS-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 1.38 | 22 | 0.16
294 | 80 | 67 | 12000 | 70 | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSGNS-H12B-1A | 95 | 47 | 61 | 21.3 / 10 / 8.7 | 115/60/1 | 19 | 20 | MIDEA | MO1BS-H12B-1A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 115/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 1.5 | 24 | 0.16
294 | 80 | 67 | 12000 | 70 | 12000 | 19 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSGNS-H12B-2A | 95 | 47 | 59 | 21.3 / 10.8 / 9.2 | 208-230/60/1 | 13 | 15 | MIDEA | MO1BS-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 1.56 | 25 | 0.16
400 | 80 | 67 | 18000 | 70 | 18800 | 25 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSGNS-H18B-2A | 95 | 47 | 72 | 20.2 / 11.5 / 9.1 | 208-230/60/1 | 15 | 20 | MIDEA | MO1BS-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 2.56 | 41 | 0.16
547 | 80 | 67 | 24000 | 70 | 24000 | 31 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSGNS-H24B-2A | 95 | 47 | 95 | 18.5 / 9.6 / 9 | 208-230/60/1 | 19 | 20 | MIDEA | MO1BS-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 3.38 | 54 | 0.32
648 | 80 | 67 | 30000 | 70 | 30000 | 43 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSGNS-H30B-2A | 95 | 47 | 143 | 22.3 / 12 / 9 | 208-230/60/1 | 28 | 30 | MIDEA | MO1BS-H30B-2A | R454B | 82' Vertical / 164' Total | 2.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2.5 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 5.31 | 85 | 0.32
677 | 80 | 67 | 36000 | 70 | 36000 | 43 | Wall Mounted | Indoor Powered From Outdoor Unit |  |  | MIDEA | MSGNS-H36B-2A | 95 | 47 | 150 | 19.5 / 9.3 / 9.1 | 208-230/60/1 | 33 | 35 | MIDEA | MO1BS-H36B-2A | R454B | 98' Vertical / 213' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Wall Mounted | - | - | - | - | [18 empty] | R-454B | 98 | - | 213 | 0.375 | 0.625 | 25 | 7.06 | 113 | 0.32
294 | 80 | 67 | 9000 | 70 | 11000 | 45 | One-Way Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCAHU-H09B-2A | 95 | 47 | 62 | 22.1 / 14.4 / 11.8 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | One-Way Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
312 | 80 | 67 | 12000 | 70 | 12000 | 45 | One-Way Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCAHU-H12B-2A | 95 | 47 | 62 | 22.1 / 12.3 / 10 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | One-Way Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
352 | 80 | 67 | 18000 | 70 | 18000 | 45 | One-Way Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCAHU-H18B-2A | 95 | 47 | 93 | 22.2 / 12.5 / 12.2 | 208-230/60/1 | 18 | 20 | MIDEA | MO1ES-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | One-Way Cassette | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3 | 48 | 0.16
294 | 80 | 67 | 6500 | 70 | 7400 | 45 | One-Way Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCAHU-H06B-2A | 95 | 47 | 62 | 22 / 15 / 12 | 208-230/60/1 | 12 | 15 | MIDEA | MO1HS-H06B-2A | R454B | 49' Vertical / 82' Total | 0.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.5 | - | - | - | - | One-Way Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
294 | 80 | 67 | 9000 | 70 | 10900 | 45 | One-Way Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCAHU-H09B-2A | 95 | 47 | 73 | 24 / 14.6 / 12.1 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | One-Way Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
312 | 80 | 67 | 12000 | 70 | 12500 | 45 | One-Way Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCAHU-H12B-2A | 95 | 47 | 73 | 23 / 13 / 10 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | One-Way Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
352 | 80 | 67 | 16700 | 70 | 20000 | 45 | One-Way Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCAHU-H18B-2A | 95 | 47 | 100 | 20.6 / 12.5 / 12.2 | 208-230/60/1 | 19 | 20 | MIDEA | MO1HS-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | One-Way Cassette | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3.44 | 55 | 0.16
312 | 80 | 67 | 9000 | 70 | 10000 | 35 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHU-H09B-2A | 95 | 47 | 63 | 21.6 / 14.3 / 11.3 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
365 | 80 | 67 | 12000 | 70 | 12000 | 35 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHU-H12B-2A | 95 | 47 | 63 | 21.1 / 12.5 / 10.4 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
389 | 80 | 67 | 16800 | 70 | 18000 | 35 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHU-H18B-2A | 95 | 47 | 93 | 20.7 / 12.5 / 11.4 | 208-230/60/1 | 18 | 20 | MIDEA | MO1ES-H18B-2A | R454B | 66' Vertical / 98.4' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 66 | - | 98.4 | 0.25 | 0.5 | 25 | 3 | 48 | 0.16
706 | 80 | 67 | 24000 | 70 | 25000 | 47 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHU-H24B-2A | 95 | 47 | 122 | 22 / 12 / 10.5 | 208-230/60/1 | 24 | 25 | MIDEA | MO1ES-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 4.44 | 71 | 0.32
948 | 80 | 67 | 36000 | 70 | 38000 | 59 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHS-H36B-2A | 95 | 47 | 152 | 20 / 9.6 / 10.3 | 208-230/60/1 | 33 | 35 | MIDEA | MO1BU-H36B-2A | R454B | 98' Vertical / 246' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 5.75 | 92 | 0.32
1124 | 80 | 67 | 48000 | 70 | 50000 | 65 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHS-H48B-2A | 95 | 47 | 209 | 19 / 9.5 / 9.9 | 208-230/60/1 | 39 | 40 | MIDEA | MO1BU-H48B-2A | R454B | 98' Vertical / 246' Total | 4 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 4 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32
312 | 80 | 67 | 9000 | 70 | 10000 | 35 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHU-H09B-2A | 95 | 47 | 73 | 22.6 / 14 / 12.1 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
365 | 80 | 67 | 12000 | 70 | 12000 | 35 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHU-H12B-2A | 95 | 47 | 73 | 22.2 / 12.5 / 11.6 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
389 | 80 | 67 | 16000 | 70 | 19000 | 35 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHU-H18B-2A | 95 | 47 | 100 | 20 / 12.5 / 12.3 | 208-230/60/1 | 19 | 20 | MIDEA | MO1HS-H18B-2A | R454B | 66' Vertical / 98.4' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 66 | - | 98.4 | 0.25 | 0.5 | 25 | 3.44 | 55 | 0.16
706 | 80 | 67 | 23400 | 70 | 25000 | 47 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHU-H24B-2A | 95 | 47 | 130 | 20.7 / 12 / 11.6 | 208-230/60/1 | 24.9 | 25 | MIDEA | MO1HS-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 3.94 | 63 | 0.32
948 | 80 | 67 | 36600 | 70 | 37000 | 59 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHS-H36B-2A | 95 | 47 | 207 | 21.2 / 12 / 10.6 | 208-230/60/1 | 38 | 40 | MIDEA | MO1HU-H36B-2A | R454B | 98' Vertical / 246' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32
1124 | 80 | 67 | 48000 | 70 | 53000 | 65 | Round Flow Cassette | Indoor Powered From Outdoor Unit |  |  | MIDEA | MCDHS-H48B-2A | 95 | 47 | 209 | 18 / 10 / 11 | 208-230/60/1 | 44 | 45 | MIDEA | MO1HU-H48B-2A | R454B | 98' Vertical / 246' Total | 4 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 4 | - | - | - | - | Round Flow Cassette | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32
288 | 80 | 67 | 9000 | 70 | 10000 | 64 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHU-H09B-2A | 95 | 47 | 63 | 19.7 / 13 / 11.5 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
265 | 80 | 67 | 9000 | 70 | 10000 | 39 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDLHU-H09B-2A | 95 | 47 | 63 | 19.5 / 12.8 / 11 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
350 | 80 | 67 | 12000 | 70 | 12000 | 64 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHU-H12B-2A | 95 | 47 | 63 | 19.5 / 12 / 10.5 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
324 | 80 | 67 | 11500 | 70 | 12000 | 39 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDLHU-H12B-2A | 95 | 47 | 63 | 19 / 11.7 / 10.2 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.5 | 25 | 2 | 32 | 0.16
618 | 80 | 67 | 17500 | 70 | 20000 | 80 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHU-H18B-2A | 95 | 47 | 93 | 20 / 13.3 / 11.3 | 208-230/60/1 | 18 | 20 | MIDEA | MO1ES-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3 | 48 | 0.16
559 | 80 | 67 | 17000 | 70 | 20000 | 54 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDLHU-H18B-2A | 95 | 47 | 93 | 20 / 12.5 / 10.5 | 208-230/60/1 | 18 | 20 | MIDEA | MO1ES-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.375 | 0.625 | 25 | 3 | 48 | 0.16
706 | 80 | 67 | 24000 | 70 | 25000 | 80 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHU-H24B-2A | 95 | 47 | 122 | 19 / 12.5 / 11 | 208-230/60/1 | 24 | 25 | MIDEA | MO1ES-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 4.44 | 71 | 0.32
1060 | 80 | 67 | 36000 | 70 | 40000 | 106 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHS-H36B-2A | 95 | 47 | 152 | 18.7 / 10.1 / 10.2 | 208-230/60/1 | 33 | 35 | MIDEA | MO1BU-H36B-2A | R454B | 98' Vertical / 246' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 5.75 | 92 | 0.32
1472 | 80 | 67 | 48000 | 70 | 50000 | 111 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHS-H48B-2A | 95 | 47 | 209 | 17.1 / 10 / 9.8 | 208-230/60/1 | 39 | 40 | MIDEA | MO1BU-H48B-2A | R454B | 98' Vertical / 246' Total | 4 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 4 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32
1707 | 80 | 67 | 58000 | 70 | 60000 | 161 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHS-H60B-2A | 95 | 47 | 209 | 17 / 10 / 9.7 | 208-230/60/1 | 42 | 45 | MIDEA | MO1BU-H60B-2A | R454B | 98' Vertical / 246' Total | 5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 5 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 9.06 | 145 | 0.32
265 | 80 | 67 | 6500 | 70 | 8000 | 39 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDLHU-H06B-2A | 95 | 47 | 62 | 21.4 / 14.4 / 13.8 | 208-230/60/1 | 12 | 15 | MIDEA | MO1HS-H06B-2A | R454B | 33' Vertical / 82' Total | 0.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.5 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 33 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
288 | 80 | 67 | 9000 | 70 | 9900 | 64 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHU-H09B-2A | 95 | 47 | 73 | 20.5 / 14 / 13.8 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
265 | 80 | 67 | 9000 | 70 | 10000 | 39 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDLHU-H09B-2A | 95 | 47 | 73 | 21.4 / 13.4 / 12.5 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H09B-2A | R454B | 33' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 33 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
350 | 80 | 67 | 12000 | 70 | 12000 | 64 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHU-H12B-2A | 95 | 47 | 73 | 20 / 12 / 10.6 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
324 | 80 | 67 | 12000 | 70 | 12500 | 39 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDLHU-H12B-2A | 95 | 47 | 73 | 20 / 12 / 10 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H12B-2A | R454B | 33' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 33 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
618 | 80 | 67 | 17500 | 70 | 19500 | 80 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHU-H18B-2A | 95 | 47 | 100 | 18.4 / 12 / 11.1 | 208-230/60/1 | 19 | 20 | MIDEA | MO1HS-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3.44 | 55 | 0.16
560 | 80 | 67 | 17000 | 70 | 19000 | 54 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDLHU-H18B-2A | 95 | 47 | 100 | 18 / 12 / 10.5 | 208-230/60/1 | 19 | 20 | MIDEA | MO1HS-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3.44 | 55 | 0.16
706 | 80 | 67 | 24000 | 70 | 26000 | 80 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHU-H24B-2A | 95 | 47 | 130 | 19 / 12 / 11.7 | 208-230/60/1 | 24.9 | 25 | MIDEA | MO1HS-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 3.94 | 63 | 0.32
1060 | 80 | 67 | 36000 | 70 | 42000 | 106 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHS-H36B-2A | 95 | 47 | 207 | 17.7 / 12 / 11.1 | 208-230/60/1 | 38 | 40 | MIDEA | MO1HU-H36B-2A | R454B | 98' Vertical / 246' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32
1472 | 80 | 67 | 48000 | 70 | 52000 | 111 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHS-H48B-2A | 95 | 47 | 209 | 16.7 / 10.4 / 10.8 | 208-230/60/1 | 44 | 45 | MIDEA | MO1HU-H48B-2A | R454B | 98' Vertical / 246' Total | 4 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 4 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32
1707 | 80 | 67 | 55000 | 70 | 60000 | 161 | Slim Duct | Indoor Powered From Outdoor Unit |  |  | MIDEA | MDHHS-H60B-2A | 95 | 47 | 230 | 15.8 / 10.2 / 10.4 | 208-230/60/1 | 44 | 45 | MIDEA | MO1HU-H60B-2A | R454B | 98' Vertical / 246' Total | 5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 5 | - | - | - | - | Slim Duct | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 9.5 | 152 | 0.32
377 | 80 | 67 | 9000 | 70 | 9000 | 33 | Console | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFAHU-H09B-2A | 95 | 47 | 62 | 26 / 16.2 / 13.9 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Console | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
377 | 80 | 67 | 12000 | 70 | 12000 | 33 | Console | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFAHU-H12B-2A | 95 | 47 | 62 | 24.6 / 12.7 / 11 | 208-230/60/1 | 12 | 15 | MIDEA | MO1ES-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Console | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2 | 32 | 0.16
441 | 80 | 67 | 16000 | 70 | 17000 | 33 | Console | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFAHU-H16B-2A | 95 | 47 | 93 | 23.8 / 12.5 / 13.5 | 208-230/60/1 | 18 | 20 | MIDEA | MO1ES-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.3333 | - | - | - | - | Console | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3 | 48 | 0.16
377 | 80 | 67 | 9000 | 70 | 9000 | 33 | Console | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFAHU-H09B-2A | 95 | 47 | 73 | 27.2 / 15.1 / 10.9 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H09B-2A | R454B | 49' Vertical / 82' Total | 0.75 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 0.75 | - | - | - | - | Console | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
377 | 80 | 67 | 12000 | 70 | 12000 | 33 | Console | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFAHU-H12B-2A | 95 | 47 | 73 | 25 / 12.5 / 10.5 | 208-230/60/1 | 15 | 15 | MIDEA | MO1HS-H12B-2A | R454B | 49' Vertical / 82' Total | 1 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1 | - | - | - | - | Console | - | - | - | - | [18 empty] | R-454B | 49 | - | 82 | 0.25 | 0.375 | 25 | 2.19 | 35 | 0.16
441 | 80 | 67 | 16000 | 70 | 17000 | 33 | Console | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFAHU-H16B-2A | 95 | 47 | 100 | 20 / 12.5 / 10.3 | 208-230/60/1 | 19 | 20 | MIDEA | MO1HS-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.3333 | - | - | - | - | Console | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3.44 | 55 | 0.16
547 | 80 | 67 | 18000 | 70 | 18000 | 58 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHU-H18B-2A | 95 | 47 | 93 | 22.3 / 12.5 / 10.4 | 208-230/60/1 | 18 | 20 | MIDEA | MO1ES-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3 | 48 | 0.16
706 | 80 | 67 | 24000 | 70 | 24400 | 61 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHU-H24B-2A | 95 | 47 | 122 | 21.1 / 12.2 / 11.1 | 208-230/60/1 | 24 | 25 | MIDEA | MO1ES-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 4.44 | 71 | 0.32
1089 | 80 | 67 | 36000 | 70 | 38000 | 89 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHS-H36B-2A | 95 | 47 | 152 | 20 / 10.1 / 10 | 208-230/60/1 | 33 | 35 | MIDEA | MO1BU-H36B-2A | R454B | 98' Vertical / 246' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 5.75 | 92 | 0.32
1236 | 80 | 67 | 54000 | 70 | 60000 | 95 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHS-H60B-2A | 95 | 47 | 209 | 19.5 / 9.5 / 9.5 | 208-230/60/1 | 42 | 45 | MIDEA | MO1BU-H60B-2A | R454B | 98' Vertical / 246' Total | 5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 5 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 9.06 | 145 | 0.32
547 | 80 | 67 | 17000 | 70 | 19000 | 58 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHU-H18B-2A | 95 | 47 | 100 | 20.4 / 12.5 / 10.3 | 208-230/60/1 | 19 | 20 | MIDEA | MO1HS-H18B-2A | R454B | 66' Vertical / 98' Total | 1.5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 1.5 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 66 | - | 98 | 0.25 | 0.5 | 25 | 3.44 | 55 | 0.16
706 | 80 | 67 | 22000 | 70 | 26000 | 61 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHU-H24B-2A | 95 | 47 | 130 | 20.4 / 12 / 12.1 | 208-230/60/1 | 24.9 | 25 | MIDEA | MO1HS-H24B-2A | R454B | 82' Vertical / 164' Total | 2 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 2 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 82 | - | 164 | 0.375 | 0.625 | 25 | 3.94 | 63 | 0.32
1089 | 80 | 67 | 36400 | 70 | 38000 | 88.85 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHS-H36B-2A | 95 | 47 | 207 | 20 / 12 / 10.8 | 208-230/60/1 | 38 | 40 | MIDEA | MO1HU-H36B-2A | R454B | 98' Vertical / 246' Total | 3 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 3 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32
1236 | 80 | 67 | 48000 | 70 | 52000 | 89.07 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHS-H48B-2A | 95 | 47 | 209 | 18.5 / 9.4 / 10.1 | 208-230/60/1 | 44 | 45 | MIDEA | MO1HU-H48B-2A | R454B | 98' Vertical / 246' Total | 4 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 4 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32
1236 | 80 | 67 | 54000 | 70 | 60000 | 95.24 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHS-H60B-2A | 95 | 47 | 230 | 18 / 9 / 10.7 | 208-230/60/1 | 44 | 45 | MIDEA | MO1HU-H60B-2A | R454B | 98' Vertical / 246' Total | 5 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 5 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 9.5 | 152 | 0.32
1236 | 80 | 67 | 48000 | 70 | 50000 | 89 | Ceiling & Floor | Indoor Powered From Outdoor Unit |  |  | MIDEA | MFBHS-H48B-2A | 95 | 47 | 209 | 19.8 / 9.5 / 10.2 | 208-230/60/1 | 39 | 40 | MIDEA | MO1BU-H48B-2A | R454B | 98' Vertical / 246' Total | 4 | HEAT PUMP | 208-230/60/1 (SINGLE POINT POWER) | 1 | 4 | - | - | - | - | Ceiling & Floor | - | - | - | - | [18 empty] | R-454B | 98 | - | 246 | 0.375 | 0.75 | 25 | 7.94 | 127 | 0.32

## SCHEDULE NOTES
Provide with 7-day programmable thermostat
Provide with Midea wired controller with built-in Wi-Fi
Provide with field installed condensate pump
Provide with field installed disconnect. Disconnect shall be provided and installed by electrical contractor

## SOURCES
Midea single-zone heat pump systems from the Midea SUBMITTAL DATA SHEETs (Desktop/Midea Cut Sheets), one row per indoor/outdoor pair.
Cooling: rated capacity at 80F DB / 67F WB indoor, 95F outdoor. Heating: rated capacity at 47F outdoor, 70F indoor.
Sensible capacity is not printed on the submittals and the column has been removed.
CFM: indoor high speed (H) airflow. Weights: net. SEER2 / EER2 / HSPF2 (HSPF2 region IV) as printed.
Electrical: system MCA / MOCP, single point power (indoor powered from the outdoor unit).
Refrigerant: max height difference, max piping length, liquid / gas line sizes, max pre-charged length, pre-charged amount (oz; lbs = oz / 16) and additional charge (oz/ft) as printed.
Multi-zone systems are not included yet.