## SCHEDULE
SCHEDULE RANGE | [29 empty] | FILTERS | [6 empty] | DOCUMENTATION | [17 empty] | REFRIGERANT CALCULATIONS
UNITARY & LIGHT COMMERCIAL SPLIT SYSTEM SCHEDULE | [29 empty] | SIZE | COOLING ONLY OR HEAT PUMP | NOMINAL EFFICIENCY | ELECTRICAL | KW | STAGES | FAN TYPE | SUBMITTAL (OUTDOOR UNIT) | SUBMITTAL (INDOOR UNIT) | SUBMITTAL (SYSTEM) | ENGINEERING MANUAL (SYSTEM) | ENGINEERING MANUAL (OUTDOOR UNIT) | ENGINEERING MANUAL (INDOOR UNIT) | CAPACITY TABLE | INSTALLATION MANUAL (OUTDOOR) | INSTALLATION MANUAL (INDOOR) | INSTALLATION MANUAL (SYSTEM) | REVIT (OUTDOOR) | REVIT (INDOOR) | REVIT (SYSTEM) | CAD (OUTDOOR) | CAD (INDOOR) | CAD (SYSTEM) | CONTROLS OPTIONS | OPERATION MANUAL | REFRIGERANT | MAX VERTICAL SEPARATION (ODU TO IDU) (FT) | MAX VERTICAL SEPARATION (IDU TO IDU) (FT) | MAX TOTAL LINE SET (FT) | LIQUID LINE CONNECTION (IN) | SUCTION LINE CONNECTION (IN) | PRE-CHARGE PIPING LENGTH (FT) | FACTORY CHARGE (LBS) | FACTORY CHARGE (OZ) | ADDITIONAL CHARGE (OZ/FT)
INDOOR AIR HANDLING UNIT | [16 empty] | OUTDOOR CONDENSING UNIT
MAKE | MODEL | SUPPLY FAN |  |  | COOLING |  |  |  |  | HEAT PUMP TOTAL CAPACITY | AUX. ELECTRIC HEAT |  | ELECTRICAL DATA |  |  | WEIGHT | MAKE | MODEL | HEAT PUMP HEATING DATA |  |  | ELECTRICAL DATA |  |  | OUTDOOR AMBIENT (COOLING) | REFRIGERANT | EFFICIENCY | WEIGHT | COMPRESSOR STAGES
|  | AIRFLOW (CFM) | MOTOR (HP) | MOTOR TYPE | EAT (DB) | EAT (WB) | LAT (DB) | TOTAL CAPACITY | SENSIBLE CAPACITY |  | kW | TEMPERATURE RISE (DB) | VOLTAGE / PHASE | MCA | MOP |  |  |  | OUTDOOR AMBIENT (DB) | TOTAL CAPACITY | EFFICIENCY | VOLTAGE / PHASE | MCA | MOP
DAIKIN | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | - | - | 208/1 | 4.9 | 15 | 115 | DAIKIN | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter | 1.5 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA18AAVJU | FTA18AAVJUD |  | RZA18AAVJU | FTA18AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 3 | 15.965 | 208/1 | 18.4 | 20 | 115 | DAIKIN | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter | 1.5 | HEAT PUMP | Sky Air | 208/1 | 3 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 3 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA18AAVJU | FTA18AAVJUD |  | RZA18AAVJU | FTA18AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 5 | 26.6083 | 208/1 | 26.5 | 30 | 115 | DAIKIN | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter | 1.5 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA18AAVJU | FTA18AAVJUD |  | RZA18AAVJU | FTA18AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 6 | 31.93 | 208/1 | 32 | 35 | 115 | DAIKIN | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter | 1.5 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA18AAVJU | FTA18AAVJUD |  | RZA18AAVJU | FTA18AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 8 | 42.5733 | 208/1 | 41 | 45 | 115 | DAIKIN | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter | 1.5 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA18AAVJU | FTA18AAVJUD |  | RZA18AAVJU | FTA18AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA18AAVJUD | 600 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 17200 | 12100 | 21000 | 10 | 53.2167 | 208/1 | 48.2 | 50 | 115 | DAIKIN | RZA18AAVJU | 47 | 21000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.5/11.7 (SEER2/EER2) | 234 | Inverter | 1.5 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA18AAVJUD-RZA18AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA18AAVJU | FTA18AAVJUD |  | RZA18AAVJU | FTA18AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | - | - | 208/1 | 4.9 | 15 | 115 | DAIKIN | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter | 2 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 0 Kw |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA24AAVJU | FTA24AAVJUD |  | RZA24AAVJU | FTA24AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 3 | 11.9738 | 208/1 | 18.4 | 20 | 115 | DAIKIN | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter | 2 | HEAT PUMP | Sky Air | 208/1 | 3 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 3 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA24AAVJU | FTA24AAVJUD |  | RZA24AAVJU | FTA24AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 5 | 19.9563 | 208/1 | 26.5 | 30 | 115 | DAIKIN | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter | 2 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA24AAVJU | FTA24AAVJUD |  | RZA24AAVJU | FTA24AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 6 | 23.9475 | 208/1 | 32 | 35 | 115 | DAIKIN | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter | 2 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA24AAVJU | FTA24AAVJUD |  | RZA24AAVJU | FTA24AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 8 | 31.93 | 208/1 | 41 | 45 | 115 | DAIKIN | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter | 2 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA24AAVJU | FTA24AAVJUD |  | RZA24AAVJU | FTA24AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA24AAVJUD | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 24000 | 16900 | 27000 | 10 | 39.9125 | 208/1 | 48.2 | 50 | 115 | DAIKIN | RZA24AAVJU | 47 | 27000 | 9.0 HSPF2 | 208/1 | 19.8 | 20 | 95 | R32 | 17.0/11.7 (SEER2/EER2) | 234 | Inverter | 2 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA24AAVJUD-RZA24AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA24AAVJU | FTA24AAVJUD |  | RZA24AAVJU | FTA24AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | - | - | 208/1 | 4.9 | 15 | 118 | DAIKIN | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter | 2.5 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA30AAVJU | FTA30AAVJUD |  | RZA30AAVJU | FTA30AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 3 | 9.579 | 208/1 | 18.4 | 20 | 118 | DAIKIN | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter | 2.5 | HEAT PUMP | Sky Air | 208/1 | 3 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 3 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA30AAVJU | FTA30AAVJUD |  | RZA30AAVJU | FTA30AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 5 | 15.965 | 208/1 | 26.5 | 30 | 118 | DAIKIN | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter | 2.5 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA30AAVJU | FTA30AAVJUD |  | RZA30AAVJU | FTA30AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 6 | 19.158 | 208/1 | 32 | 35 | 118 | DAIKIN | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter | 2.5 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA30AAVJU | FTA30AAVJUD |  | RZA30AAVJU | FTA30AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 8 | 25.544 | 208/1 | 41 | 45 | 118 | DAIKIN | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter | 2.5 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA30AAVJU | FTA30AAVJUD |  | RZA30AAVJU | FTA30AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA30AAVJUD | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 61 | 29400 | 20900 | 35000 | 10 | 31.93 | 208/1 | 48.2 | 50 | 118 | DAIKIN | RZA30AAVJU | 47 | 35000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/11.0 (SEER2/EER2) | 234 | Inverter | 2.5 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA30AAVJUD-RZA30AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA30AAVJU | FTA30AAVJUD |  | RZA30AAVJU | FTA30AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | - | - | 208/1 | 4.9 | 15 | 118 | DAIKIN | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter | 3 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA36AAVJU | FTA36AAVJUD |  | RZA36AAVJU | FTA36AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 3 | 9.1229 | 208/1 | 18.4 | 20 | 118 | DAIKIN | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter | 3 | HEAT PUMP | Sky Air | 208/1 | 3 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 3 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA36AAVJU | FTA36AAVJUD |  | RZA36AAVJU | FTA36AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 5 | 15.2048 | 208/1 | 26.5 | 30 | 118 | DAIKIN | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter | 3 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA36AAVJU | FTA36AAVJUD |  | RZA36AAVJU | FTA36AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 6 | 18.2457 | 208/1 | 32 | 35 | 118 | DAIKIN | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter | 3 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA36AAVJU | FTA36AAVJUD |  | RZA36AAVJU | FTA36AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 8 | 24.3276 | 208/1 | 41 | 45 | 118 | DAIKIN | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter | 3 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA36AAVJU | FTA36AAVJUD |  | RZA36AAVJU | FTA36AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA36AAVJUD | 1050 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 35000 | 23700 | 40500 | 10 | 30.4095 | 208/1 | 48.2 | 50 | 118 | DAIKIN | RZA36AAVJU | 47 | 40500 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.8/10.0 (SEER2/EER2) | 234 | Inverter | 3 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA36AAVJUD-RZA36AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA36AAVJU | FTA36AAVJUD |  | RZA36AAVJU | FTA36AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | - | - | 208/1 | 6.5 | 15 | 143 | DAIKIN | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter | 3.5 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA42AAVJU | FTA42AAVJUD |  | RZA42AAVJU | FTA42AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 5 | 11.4036 | 208/1 | 28.2 | 30 | 143 | DAIKIN | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter | 3.5 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA42AAVJU | FTA42AAVJUD |  | RZA42AAVJU | FTA42AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 6 | 13.6843 | 208/1 | 33.6 | 35 | 143 | DAIKIN | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter | 3.5 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA42AAVJU | FTA42AAVJUD |  | RZA42AAVJU | FTA42AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 8 | 18.2457 | 208/1 | 42.6 | 45 | 143 | DAIKIN | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter | 3.5 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA42AAVJU | FTA42AAVJUD |  | RZA42AAVJU | FTA42AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 10 | 22.8071 | 208/1 | 49.8 | 50 | 143 | DAIKIN | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter | 3.5 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA42AAVJU | FTA42AAVJUD |  | RZA42AAVJU | FTA42AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 15 | 34.2107 | 208/1 | 71.5 | 80 | 143 | DAIKIN | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter | 3.5 | HEAT PUMP | Sky Air | 208/1 | 15 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 15 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA42AAVJU | FTA42AAVJUD |  | RZA42AAVJU | FTA42AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA42AAVJUD | 1400 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 40500 | 29500 | 48000 | 19 | 43.3336 | 208/1 | 93.2 | 100 | 143 | DAIKIN | RZA42AAVJU | 47 | 48000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 16.0/10.0 (SEER2/EER2) | 234 | Inverter | 3.5 | HEAT PUMP | Sky Air | 208/1 | 19 | Inverter | Variable Speed ECM | FTA42AAVJUD-RZA42AAVJU - 19 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA42AAVJU | FTA42AAVJUD |  | RZA42AAVJU | FTA42AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | - | - | 208/1 | 6.5 | 15 | 143 | DAIKIN | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter | 4 | HEAT PUMP | Sky Air | 208/1 | - | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 0 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA48AAVJU | FTA48AAVJUD |  | RZA48AAVJU | FTA48AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 5 | 10.5033 | 208/1 | 28.2 | 30 | 143 | DAIKIN | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter | 4 | HEAT PUMP | Sky Air | 208/1 | 5 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 5 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA48AAVJU | FTA48AAVJUD |  | RZA48AAVJU | FTA48AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 6 | 12.6039 | 208/1 | 33.6 | 35 | 143 | DAIKIN | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter | 4 | HEAT PUMP | Sky Air | 208/1 | 6 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 6 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA48AAVJU | FTA48AAVJUD |  | RZA48AAVJU | FTA48AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 8 | 16.8053 | 208/1 | 42.6 | 45 | 143 | DAIKIN | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter | 4 | HEAT PUMP | Sky Air | 208/1 | 8 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 8 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA48AAVJU | FTA48AAVJUD |  | RZA48AAVJU | FTA48AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 10 | 21.0066 | 208/1 | 49.8 | 50 | 143 | DAIKIN | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter | 4 | HEAT PUMP | Sky Air | 208/1 | 10 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 10 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA48AAVJU | FTA48AAVJUD |  | RZA48AAVJU | FTA48AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 15 | 31.5099 | 208/1 | 71.5 | 80 | 143 | DAIKIN | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter | 4 | HEAT PUMP | Sky Air | 208/1 | 15 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 15 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA48AAVJU | FTA48AAVJUD |  | RZA48AAVJU | FTA48AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | FTA48AAVJUD | 1520 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 47000 | 32000 | 55000 | 19 | 39.9125 | 208/1 | 93.2 | 100 | 143 | DAIKIN | RZA48AAVJU | 47 | 55000 | 9.0 HSPF2 | 208/1 | 34.6 | 35 | 95 | R32 | 15.2/8.9 (SEER2/EER2) | 143 | Inverter | 4 | HEAT PUMP | Sky Air | 208/1 | 19 | Inverter | Variable Speed ECM | FTA48AAVJUD-RZA48AAVJU - 19 kW |  |  | ENGINEERING MANUAL - FTA SKY AIR | ENGINEERING MANUAL - FTA SKY AIR |  | CAPACITY TABLE - FTA SKY AIR | INSTALLATION MANUAL - RZA | INSTALLATION MANUAL - FTA |  | RZA48AAVJU | FTA48AAVJUD |  | RZA48AAVJU | FTA48AAVJUD |  |  |  | R-32 | 98 | - | 230 | 0.375 | 0.625 | 25 | 7.5 | 120 | 0.04
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | - | - | 208/1 | 5.8 | 15 | 112 | DAIKIN | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM | DH4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 3 | 15.45 | 208/1 | 19 | 20 | 112 | DAIKIN | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DH4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 5 | 25.75 | 208/1 | 27 | 30 | 112 | DAIKIN | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DH4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 6 | 30.9 | 208/1 | 32.8 | 35 | 112 | DAIKIN | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DH4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 8 | 41.2 | 208/1 | 41.9 | 45 | 112 | DAIKIN | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DH4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 10 | 51.5 | 208/1 | 49.1 | 50 | 112 | DAIKIN | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DH4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 59 | 18000 | 14040 | 17400 | 15 | 77.25 | 208/1 | 70.8 | 90 | 112 | DAIKIN | DH4SEA1810 | 47 | 17400 | 7.8 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DH4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | - | - | 208/1 | 5.8 | 15 | 112 | DAIKIN | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM | DH4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 3 | 12.4403 | 208/1 | 19 | 20 | 112 | DAIKIN | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DH4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 5 | 20.7338 | 208/1 | 27 | 30 | 112 | DAIKIN | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DH4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 6 | 24.8805 | 208/1 | 32.8 | 35 | 112 | DAIKIN | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DH4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 8 | 33.174 | 208/1 | 41.9 | 45 | 112 | DAIKIN | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DH4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 10 | 41.4675 | 208/1 | 49.1 | 50 | 112 | DAIKIN | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DH4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | AMST24BU1300 | 770 | 0.75 | ECM | 80 | 67 | 59 | 23800 | 17850 | 22000 | 15 | 62.2013 | 208/1 | 70.8 | 90 | 112 | DAIKIN | DH4SEA2410 | 47 | 22000 | 7.8 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 160 | 1 | 2 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DH4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | - | - | 208/1 | 5.6 | 15 | 129 | DAIKIN | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM | DH4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 3 | 9.0368 | 208/1 | 19 | 20 | 129 | DAIKIN | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DH4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 5 | 15.0613 | 208/1 | 27 | 30 | 129 | DAIKIN | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DH4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 6 | 18.0736 | 208/1 | 32.7 | 35 | 129 | DAIKIN | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DH4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 8 | 24.0981 | 208/1 | 42 | 45 | 129 | DAIKIN | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DH4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 10 | 30.1226 | 208/1 | 49 | 50 | 129 | DAIKIN | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DH4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | AMST30BU1300 | 1060 | 0.75 | ECM | 80 | 67 | 59 | 28600 | 22880 | 28600 | 15 | 45.184 | 208/1 | 49.1 | 80 | 129 | DAIKIN | DH4SEA3010 | 47 | 28600 | 7.8 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 174 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DH4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM | DH4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 3 | 8.0496 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DH4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 5 | 13.416 | 208/1 | 29 | 35 | 153 | DAIKIN | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DH4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 6 | 16.0992 | 208/1 | 34 | 40 | 153 | DAIKIN | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DH4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 8 | 21.4655 | 208/1 | 43 | 50 | 153 | DAIKIN | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DH4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 10 | 26.8319 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DH4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 15 | 40.2479 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DH4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 35000 | 19 | 50.9807 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DH4SEA3610 | 47 | 35000 | 7.5 HSPF2 | 208/1 | 21.5 | 35 | 95 | R32 | 15/12.5 (SEER2/EER2) | 196 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/1 | 19 | 1 | ECM | DH4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | - | - | 208/1 | 5.9 | 15 | 153 | DAIKIN | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM | DH4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 3 | 7.1485 | 208/1 | 19 | 20 | 153 | DAIKIN | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DH4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 5 | 11.9142 | 208/1 | 28 | 30 | 153 | DAIKIN | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DH4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 6 | 14.297 | 208/1 | 33 | 35 | 153 | DAIKIN | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DH4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 8 | 19.0627 | 208/1 | 42 | 45 | 153 | DAIKIN | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DH4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 10 | 23.8284 | 208/1 | 49 | 50 | 153 | DAIKIN | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DH4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 15 | 35.7425 | 208/1 | 70.9 | 80 | 153 | DAIKIN | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DH4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1340 | 0.75 | ECM | 80 | 67 | 59 | 40000 | 30400 | 39500 | 19 | 45.2739 | 208/1 | 92.5 | 100 | 153 | DAIKIN | DH4SEA4210 | 47 | 39500 | 7.8 HSPF2 | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 262 | 1 | 3.5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 19 | 1 | ECM | DH4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM | DH4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 3 | 5.9869 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DH4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 5 | 9.9781 | 208/1 | 29 | 30 | 153 | DAIKIN | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DH4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 6 | 11.9738 | 208/1 | 34 | 35 | 153 | DAIKIN | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DH4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 8 | 15.965 | 208/1 | 43 | 45 | 153 | DAIKIN | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DH4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 10 | 19.9563 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DH4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 15 | 29.9344 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DH4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 19 | 37.9169 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DH4SEA4810 | 47 | 46000 | 7.8 HSPF2 | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 269 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/1 | 19 | 1 | ECM | DH4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | - | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 3 | 4.7895 | 208/1 | 22 | 25 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 5 | 7.9825 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 6 | 9.579 | 208/1 | 36 | 40 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 8 | 12.772 | 208/1 | 45 | 45 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 10 | 15.965 | 208/1 | 52 | 60 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 15 | 23.9475 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 20 | 31.93 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 20 | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 25 | 39.9125 | 208/1 | 117 | 125 | 167 | DAIKIN | DH4SEA6010 | 47 | 57000 | 8.2 HSPF2 | 208/1 | 31.1 | 50 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 300 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/1 | 25 | 1 | ECM | DH4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | - | - | 208/1 | 5.8 | 15 | 112 | DAIKIN | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM | DH5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.5 | 88 | 0.55
DAIKIN | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 3 | 15.085 | 208/1 | 19 | 20 | 112 | DAIKIN | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM | DH5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.5 | 88 | 0.55
DAIKIN | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 5 | 25.1417 | 208/1 | 27 | 30 | 112 | DAIKIN | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM | DH5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.5 | 88 | 0.55
DAIKIN | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 6 | 30.1701 | 208/1 | 32.8 | 35 | 112 | DAIKIN | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM | DH5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.5 | 88 | 0.55
DAIKIN | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 8 | 40.2268 | 208/1 | 41.9 | 45 | 112 | DAIKIN | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM | DH5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.5 | 88 | 0.55
DAIKIN | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 10 | 50.2835 | 208/1 | 49.1 | 50 | 112 | DAIKIN | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM | DH5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.5 | 88 | 0.55
DAIKIN | AMST24BU1300 | 635 | 0.75 | ECM | 80 | 67 | 57 | 18000 | 12780 | 18800 | 15 | 75.4252 | 208/1 | 70.8 | 90 | 112 | DAIKIN | DH5SEA1810 | 47 | 18800 | 7.8 HSPF2 | 208/1 | 12.6 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 1.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM | DH5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.5 | 88 | 0.55
DAIKIN | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | - | - | 208/1 | 5.8 | 15 | 112 | DAIKIN | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM | DH5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.1875 | 83 | 0.55
DAIKIN | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 3 | 12.36 | 208/1 | 19 | 20 | 112 | DAIKIN | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM | DH5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.1875 | 83 | 0.55
DAIKIN | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 5 | 20.6 | 208/1 | 27 | 30 | 112 | DAIKIN | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM | DH5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.1875 | 83 | 0.55
DAIKIN | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 6 | 24.72 | 208/1 | 32.8 | 35 | 112 | DAIKIN | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM | DH5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.1875 | 83 | 0.55
DAIKIN | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 8 | 32.96 | 208/1 | 41.9 | 45 | 112 | DAIKIN | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM | DH5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.1875 | 83 | 0.55
DAIKIN | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 10 | 41.2 | 208/1 | 49.1 | 50 | 112 | DAIKIN | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM | DH5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.1875 | 83 | 0.55
DAIKIN | AMST24BU1300 | 775 | 0.75 | ECM | 80 | 67 | 59 | 24000 | 18000 | 24200 | 15 | 61.8 | 208/1 | 70.8 | 90 | 112 | DAIKIN | DH5SEA2410 | 47 | 24200 | 7.8 HSPF2 | 208/1 | 15.2 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 171 | 1 | 2 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM | DH5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.1875 | 83 | 0.55
DAIKIN | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | - | - | 208/1 | 5.6 | 15 | 129 | DAIKIN | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM | DH5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.875 | 94 | 0.55
DAIKIN | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 3 | 9.1229 | 208/1 | 19 | 20 | 129 | DAIKIN | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM | DH5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.875 | 94 | 0.55
DAIKIN | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 5 | 15.2048 | 208/1 | 27 | 30 | 129 | DAIKIN | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM | DH5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.875 | 94 | 0.55
DAIKIN | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 6 | 18.2457 | 208/1 | 32.7 | 35 | 129 | DAIKIN | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM | DH5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.875 | 94 | 0.55
DAIKIN | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 8 | 24.3276 | 208/1 | 42 | 45 | 129 | DAIKIN | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM | DH5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.875 | 94 | 0.55
DAIKIN | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 10 | 30.4095 | 208/1 | 49 | 50 | 129 | DAIKIN | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM | DH5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.875 | 94 | 0.55
DAIKIN | AMST30BU1300 | 1050 | 0.75 | ECM | 80 | 67 | 59 | 30000 | 23400 | 31200 | 15 | 45.6143 | 208/1 | 49.1 | 80 | 129 | DAIKIN | DH5SEA3010 | 47 | 31200 | 7.8 HSPF2 | 208/1 | 17.1 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 215 | 1 | 2.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM | DH5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 5.875 | 94 | 0.55
DAIKIN | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM | DH5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.9375 | 95 | 0.58
DAIKIN | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 3 | 9.579 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM | DH5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.9375 | 95 | 0.58
DAIKIN | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 5 | 15.965 | 208/1 | 29 | 35 | 153 | DAIKIN | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM | DH5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.9375 | 95 | 0.58
DAIKIN | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 6 | 19.158 | 208/1 | 34 | 40 | 153 | DAIKIN | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM | DH5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.9375 | 95 | 0.58
DAIKIN | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 8 | 25.544 | 208/1 | 43 | 50 | 153 | DAIKIN | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM | DH5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.9375 | 95 | 0.58
DAIKIN | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 10 | 31.93 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM | DH5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.9375 | 95 | 0.58
DAIKIN | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 15 | 47.895 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM | DH5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.9375 | 95 | 0.58
DAIKIN | AMST36CU1300 | 1000 | 0.75 | ECM | 80 | 67 | 58 | 35500 | 25205 | 36200 | 19 | 60.667 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DH5SEA3610 | 47 | 36200 | 7.8 HSPF2 | 208/1 | 24 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 222 | 1 | 3 | HEAT PUMP | 16.0 SEER2 | 208/1 | 19 | 1 | ECM | DH5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.9375 | 95 | 0.58
DAIKIN | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | - | - | 208/1 | 5.9 | 15 | 153 | DAIKIN | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM | DH5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 3 | 7.0956 | 208/1 | 19 | 20 | 153 | DAIKIN | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM | DH5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 5 | 11.8259 | 208/1 | 28 | 30 | 153 | DAIKIN | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM | DH5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 6 | 14.1911 | 208/1 | 33 | 35 | 153 | DAIKIN | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM | DH5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 8 | 18.9215 | 208/1 | 42 | 45 | 153 | DAIKIN | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM | DH5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 10 | 23.6519 | 208/1 | 49 | 50 | 153 | DAIKIN | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM | DH5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 15 | 35.4778 | 208/1 | 70.9 | 80 | 153 | DAIKIN | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM | DH5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST42CU1300 | 1350 | 0.75 | ECM | 80 | 67 | 59 | 42000 | 31920 | 40000 | 19 | 44.9385 | 208/1 | 92.5 | 100 | 153 | DAIKIN | DH5SEA4210 | 47 | 40000 | 7.8 HSPF2 | 208/1 | 21.4 | 35 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 257 | 1 | 3.5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 19 | 1 | ECM | DH5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 8.6875 | 139 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM | DH5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 3 | 5.9869 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM | DH5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 5 | 9.9781 | 208/1 | 29 | 30 | 153 | DAIKIN | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM | DH5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 6 | 11.9738 | 208/1 | 34 | 35 | 153 | DAIKIN | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM | DH5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 8 | 15.965 | 208/1 | 43 | 45 | 153 | DAIKIN | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM | DH5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 10 | 19.9563 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM | DH5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 15 | 29.9344 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM | DH5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 48600 | 38394 | 47100 | 19 | 37.9169 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DH5SEA4810 | 47 | 47100 | 7.8 HSPF2 | 208/1 | 28.3 | 45 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 264 | 1 | 4 | HEAT PUMP | 16.0 SEER2 | 208/1 | 19 | 1 | ECM | DH5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | - | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 3 | 4.7895 | 208/1 | 22 | 25 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 3 | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 5 | 7.9825 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 5 | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 6 | 9.579 | 208/1 | 36 | 40 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 6 | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 8 | 12.772 | 208/1 | 45 | 45 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 8 | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 10 | 15.965 | 208/1 | 52 | 60 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 10 | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 15 | 23.9475 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 15 | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 20 | 31.93 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 20 | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 60800 | 48032 | 60400 | 25 | 39.9125 | 208/1 | 117 | 125 | 167 | DAIKIN | DH5SEA6010 | 47 | 60400 | 8.2 HSPF2 | 208/1 | 38.8 | 60 | 95 | R32 | 16.0/12.0 (SEER2/EER2) | 309 | 1 | 5 | HEAT PUMP | 16.0 SEER2 | 208/1 | 25 | 1 | ECM | DH5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH5SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH5SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 11.5625 | 185 | 0.64
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | - | - | 208/1 | 4.9 | 15 | 115 | DAIKIN | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA1810 |  |  | DH6VSA1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 3 | 15.7033 | 208/1 | 18.4 | 20 | 115 | DAIKIN | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 3 | Inverter | Variable Speed ECM | DH6VSA1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA1810 |  |  | DH6VSA1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 5 | 26.1721 | 208/1 | 26.5 | 30 | 115 | DAIKIN | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH6VSA1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA1810 |  |  | DH6VSA1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 6 | 31.4066 | 208/1 | 32 | 35 | 115 | DAIKIN | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH6VSA1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA1810 |  |  | DH6VSA1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 8 | 41.8754 | 208/1 | 41 | 45 | 115 | DAIKIN | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH6VSA1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA1810 |  |  | DH6VSA1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | 17400 | 10 | 52.3443 | 208/1 | 48.5 | 50 | 115 | DAIKIN | DH6VSA1810 | 47 | 17400 | 8.8 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 19.0/12.0 (SEER2/EER2) | 122 | Inverter | 1.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH6VSA1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA1810 |  |  | DH6VSA1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | - | - | 208/1 | 4.9 | 15 | 115 | DAIKIN | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA2410 |  |  | DH6VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 3 | 11.9738 | 208/1 | 18.4 | 20 | 115 | DAIKIN | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 3 | Inverter | Variable Speed ECM | DH6VSA2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA2410 |  |  | DH6VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 5 | 19.9563 | 208/1 | 26.5 | 30 | 115 | DAIKIN | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH6VSA2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA2410 |  |  | DH6VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 6 | 23.9475 | 208/1 | 32 | 35 | 115 | DAIKIN | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH6VSA2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA2410 |  |  | DH6VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 8 | 31.93 | 208/1 | 41 | 45 | 115 | DAIKIN | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH6VSA2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA2410 |  |  | DH6VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | 23200 | 10 | 39.9125 | 208/1 | 48.5 | 50 | 115 | DAIKIN | DH6VSA2410 | 47 | 23200 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 122 | Inverter | 2 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH6VSA2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA2410 |  |  | DH6VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | - | - | 208/1 | 6.5 | 15 | 140 | DAIKIN | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3010 |  |  | DH6VSA3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 5 | 15.8069 | 208/1 | 28.1 | 30 | 140 | DAIKIN | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH6VSA3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3010 |  |  | DH6VSA3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 6 | 18.9683 | 208/1 | 33.6 | 35 | 140 | DAIKIN | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH6VSA3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3010 |  |  | DH6VSA3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 8 | 25.2911 | 208/1 | 42.6 | 45 | 140 | DAIKIN | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH6VSA3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3010 |  |  | DH6VSA3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 10 | 31.6139 | 208/1 | 49.9 | 50 | 140 | DAIKIN | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH6VSA3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3010 |  |  | DH6VSA3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 15 | 47.4208 | 208/1 | 71.5 | 80 | 140 | DAIKIN | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH6VSA3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3010 |  |  | DH6VSA3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | 28800 | 19 | 60.0663 | 208/1 | 93.2 | 100 | 140 | DAIKIN | DH6VSA3010 | 47 | 28800 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 132 | Inverter | 2.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM | DH6VSA3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3010 |  |  | DH6VSA3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | - | - | 208/1 | 6.5 | 15 | 140 | DAIKIN | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA3610 | DFVE42CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3610 |  |  | DH6VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 5 | 12.6706 | 208/1 | 28.1 | 30 | 140 | DAIKIN | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH6VSA3610 | DFVE42CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3610 |  |  | DH6VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 6 | 15.2048 | 208/1 | 33.6 | 35 | 140 | DAIKIN | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH6VSA3610 | DFVE42CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3610 |  |  | DH6VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 8 | 20.273 | 208/1 | 42.6 | 45 | 140 | DAIKIN | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH6VSA3610 | DFVE42CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3610 |  |  | DH6VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 10 | 25.3413 | 208/1 | 49.9 | 50 | 140 | DAIKIN | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH6VSA3610 | DFVE42CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3610 |  |  | DH6VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 15 | 38.0119 | 208/1 | 71.5 | 80 | 140 | DAIKIN | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH6VSA3610 | DFVE42CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3610 |  |  | DH6VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE42CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | 34600 | 19 | 48.1484 | 208/1 | 93.2 | 100 | 140 | DAIKIN | DH6VSA3610 | 47 | 34600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 137 | Inverter | 3 | HEAT PUMP | 16.2 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM | DH6VSA3610 | DFVE42CP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA3610 |  |  | DH6VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | - | - | 208/1 | 6.5 | 15 | 150 | DAIKIN | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4210 |  |  | DH6VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 5 | 12.0947 | 208/1 | 28.1 | 30 | 150 | DAIKIN | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH6VSA4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4210 |  |  | DH6VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 6 | 14.5136 | 208/1 | 33.6 | 35 | 150 | DAIKIN | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH6VSA4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4210 |  |  | DH6VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 8 | 19.3515 | 208/1 | 42.6 | 45 | 150 | DAIKIN | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH6VSA4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4210 |  |  | DH6VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 10 | 24.1894 | 208/1 | 49.9 | 50 | 150 | DAIKIN | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH6VSA4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4210 |  |  | DH6VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 15 | 36.2841 | 208/1 | 71.5 | 80 | 150 | DAIKIN | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH6VSA4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4210 |  |  | DH6VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | 40000 | 20 | 48.3788 | 208/1 | 93.2 | 100 | 150 | DAIKIN | DH6VSA4210 | 47 | 40000 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 3.5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DH6VSA4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4210 |  |  | DH6VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | - | - | 208/1 | 6.5 | 15 | 150 | DAIKIN | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4810 |  |  | DH6VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 5 | 11.5688 | 208/1 | 28.1 | 30 | 150 | DAIKIN | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH6VSA4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4810 |  |  | DH6VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 6 | 13.8826 | 208/1 | 33.6 | 35 | 150 | DAIKIN | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH6VSA4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4810 |  |  | DH6VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 8 | 18.5101 | 208/1 | 42.6 | 45 | 150 | DAIKIN | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH6VSA4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4810 |  |  | DH6VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 10 | 23.1377 | 208/1 | 49.9 | 50 | 150 | DAIKIN | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH6VSA4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4810 |  |  | DH6VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 15 | 34.7065 | 208/1 | 71.5 | 80 | 150 | DAIKIN | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH6VSA4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4810 |  |  | DH6VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33125 | 45500 | 20 | 46.2754 | 208/1 | 93.2 | 100 | 150 | DAIKIN | DH6VSA4810 | 47 | 45500 | 8.2 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 168 | Inverter | 4 | HEAT PUMP | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DH6VSA4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA4810 |  |  | DH6VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA6010 |  |  | DH6VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | DAIKIN | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH6VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA6010 |  |  | DH6VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | DAIKIN | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH6VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA6010 |  |  | DH6VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | DAIKIN | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH6VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA6010 |  |  | DH6VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | DAIKIN | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH6VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA6010 |  |  | DH6VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH6VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA6010 |  |  | DH6VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DH6VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA6010 |  |  | DH6VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | 54500 | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | DAIKIN | DH6VSA6010 | 47 | 54500 | 8.2 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 179 | Inverter | 5 | HEAT PUMP | 16.2 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM | DH6VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH6VSA | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH6VSA | INSTALLATION MANUAL - DFVE |  | DH6VSA6010 |  |  | DH6VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | - | - | 208/1 | 4.9 | 15 | 129 | DAIKIN | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM | DH7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.75 | 15 | 6.4375 | 103 | 0.55
DAIKIN | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 3 | 12.2808 | 208/1 | 18.4 | 20 | 129 | DAIKIN | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 3 | 2 | Variable Speed ECM | DH7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.75 | 15 | 6.4375 | 103 | 0.55
DAIKIN | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 5 | 20.4679 | 208/1 | 26.5 | 30 | 129 | DAIKIN | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM | DH7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.75 | 15 | 6.4375 | 103 | 0.55
DAIKIN | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 6 | 24.5615 | 208/1 | 32 | 35 | 129 | DAIKIN | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM | DH7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.75 | 15 | 6.4375 | 103 | 0.55
DAIKIN | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 8 | 32.7487 | 208/1 | 41 | 45 | 129 | DAIKIN | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM | DH7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.75 | 15 | 6.4375 | 103 | 0.55
DAIKIN | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 10 | 40.9359 | 208/1 | 48.2 | 50 | 129 | DAIKIN | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM | DH7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.75 | 15 | 6.4375 | 103 | 0.55
DAIKIN | DMVT30BP1300 | 780 | 0.5 | Variable Speed ECM | 80 | 67 | 58 | 24000 | 18000 | 23400 | 15 | 61.4038 | 208/1 | 69.9 | 70 | 129 | DAIKIN | DH7TCA2410 | 47 | 23400 | 8.2 HSPF2 | 208/1 | 15 | 20 | 95 | R32 | 17.5/12.5 (SEER2/EER2 | 219 | 2 | 2 | HEAT PUMP | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM | DH7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.75 | 15 | 6.4375 | 103 | 0.55
DAIKIN | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | - | - | 208/1 | 6.5 | 15 | 153 | DAIKIN | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM | DH7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 8.0625 | 129 | 0.58
DAIKIN | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 5 | 13.416 | 208/1 | 28.2 | 35 | 153 | DAIKIN | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM | DH7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 8.0625 | 129 | 0.58
DAIKIN | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 6 | 16.0992 | 208/1 | 33.6 | 40 | 153 | DAIKIN | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM | DH7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 8.0625 | 129 | 0.58
DAIKIN | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 8 | 21.4655 | 208/1 | 42.6 | 50 | 153 | DAIKIN | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM | DH7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 8.0625 | 129 | 0.58
DAIKIN | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 10 | 26.8319 | 208/1 | 49.8 | 60 | 153 | DAIKIN | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM | DH7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 8.0625 | 129 | 0.58
DAIKIN | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 15 | 40.2479 | 208/1 | 71.5 | 80 | 153 | DAIKIN | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM | DH7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 8.0625 | 129 | 0.58
DAIKIN | DMVT42CP1300 | 1190 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 34800 | 27144 | 34400 | 19 | 50.9807 | 208/1 | 93.2 | 100 | 153 | DAIKIN | DH7TCA3610 | 47 | 34400 | 8.1 HSPF2 | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 262 | 2 | 3 | HEAT PUMP | 17.2 SEER2 | 208/1 | 19 | 2 | Variable Speed ECM | DH7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 8.0625 | 129 | 0.58
DAIKIN | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM | DH7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 14.3125 | 229 | 0.64
DAIKIN | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 5 | 10.4346 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM | DH7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 14.3125 | 229 | 0.64
DAIKIN | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 6 | 12.5216 | 208/1 | 35.7 | 40 | 167 | DAIKIN | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM | DH7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 14.3125 | 229 | 0.64
DAIKIN | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 8 | 16.6954 | 208/1 | 44.7 | 45 | 167 | DAIKIN | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM | DH7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 14.3125 | 229 | 0.64
DAIKIN | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 10 | 20.8693 | 208/1 | 52 | 60 | 167 | DAIKIN | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM | DH7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 14.3125 | 229 | 0.64
DAIKIN | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 15 | 31.3039 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM | DH7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 14.3125 | 229 | 0.64
DAIKIN | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 20 | 41.7386 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 20 | 2 | Variable Speed ECM | DH7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 14.3125 | 229 | 0.64
DAIKIN | DMVT60DP1300 | 1530 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 35340 | 48800 | 25 | 52.1732 | 208/1 | 117 | 125 | 167 | DAIKIN | DH7TCA4810 | 47 | 48800 | 8.2 HSPF2 | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 308 | 2 | 4 | HEAT PUMP | 17.2 SEER2 | 208/1 | 25 | 2 | Variable Speed ECM | DH7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 14.3125 | 229 | 0.64
DAIKIN | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM | DH7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 12.375 | 198 | 0.64
DAIKIN | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 5 | 8.4471 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM | DH7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 12.375 | 198 | 0.64
DAIKIN | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 6 | 10.1365 | 208/1 | 35.7 | 40 | 167 | DAIKIN | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM | DH7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 12.375 | 198 | 0.64
DAIKIN | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 8 | 13.5153 | 208/1 | 44.7 | 45 | 167 | DAIKIN | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM | DH7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 12.375 | 198 | 0.64
DAIKIN | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 10 | 16.8942 | 208/1 | 52 | 60 | 167 | DAIKIN | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM | DH7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 12.375 | 198 | 0.64
DAIKIN | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 15 | 25.3413 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM | DH7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 12.375 | 198 | 0.64
DAIKIN | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 20 | 33.7884 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 20 | 2 | Variable Speed ECM | DH7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 12.375 | 198 | 0.64
DAIKIN | DMVT60DP1300 | 1890 | 1 | Variable Speed ECM | 80 | 67 | 58 | 57000 | 42750 | 58000 | 25 | 42.2354 | 208/1 | 117 | 125 | 167 | DAIKIN | DH7TCA6010 | 47 | 58000 | 8.2 HSPF2 | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/11.7 (SEER2/EER2) | 306 | 2 | 5 | HEAT PUMP | 17.2 SEER2 | 208/1 | 25 | 2 | Variable Speed ECM | DH7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DH7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DH7TC | INSTALLATION MANUAL - DMVT | [9 empty] | R-32 | 80 | - | 150 | 0.375 | 0.875 | 15 | 12.375 | 198 | 0.64
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | - | - | 208/1 | 6.5 | 15 | 140 | DAIKIN | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH7VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA2410 |  |  | DH7VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 5 | 15.8069 | 208/1 | 28.1 | 30 | 140 | DAIKIN | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH7VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA2410 |  |  | DH7VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 6 | 18.9683 | 208/1 | 33.6 | 35 | 140 | DAIKIN | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH7VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA2410 |  |  | DH7VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 8 | 25.2911 | 208/1 | 42.6 | 45 | 140 | DAIKIN | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH7VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA2410 |  |  | DH7VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 10 | 31.6139 | 208/1 | 49.9 | 50 | 140 | DAIKIN | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH7VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA2410 |  |  | DH7VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 15 | 47.4208 | 208/1 | 71.5 | 80 | 140 | DAIKIN | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH7VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA2410 |  |  | DH7VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 59 | 23200 | 17400 | 23200 | 19 | 60.0663 | 208/1 | 93.2 | 100 | 140 | DAIKIN | DH7VSA2410 | 47 | 23200 | 8.8 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 132 | Inverter | 2 | HEAT PUMP | 17.5 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM | DH7VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA2410 |  |  | DH7VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | - | - | 208/1 | 6.5 | 15 | 150 | DAIKIN | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH7VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA3610 |  |  | DH7VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 5 | 12.0947 | 208/1 | 28.1 | 30 | 150 | DAIKIN | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH7VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA3610 |  |  | DH7VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 6 | 14.5136 | 208/1 | 33.6 | 35 | 150 | DAIKIN | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH7VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA3610 |  |  | DH7VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 8 | 19.3515 | 208/1 | 42.6 | 45 | 150 | DAIKIN | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH7VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA3610 |  |  | DH7VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 10 | 24.1894 | 208/1 | 49.9 | 50 | 150 | DAIKIN | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH7VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA3610 |  |  | DH7VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 15 | 36.2841 | 208/1 | 71.5 | 80 | 150 | DAIKIN | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH7VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA3610 |  |  | DH7VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 35000 | 27650 | 35000 | 20 | 48.3788 | 208/1 | 93.2 | 100 | 150 | DAIKIN | DH7VSA3610 | 47 | 35000 | 8.8 HSPF2 | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 168 | Inverter | 3 | HEAT PUMP | 17.5 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DH7VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA3610 |  |  | DH7VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH7VSA4210 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4210 |  |  | DH7VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 5 | 11.5688 | 208/1 | 30.2 | 35 | 167 | DAIKIN | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH7VSA4210 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4210 |  |  | DH7VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 6 | 13.8826 | 208/1 | 35.8 | 40 | 167 | DAIKIN | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH7VSA4210 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4210 |  |  | DH7VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 8 | 18.5101 | 208/1 | 44.8 | 45 | 167 | DAIKIN | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH7VSA4210 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4210 |  |  | DH7VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 10 | 23.1377 | 208/1 | 52 | 60 | 167 | DAIKIN | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH7VSA4210 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4210 |  |  | DH7VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 15 | 34.7065 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH7VSA4210 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4210 |  |  | DH7VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 20 | 46.2754 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DH7VSA4210 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4210 |  |  | DH7VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 59 | 41000 | 29520 | 41000 | 25 | 57.8442 | 208/1 | 117 | 125 | 167 | DAIKIN | DH7VSA4210 | 47 | 41000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 3.5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM | DH7VSA4210 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4210 |  |  | DH7VSA4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH7VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4810 |  |  | DH7VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | DAIKIN | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH7VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4810 |  |  | DH7VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | DAIKIN | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH7VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4810 |  |  | DH7VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | DAIKIN | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH7VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4810 |  |  | DH7VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | DAIKIN | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH7VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4810 |  |  | DH7VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH7VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4810 |  |  | DH7VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DH7VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4810 |  |  | DH7VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 46500 | 33480 | 54000 | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | DAIKIN | DH7VSA4810 | 47 | 54000 | 8.8 HSPF2 | 208/1 | 37.5 | 40 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 179 | Inverter | 4 | HEAT PUMP | 17.5 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM | DH7VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA4810 |  |  | DH7VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH7VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA6010 |  |  | DH7VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | DAIKIN | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DH7VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA6010 |  |  | DH7VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | DAIKIN | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DH7VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA6010 |  |  | DH7VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | DAIKIN | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DH7VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA6010 |  |  | DH7VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | DAIKIN | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DH7VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA6010 |  |  | DH7VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DH7VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA6010 |  |  | DH7VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DH7VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA6010 |  |  | DH7VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 52000 | 37440 | 54000 | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | DAIKIN | DH7VSA6010 | 47 | 54000 | 9.0 HSPF2 | 208/1 | 34.4 | 40 | 95 | R32 | 18.0/9.8 (SEER2/EER2) | 236 | Inverter | 5 | HEAT PUMP | 17.5 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM | DH7VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DH7VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH7VS | INSTALLATION MANUAL - DFVE |  | DH7VSA6010 |  |  | DH7VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 58.4375 | 23000 | 18630 | 23000 | - | - | 115/1 | 6.5 | 15 | 155 | DAIKIN | DH9VSA241C | 17 | 23000 | 9.2 HSPF2 | 208/1 | 17.4 | 20 | 95 | R32 | 19.2 / 11.7 (SEER2/EER2) | 230 | Inverter | 2 | HEAT PUMP | 19.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH9VSA241C | DFVE48CP1300 |  |  | ENGINEERING MANUAL - DH9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH9VS | INSTALLATION MANUAL - DFVE | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.3915 | 34200 | 28044 | 32000 | - | - | 115/1 | 6.5 | 15 | 155 | DAIKIN | DH9VSA361C | 17 | 32000 | 9.2 HSPF2 | 208/1 | 21.8 | 25 | 95 | R32 | 19.0 / 11.7 (SEER2/EER2) | 230 | Inverter | 3 | HEAT PUMP | 19.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DH9VSA361C | DFVE48CP1300 |  |  | ENGINEERING MANUAL - DH9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DH9VS | INSTALLATION MANUAL - DFVE | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | - | 1 | ECM | DH4SEA3630 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3630 |  |  | DH4SEA3630 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 3 | 8.0496 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 3 | 1 | ECM | DH4SEA3630 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3630 |  |  | DH4SEA3630 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 5 | 13.416 | 208/1 | 29 | 35 | 153 | DAIKIN | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 5 | 1 | ECM | DH4SEA3630 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3630 |  |  | DH4SEA3630 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 6 | 16.0992 | 208/1 | 34 | 40 | 153 | DAIKIN | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 6 | 1 | ECM | DH4SEA3630 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3630 |  |  | DH4SEA3630 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 8 | 21.4655 | 208/1 | 43 | 50 | 153 | DAIKIN | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 8 | 1 | ECM | DH4SEA3630 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3630 |  |  | DH4SEA3630 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 10 | 26.8319 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 10 | 1 | ECM | DH4SEA3630 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3630 |  |  | DH4SEA3630 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 15 | 40.2479 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 15 | 1 | ECM | DH4SEA3630 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3630 |  |  | DH4SEA3630 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 19 | 50.9807 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DH4SEA3630 | 47 | 34400 | 7.5 HSPF2 | 208/3 | 14.2 | 20 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 208/3 | 19 | 1 | ECM | DH4SEA3630 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3630 |  |  | DH4SEA3630 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | - | 1 | ECM | DH4SEA4830 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4830 |  |  | DH4SEA4830 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 3 | 5.9869 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 3 | 1 | ECM | DH4SEA4830 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4830 |  |  | DH4SEA4830 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 5 | 9.9781 | 208/1 | 29 | 30 | 153 | DAIKIN | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 5 | 1 | ECM | DH4SEA4830 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4830 |  |  | DH4SEA4830 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 6 | 11.9738 | 208/1 | 34 | 35 | 153 | DAIKIN | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 6 | 1 | ECM | DH4SEA4830 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4830 |  |  | DH4SEA4830 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 8 | 15.965 | 208/1 | 43 | 45 | 153 | DAIKIN | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 8 | 1 | ECM | DH4SEA4830 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4830 |  |  | DH4SEA4830 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 10 | 19.9563 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 10 | 1 | ECM | DH4SEA4830 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4830 |  |  | DH4SEA4830 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 15 | 29.9344 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 15 | 1 | ECM | DH4SEA4830 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4830 |  |  | DH4SEA4830 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 19 | 37.9169 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DH4SEA4830 | 47 | 46000 | 7.8 HSPF2 | 208/3 | 16.5 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 208/3 | 19 | 1 | ECM | DH4SEA4830 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4830 |  |  | DH4SEA4830 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | - | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 3 | 4.7895 | 208/1 | 22 | 25 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 3 | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 5 | 7.9825 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 5 | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 6 | 9.579 | 208/1 | 36 | 40 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 6 | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 8 | 12.772 | 208/1 | 45 | 45 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 8 | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 10 | 15.965 | 208/1 | 52 | 60 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 10 | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 15 | 23.9475 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 15 | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 20 | 31.93 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 20 | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 25 | 39.9125 | 208/1 | 117 | 125 | 167 | DAIKIN | DH4SEA6030 | 47 | 57000 | 8.2 HSPF2 | 208/3 | 20.5 | 35 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 208/3 | 25 | 1 | ECM | DH4SEA6030 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6030 |  |  | DH4SEA6030 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | - | 1 | ECM | DH4SEA3640 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3640 |  |  | DH4SEA3640 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 3 | 8.0496 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 3 | 1 | ECM | DH4SEA3640 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3640 |  |  | DH4SEA3640 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 5 | 13.416 | 208/1 | 29 | 35 | 153 | DAIKIN | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 5 | 1 | ECM | DH4SEA3640 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3640 |  |  | DH4SEA3640 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 6 | 16.0992 | 208/1 | 34 | 40 | 153 | DAIKIN | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 6 | 1 | ECM | DH4SEA3640 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3640 |  |  | DH4SEA3640 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 8 | 21.4655 | 208/1 | 43 | 50 | 153 | DAIKIN | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 8 | 1 | ECM | DH4SEA3640 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3640 |  |  | DH4SEA3640 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 10 | 26.8319 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 10 | 1 | ECM | DH4SEA3640 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3640 |  |  | DH4SEA3640 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 15 | 40.2479 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 15 | 1 | ECM | DH4SEA3640 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3640 |  |  | DH4SEA3640 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST36CU1300 | 1190 | 0.75 | ECM | 80 | 67 | 59 | 35000 | 26600 | 34400 | 19 | 50.9807 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DH4SEA3640 | 47 | 34400 | 7.5 HSPF2 | 460/3 | 6.7 | 10 | 95 | R32 | 15.0/12.5 (SEER2/EER2) | 199 | 1 | 3 | HEAT PUMP | 14.3 SEER2 | 460/3 | 19 | 1 | ECM | DH4SEA3640 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA3640 |  |  | DH4SEA3640 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1875 | 83 | 0.58
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | - | 1 | ECM | DH4SEA4840 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4840 |  |  | DH4SEA4840 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 3 | 5.9869 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 3 | 1 | ECM | DH4SEA4840 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4840 |  |  | DH4SEA4840 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 5 | 9.9781 | 208/1 | 29 | 30 | 153 | DAIKIN | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 5 | 1 | ECM | DH4SEA4840 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4840 |  |  | DH4SEA4840 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 6 | 11.9738 | 208/1 | 34 | 35 | 153 | DAIKIN | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 6 | 1 | ECM | DH4SEA4840 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4840 |  |  | DH4SEA4840 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 8 | 15.965 | 208/1 | 43 | 45 | 153 | DAIKIN | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 8 | 1 | ECM | DH4SEA4840 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4840 |  |  | DH4SEA4840 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 10 | 19.9563 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 10 | 1 | ECM | DH4SEA4840 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4840 |  |  | DH4SEA4840 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 15 | 29.9344 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 15 | 1 | ECM | DH4SEA4840 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4840 |  |  | DH4SEA4840 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST48CU1300 | 1600 | 0.75 | ECM | 80 | 67 | 59 | 46100 | 36419 | 46000 | 19 | 37.9169 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DH4SEA4840 | 47 | 46000 | 7.8 HSPF2 | 460/3 | 8 | 10 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 266 | 1 | 4 | HEAT PUMP | 14.3 SEER2 | 460/3 | 19 | 1 | ECM | DH4SEA4840 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA4840 |  |  | DH4SEA4840 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 10.875 | 174 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | - | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 3 | 4.7895 | 208/1 | 22 | 25 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 3 | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 5 | 7.9825 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 5 | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 6 | 9.579 | 208/1 | 36 | 40 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 6 | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 8 | 12.772 | 208/1 | 45 | 45 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 8 | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 10 | 15.965 | 208/1 | 52 | 60 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 10 | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 15 | 23.9475 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 15 | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 20 | 31.93 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 20 | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | AMST60DU1300 | 2000 | 1 | ECM | 80 | 67 | 59 | 57300 | 44121 | 57000 | 25 | 39.9125 | 208/1 | 117 | 125 | 167 | DAIKIN | DH4SEA6040 | 47 | 57000 | 8.2 HSPF2 | 460/3 | 10.4 | 15 | 95 | R32 | 14.5/12.5 (SEER2/EER2) | 288 | 1 | 5 | HEAT PUMP | 14.3 SEER2 | 460/3 | 25 | 1 | ECM | DH4SEA6040 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DH4SEA THREE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DH4SEA THREE PHASE | INSTALLATION MANUAL - AMST |  | DH4SEA6040 |  |  | DH4SEA6040 |  |  |  |  | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 12.125 | 194 | 0.64
DAIKIN | DAQ09033 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | - | - | 208/3 | 15.5 | 20 | 430 | DAIKIN | DH6TE09030 | 47 | 85000 | 2.25 COP | 208/3 | 38.7 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 | 7.5 | HEAT PUMP | 16.0 IEER | 208/3 | - | 2 | ECM | DH6TE09030 | DAQ09033 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE09030 |  |  | DH6TE09030 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09033 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 15 | 17.1054 | 208/3 | 54.8 | 60 | 430 | DAIKIN | DH6TE09030 | 47 | 85000 | 2.25 COP | 208/3 | 38.7 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 | 7.5 | HEAT PUMP | 16.0 IEER | 208/3 | 15 | 2 | ECM | DH6TE09030 | DAQ09033 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE09030 |  |  | DH6TE09030 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09033 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 20 | 22.8071 | 208/3 | 67.3 | 70 | 430 | DAIKIN | DH6TE09030 | 47 | 85000 | 2.25 COP | 208/3 | 38.7 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 | 7.5 | HEAT PUMP | 16.0 IEER | 208/3 | 20 | 2 | ECM | DH6TE09030 | DAQ09033 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE09030 |  |  | DH6TE09030 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09033 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 30 | 34.2107 | 208/3 | 92.3 | 100 | 430 | DAIKIN | DH6TE09030 | 47 | 85000 | 2.25 COP | 208/3 | 38.7 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 | 7.5 | HEAT PUMP | 16.0 IEER | 208/3 | 30 | 2 | ECM | DH6TE09030 | DAQ09033 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE09030 |  |  | DH6TE09030 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | - | - | 208/3 | 15.5 | 20 | 430 | DAIKIN | DH6TE12030 | 47 | 97000 | 2.25 COP | 208/3 | 41.6 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 | 10 | HEAT PUMP | 16.0 IEER | 208/3 | - | 2 | ECM | DH6TE12030 | DAQ12033 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE12030 |  |  | DH6TE12030 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 15 | 12.6539 | 208/3 | 54.8 | 60 | 430 | DAIKIN | DH6TE12030 | 47 | 97000 | 2.25 COP | 208/3 | 41.6 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 | 10 | HEAT PUMP | 16.0 IEER | 208/3 | 15 | 2 | ECM | DH6TE12030 | DAQ12033 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE12030 |  |  | DH6TE12030 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 20 | 16.8719 | 208/3 | 67.3 | 70 | 430 | DAIKIN | DH6TE12030 | 47 | 97000 | 2.25 COP | 208/3 | 41.6 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 | 10 | HEAT PUMP | 16.0 IEER | 208/3 | 20 | 2 | ECM | DH6TE12030 | DAQ12033 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE12030 |  |  | DH6TE12030 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 30 | 25.3078 | 208/3 | 92.3 | 100 | 430 | DAIKIN | DH6TE12030 | 47 | 97000 | 2.25 COP | 208/3 | 41.6 | 50 | 95 | R32 | 16.0 IEER | 417 | 2 | 10 | HEAT PUMP | 16.0 IEER | 208/3 | 30 | 2 | ECM | DH6TE12030 | DAQ12033 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE12030 |  |  | DH6TE12030 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ09034 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | - | - | 460/3 | 5.2 | 15 | 430 | DAIKIN | DH6TE09040 | 47 | 85000 | 2.25 COP | 460/3 | 17.9 | 20 | 95 | R32 | 16.0 IEER | 417 | 2 | 7.5 | HEAT PUMP | 16.0 IEER | 460/3 | - | 2 | ECM | DH6TE09040 | DAQ09034 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE09040 |  |  | DH6TE09040 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09034 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 15 | 17.1054 | 460/3 | 27.4 | 30 | 430 | DAIKIN | DH6TE09040 | 47 | 85000 | 2.25 COP | 460/3 | 17.9 | 20 | 95 | R32 | 16.0 IEER | 417 | 2 | 7.5 | HEAT PUMP | 16.0 IEER | 460/3 | 15 | 2 | ECM | DH6TE09040 | DAQ09034 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE09040 |  |  | DH6TE09040 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09034 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 20 | 22.8071 | 460/3 | 34.6 | 35 | 430 | DAIKIN | DH6TE09040 | 47 | 85000 | 2.25 COP | 460/3 | 17.9 | 20 | 95 | R32 | 16.0 IEER | 417 | 2 | 7.5 | HEAT PUMP | 16.0 IEER | 460/3 | 20 | 2 | ECM | DH6TE09040 | DAQ09034 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE09040 |  |  | DH6TE09040 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09034 | 2800 | 1 | ECM | 80 | 67 | 58.6 | 91999 | 64399 | 85000 | 30 | 34.2107 | 460/3 | 49.1 | 50 | 430 | DAIKIN | DH6TE09040 | 47 | 85000 | 2.25 COP | 460/3 | 17.9 | 20 | 95 | R32 | 16.0 IEER | 417 | 2 | 7.5 | HEAT PUMP | 16.0 IEER | 460/3 | 30 | 2 | ECM | DH6TE09040 | DAQ09034 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE09040 |  |  | DH6TE09040 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | - | - | 460/3 | 5.2 | 15 | 430 | DAIKIN | DH6TE12040 | 47 | 97000 | 2.25 COP | 460/3 | 20.8 | 25 | 95 | R32 | 16.0 IEER | 417 | 2 | 10 | HEAT PUMP | 16.0 IEER | 460/3 | - | 2 | ECM | DH6TE12040 | DAQ12034 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE12040 |  |  | DH6TE12040 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 15 | 12.6539 | 460/3 | 27.4 | 30 | 430 | DAIKIN | DH6TE12040 | 47 | 97000 | 2.25 COP | 460/3 | 20.8 | 25 | 95 | R32 | 16.0 IEER | 417 | 2 | 10 | HEAT PUMP | 16.0 IEER | 460/3 | 15 | 2 | ECM | DH6TE12040 | DAQ12034 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE12040 |  |  | DH6TE12040 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 20 | 16.8719 | 460/3 | 34.6 | 35 | 430 | DAIKIN | DH6TE12040 | 47 | 97000 | 2.25 COP | 460/3 | 20.8 | 25 | 95 | R32 | 16.0 IEER | 417 | 2 | 10 | HEAT PUMP | 16.0 IEER | 460/3 | 20 | 2 | ECM | DH6TE12040 | DAQ12034 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE12040 |  |  | DH6TE12040 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 59.2 | 114999 | 91999 | 97000 | 30 | 25.3078 | 460/3 | 49.1 | 50 | 430 | DAIKIN | DH6TE12040 | 47 | 97000 | 2.25 COP | 460/3 | 20.8 | 25 | 95 | R32 | 16.0 IEER | 417 | 2 | 10 | HEAT PUMP | 16.0 IEER | 460/3 | 30 | 2 | ECM | DH6TE12040 | DAQ12034 |  |  | ENGINEERING MANUAL - DH6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DH6TE | INSTALLATION MANUAL - DAQ |  | DH6TE12040 |  |  | DH6TE12040 |  |  |  |  | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | - | - | 208/1 | 5.8 | 15 | 112 | DAIKIN | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM | DC4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 3 | 15.45 | 208/1 | 19 | 20 | 112 | DAIKIN | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DC4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 5 | 25.75 | 208/1 | 27 | 30 | 112 | DAIKIN | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DC4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 6 | 30.9 | 208/1 | 32.8 | 35 | 112 | DAIKIN | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DC4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 8 | 41.2 | 208/1 | 41.9 | 45 | 112 | DAIKIN | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DC4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 10 | 51.5 | 208/1 | 49.1 | 50 | 112 | DAIKIN | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DC4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.3381 | 17600 | 12496 | - | 15 | 77.25 | 208/1 | 70.8 | 90 | 112 | DAIKIN | DC4SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.0 (SEER2/EER2) | 129 | 1 | 1.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DC4SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | - | - | 208/1 | 5.8 | 15 | 112 | DAIKIN | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM | DC4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 3 | 12.6039 | 208/1 | 19 | 20 | 112 | DAIKIN | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DC4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 5 | 21.0066 | 208/1 | 27 | 30 | 112 | DAIKIN | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DC4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 6 | 25.2079 | 208/1 | 32.8 | 35 | 112 | DAIKIN | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DC4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 8 | 33.6105 | 208/1 | 41.9 | 45 | 112 | DAIKIN | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DC4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 10 | 42.0132 | 208/1 | 49.1 | 50 | 112 | DAIKIN | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DC4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.4737 | 23400 | 16848 | - | 15 | 63.0197 | 208/1 | 70.8 | 90 | 112 | DAIKIN | DC4SEA2410 | - | - | - | 208/1 | 13.5 | 15 | 95 | R32 | 14.5/11.7 (SEER2/EER2) | 151 | 1 | 2 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DC4SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 3.625 | 58 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | - | - | 208/1 | 5.6 | 15 | 129 | DAIKIN | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM | DC4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 3 | 10.0832 | 208/1 | 19 | 20 | 129 | DAIKIN | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DC4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 5 | 16.8053 | 208/1 | 27 | 30 | 129 | DAIKIN | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DC4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 6 | 20.1663 | 208/1 | 32.7 | 35 | 129 | DAIKIN | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DC4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 8 | 26.8884 | 208/1 | 42 | 45 | 129 | DAIKIN | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DC4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 10 | 33.6105 | 208/1 | 49 | 50 | 129 | DAIKIN | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DC4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.5166 | 28400 | 21016 | - | 15 | 50.4158 | 208/1 | 49.1 | 80 | 129 | DAIKIN | DC4SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 167 | 1 | 2.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DC4SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4 | 64 | 0.55
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM | DC4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 3 | 8.1872 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DC4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 5 | 13.6453 | 208/1 | 29 | 35 | 153 | DAIKIN | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DC4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 6 | 16.3744 | 208/1 | 34 | 40 | 153 | DAIKIN | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DC4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 8 | 21.8325 | 208/1 | 43 | 50 | 153 | DAIKIN | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DC4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 10 | 27.2906 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DC4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 15 | 40.9359 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DC4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.3099 | 34400 | 26144 | - | 19 | 51.8521 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DC4SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 173 | 1 | 3 | COOLING ONLY | 14.3 SEER2 | 208/1 | 19 | 1 | ECM | DC4SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 4.3125 | 69 | 0.58
DAIKIN | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | - | - | 208/1 | 5.9 | 15 | 153 | DAIKIN | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM | DC4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 3 | 6.8914 | 208/1 | 19 | 20 | 153 | DAIKIN | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DC4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 5 | 11.4856 | 208/1 | 28 | 30 | 153 | DAIKIN | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DC4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 6 | 13.7827 | 208/1 | 33 | 35 | 153 | DAIKIN | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DC4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 8 | 18.377 | 208/1 | 42 | 45 | 153 | DAIKIN | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DC4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 10 | 22.9712 | 208/1 | 49 | 50 | 153 | DAIKIN | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DC4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 15 | 34.4568 | 208/1 | 70.9 | 80 | 153 | DAIKIN | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DC4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | AMST42CU1300 | 1390 | 0.75 | ECM | 80 | 67 | 59.4831 | 40000 | 30800 | - | 19 | 43.6453 | 208/1 | 92.5 | 100 | 153 | DAIKIN | DC4SEA4210 | - | - | - | 208/1 | 19 | 30 | 95 | R32 | 14.5/12.0 (SEER2/EER2) | 225 | 1 | 3.5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 19 | 1 | ECM | DC4SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.1625 | 82.6 | 0.64
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM | DC4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 3 | 6.7458 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DC4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 5 | 11.243 | 208/1 | 29 | 30 | 153 | DAIKIN | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DC4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 6 | 13.4915 | 208/1 | 34 | 35 | 153 | DAIKIN | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DC4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 8 | 17.9887 | 208/1 | 43 | 45 | 153 | DAIKIN | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DC4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 10 | 22.4859 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DC4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 15 | 33.7289 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DC4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 57.204 | 46000 | 34960 | - | 19 | 42.7232 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DC4SEA4810 | - | - | - | 208/1 | 25.2 | 40 | 95 | R32 | 14.0/12.0 (SEER2/EER2) | 226 | 1 | 4 | COOLING ONLY | 14.3 SEER2 | 208/1 | 19 | 1 | ECM | DC4SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.6875 | 91 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | - | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 3 | 5.913 | 208/1 | 22 | 25 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 3 | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 5 | 9.8549 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 5 | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 6 | 11.8259 | 208/1 | 36 | 40 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 6 | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 8 | 15.7679 | 208/1 | 45 | 45 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 8 | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 10 | 19.7099 | 208/1 | 52 | 60 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 10 | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 15 | 29.5648 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 15 | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 20 | 39.4198 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 20 | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST60DU1300 | 1620 | 1 | ECM | 80 | 67 | 58.5551 | 56000 | 37520 | - | 25 | 49.2747 | 208/1 | 117 | 125 | 167 | DAIKIN | DC4SEA6010 | - | - | - | 208/1 | 32.4 | 50 | 95 | R32 | 14.0/11.5 (SEER2/EER2) | 239 | 1 | 5 | COOLING ONLY | 14.3 SEER2 | 208/1 | 25 | 1 | ECM | DC4SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC4SEA SINGLE PHASE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC4SEA SINGLE PHASE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.875 | 15 | 5.875 | 94 | 0.64
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | - | - | 208/1 | 5.8 | 15 | 112 | DAIKIN | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM | DC5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 3 | 15.45 | 208/1 | 19 | 20 | 112 | DAIKIN | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM | DC5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 5 | 25.75 | 208/1 | 27 | 30 | 112 | DAIKIN | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM | DC5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 6 | 30.9 | 208/1 | 32.8 | 35 | 112 | DAIKIN | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM | DC5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 8 | 41.2 | 208/1 | 41.9 | 45 | 112 | DAIKIN | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM | DC5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 10 | 51.5 | 208/1 | 49.1 | 50 | 112 | DAIKIN | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM | DC5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 620 | 0.75 | ECM | 80 | 67 | 61.5502 | 17400 | 12354 | - | 15 | 77.25 | 208/1 | 70.8 | 90 | 112 | DAIKIN | DC5SEA1810 | - | - | - | 208/1 | 11.1 | 15 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 116 | 1 | 1.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM | DC5SEA1810 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 3.375 | 54 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | - | - | 208/1 | 5.8 | 15 | 112 | DAIKIN | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM | DC5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 3 | 12.6039 | 208/1 | 19 | 20 | 112 | DAIKIN | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM | DC5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 5 | 21.0066 | 208/1 | 27 | 30 | 112 | DAIKIN | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM | DC5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 6 | 25.2079 | 208/1 | 32.8 | 35 | 112 | DAIKIN | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM | DC5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 8 | 33.6105 | 208/1 | 41.9 | 45 | 112 | DAIKIN | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM | DC5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 10 | 42.0132 | 208/1 | 49.1 | 50 | 112 | DAIKIN | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM | DC5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | AMST24BU1300 | 760 | 0.75 | ECM | 80 | 67 | 59.2982 | 23600 | 16992 | - | 15 | 63.0197 | 208/1 | 70.8 | 90 | 112 | DAIKIN | DC5SEA2410 | - | - | - | 208/1 | 13.8 | 20 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 149 | 1 | 2 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM | DC5SEA2410 | AMST24BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 4.0625 | 65 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | - | - | 208/1 | 5.6 | 15 | 129 | DAIKIN | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM | DC5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 3 | 10.0832 | 208/1 | 19 | 20 | 129 | DAIKIN | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM | DC5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 5 | 16.8053 | 208/1 | 27 | 30 | 129 | DAIKIN | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM | DC5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 6 | 20.1663 | 208/1 | 32.7 | 35 | 129 | DAIKIN | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM | DC5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 8 | 26.8884 | 208/1 | 42 | 45 | 129 | DAIKIN | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM | DC5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 10 | 33.6105 | 208/1 | 49 | 50 | 129 | DAIKIN | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM | DC5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | AMST30BU1300 | 950 | 0.75 | ECM | 80 | 67 | 59.6511 | 28600 | 20878 | - | 15 | 50.4158 | 208/1 | 49.1 | 80 | 129 | DAIKIN | DC5SEA3010 | - | - | - | 208/1 | 15.4 | 25 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 192 | 1 | 2.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM | DC5SEA3010 | AMST30BU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.75 | 15 | 5.4375 | 87 | 0.55
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM | DC5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 3 | 8.1872 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM | DC5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 5 | 13.6453 | 208/1 | 29 | 35 | 153 | DAIKIN | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM | DC5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 6 | 16.3744 | 208/1 | 34 | 40 | 153 | DAIKIN | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM | DC5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 8 | 21.8325 | 208/1 | 43 | 50 | 153 | DAIKIN | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM | DC5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 10 | 27.2906 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM | DC5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 15 | 40.9359 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM | DC5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | AMST36CU1300 | 1170 | 0.75 | ECM | 80 | 67 | 59.1896 | 34600 | 26296 | - | 19 | 51.8521 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DC5SEA3610 | - | - | - | 208/1 | 17.8 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 191 | 1 | 3 | COOLING ONLY | 15.2 SEER2 | 208/1 | 19 | 1 | ECM | DC5SEA3610 | AMST36CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 5.5 | 88 | 0.58
DAIKIN | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | - | - | 208/1 | 5.9 | 15 | 153 | DAIKIN | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM | DC5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 3 | 7.2023 | 208/1 | 19 | 20 | 153 | DAIKIN | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM | DC5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 5 | 12.0038 | 208/1 | 28 | 30 | 153 | DAIKIN | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM | DC5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 6 | 14.4045 | 208/1 | 33 | 35 | 153 | DAIKIN | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM | DC5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 8 | 19.206 | 208/1 | 42 | 45 | 153 | DAIKIN | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM | DC5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 10 | 24.0075 | 208/1 | 49 | 50 | 153 | DAIKIN | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM | DC5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 15 | 36.0113 | 208/1 | 70.9 | 80 | 153 | DAIKIN | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM | DC5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | AMST42CU1300 | 1330 | 0.75 | ECM | 80 | 67 | 59.1005 | 39500 | 30020 | - | 19 | 45.6143 | 208/1 | 92.5 | 100 | 153 | DAIKIN | DC5SEA4210 | - | - | - | 208/1 | 19.3 | 30 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 250 | 1 | 3.5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 19 | 1 | ECM | DC5SEA4210 | AMST42CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.8125 | 141 | 0.58
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | - | - | 208/1 | 7.1 | 15 | 153 | DAIKIN | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM | DC5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 3 | 6.7458 | 208/1 | 20.7 | 25 | 153 | DAIKIN | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM | DC5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 5 | 11.243 | 208/1 | 29 | 30 | 153 | DAIKIN | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM | DC5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 6 | 13.4915 | 208/1 | 34 | 35 | 153 | DAIKIN | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM | DC5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 8 | 17.9887 | 208/1 | 43 | 45 | 153 | DAIKIN | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM | DC5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 10 | 22.4859 | 208/1 | 50.5 | 60 | 153 | DAIKIN | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM | DC5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 15 | 33.7289 | 208/1 | 72.1 | 80 | 153 | DAIKIN | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM | DC5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | AMST48CU1300 | 1420 | 0.75 | ECM | 80 | 67 | 58.6385 | 45500 | 32760 | - | 19 | 42.7232 | 208/1 | 93.9 | 100 | 153 | DAIKIN | DC5SEA4810 | - | - | - | 208/1 | 25.5 | 40 | 95 | R32 | 15.2/12.5 (SEER2/EER2) | 249 | 1 | 4 | COOLING ONLY | 15.2 SEER2 | 208/1 | 19 | 1 | ECM | DC5SEA4810 | AMST48CU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 8.625 | 138 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | - | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 3 | 5.3217 | 208/1 | 22 | 25 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 3 | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 5 | 8.8694 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 5 | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 6 | 10.6433 | 208/1 | 36 | 40 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 6 | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 8 | 14.1911 | 208/1 | 45 | 45 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 8 | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 10 | 17.7389 | 208/1 | 52 | 60 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 10 | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 15 | 26.6083 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 15 | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 20 | 35.4778 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 20 | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | AMST60DU1300 | 1800 | 1 | ECM | 80 | 67 | 60.3549 | 57000 | 38190 | - | 25 | 44.3472 | 208/1 | 117 | 125 | 167 | DAIKIN | DC5SEA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12 (SEER2/EER2) | 287 | 1 | 5 | COOLING ONLY | 15.2 SEER2 | 208/1 | 25 | 1 | ECM | DC5SEA6010 | AMST60DU1300 |  |  | ENGINEERING MANUAL - DC5SE | ENGINEERING MANUAL - AMST |  | INSTALLATION MANUAL - DC5SE | INSTALLATION MANUAL - AMST | [9 empty] | R-32 | 50 | - | 79 | 0.375 | 0.875 | 15 | 10.4375 | 167 | 0.58
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | - | - | 208/1 | 4.9 | 15 | 115 | DAIKIN | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC6VSS1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS1810 |  |  | DC6VSS1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 3 | 15.7033 | 208/1 | 18.4 | 20 | 115 | DAIKIN | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 3 | Inverter | Variable Speed ECM | DC6VSS1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS1810 |  |  | DC6VSS1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 5 | 26.1721 | 208/1 | 26.5 | 30 | 115 | DAIKIN | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC6VSS1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS1810 |  |  | DC6VSS1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 6 | 31.4066 | 208/1 | 32 | 35 | 115 | DAIKIN | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC6VSS1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS1810 |  |  | DC6VSS1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 8 | 41.8754 | 208/1 | 41 | 45 | 115 | DAIKIN | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC6VSS1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS1810 |  |  | DC6VSS1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 610 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 17100 | 12825 | - | 10 | 52.3443 | 208/1 | 48.5 | 50 | 115 | DAIKIN | DC6VSS1810 | - | - | - | 208/1 | 12.8 | 15 | 95 | R32 | 18.5/12.0 (SEER2/EER2) | 119 | Inverter | 1.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC6VSS1810 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS1810 |  |  | DC6VSS1810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | - | - | 208/1 | 4.9 | 15 | 115 | DAIKIN | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC6VSS2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS2410 |  |  | DC6VSS2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 3 | 11.9738 | 208/1 | 18.4 | 20 | 115 | DAIKIN | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 3 | Inverter | Variable Speed ECM | DC6VSS2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS2410 |  |  | DC6VSS2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 5 | 19.9563 | 208/1 | 26.5 | 30 | 115 | DAIKIN | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC6VSS2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS2410 |  |  | DC6VSS2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 6 | 23.9475 | 208/1 | 32 | 35 | 115 | DAIKIN | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC6VSS2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS2410 |  |  | DC6VSS2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 8 | 31.93 | 208/1 | 41 | 45 | 115 | DAIKIN | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC6VSS2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS2410 |  |  | DC6VSS2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE24BP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 23200 | 17168 | - | 10 | 39.9125 | 208/1 | 48.5 | 50 | 115 | DAIKIN | DC6VSS2410 | - | - | - | 208/1 | 16.8 | 20 | 95 | R32 | 18.0/10.2 (SEER2/EER2) | 119 | Inverter | 2 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC6VSS2410 | DFVE24BP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS2410 |  |  | DC6VSS2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | - | - | 208/1 | 6.5 | 15 | 140 | DAIKIN | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC6VSS3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3010 |  |  | DC6VSS3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 5 | 15.8069 | 208/1 | 28.1 | 30 | 140 | DAIKIN | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC6VSS3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3010 |  |  | DC6VSS3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 6 | 18.9683 | 208/1 | 33.6 | 35 | 140 | DAIKIN | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC6VSS3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3010 |  |  | DC6VSS3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 8 | 25.2911 | 208/1 | 42.6 | 45 | 140 | DAIKIN | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC6VSS3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3010 |  |  | DC6VSS3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 10 | 31.6139 | 208/1 | 49.9 | 50 | 140 | DAIKIN | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC6VSS3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3010 |  |  | DC6VSS3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 15 | 47.4208 | 208/1 | 71.5 | 80 | 140 | DAIKIN | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC6VSS3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3010 |  |  | DC6VSS3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1010 | 0.75 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21868 | - | 19 | 60.0663 | 208/1 | 93.2 | 100 | 140 | DAIKIN | DC6VSS3010 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 17.5/10.0 (SEER2/EER2) | 129 | Inverter | 2.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM | DC6VSS3010 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3010 |  |  | DC6VSS3010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | - | - | 208/1 | 6.5 | 15 | 140 | DAIKIN | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC6VSS3610 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3610 |  |  | DC6VSS3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 5 | 12.6706 | 208/1 | 28.1 | 30 | 140 | DAIKIN | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC6VSS3610 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3610 |  |  | DC6VSS3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 6 | 15.2048 | 208/1 | 33.6 | 35 | 140 | DAIKIN | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC6VSS3610 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3610 |  |  | DC6VSS3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 8 | 20.273 | 208/1 | 42.6 | 45 | 140 | DAIKIN | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC6VSS3610 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3610 |  |  | DC6VSS3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 10 | 25.3413 | 208/1 | 49.9 | 50 | 140 | DAIKIN | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC6VSS3610 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3610 |  |  | DC6VSS3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 15 | 38.0119 | 208/1 | 71.5 | 80 | 140 | DAIKIN | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC6VSS3610 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3610 |  |  | DC6VSS3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 61 | 34200 | 26334 | - | 19 | 48.1484 | 208/1 | 93.2 | 100 | 140 | DAIKIN | DC6VSS3610 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 16.6/9.0 (SEER2/EER2) | 133 | Inverter | 3 | COOLING ONLY | 16.2 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM | DC6VSS3610 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS3610 |  |  | DC6VSS3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | - | - | 208/1 | 6.5 | 15 | 150 | DAIKIN | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC6VSS4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4210 |  |  | DC6VSS4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 5 | 12.0947 | 208/1 | 28.1 | 30 | 150 | DAIKIN | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC6VSS4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4210 |  |  | DC6VSS4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 6 | 14.5136 | 208/1 | 33.6 | 35 | 150 | DAIKIN | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC6VSS4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4210 |  |  | DC6VSS4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 8 | 19.3515 | 208/1 | 42.6 | 45 | 150 | DAIKIN | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC6VSS4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4210 |  |  | DC6VSS4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 10 | 24.1894 | 208/1 | 49.9 | 50 | 150 | DAIKIN | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC6VSS4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4210 |  |  | DC6VSS4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 15 | 36.2841 | 208/1 | 71.5 | 80 | 150 | DAIKIN | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC6VSS4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4210 |  |  | DC6VSS4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1320 | 0.75 | Variable Speed ECM | 80 | 67 | 58 | 41000 | 29930 | - | 20 | 48.3788 | 208/1 | 93.2 | 100 | 150 | DAIKIN | DC6VSS4210 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 3.5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DC6VSS4210 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4210 |  |  | DC6VSS4210 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | - | - | 208/1 | 6.5 | 15 | 150 | DAIKIN | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC6VSS4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4810 |  |  | DC6VSS4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 5 | 11.5688 | 208/1 | 28.1 | 30 | 150 | DAIKIN | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC6VSS4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4810 |  |  | DC6VSS4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 6 | 13.8826 | 208/1 | 33.6 | 35 | 150 | DAIKIN | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC6VSS4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4810 |  |  | DC6VSS4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 8 | 18.5101 | 208/1 | 42.6 | 45 | 150 | DAIKIN | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC6VSS4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4810 |  |  | DC6VSS4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 10 | 23.1377 | 208/1 | 49.9 | 50 | 150 | DAIKIN | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC6VSS4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4810 |  |  | DC6VSS4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 15 | 34.7065 | 208/1 | 71.5 | 80 | 150 | DAIKIN | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC6VSS4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4810 |  |  | DC6VSS4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1380 | 0.75 | Variable Speed ECM | 80 | 67 | 57 | 45500 | 33215 | - | 20 | 46.2754 | 208/1 | 93.2 | 100 | 150 | DAIKIN | DC6VSS4810 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 17.0/9.0 (SEER2/EER2) | 163 | Inverter | 4 | COOLING ONLY | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DC6VSS4810 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS4810 |  |  | DC6VSS4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC6VSS6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS6010 |  |  | DC6VSS6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | DAIKIN | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC6VSS6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS6010 |  |  | DC6VSS6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | DAIKIN | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC6VSS6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS6010 |  |  | DC6VSS6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | DAIKIN | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC6VSS6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS6010 |  |  | DC6VSS6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | DAIKIN | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC6VSS6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS6010 |  |  | DC6VSS6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC6VSS6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS6010 |  |  | DC6VSS6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DC6VSS6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS6010 |  |  | DC6VSS6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 58 | 53500 | 38520 | - | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | DAIKIN | DC6VSS6010 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 16.2/9.0 (SEER2/EER2) | 174 | Inverter | 5 | COOLING ONLY | 16.2 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM | DC6VSS6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC6VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC6VS | INSTALLATION MANUAL - DFVE |  | DC6VSS6010 |  |  | DC6VSS6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | - | - | 208/1 | 4.9 | 15 | 129 | DAIKIN | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM | DC7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 3 | 11.4036 | 208/1 | 18.4 | 20 | 129 | DAIKIN | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 3 | 2 | Variable Speed ECM | DC7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 5 | 19.006 | 208/1 | 26.5 | 30 | 129 | DAIKIN | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM | DC7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 6 | 22.8071 | 208/1 | 32 | 35 | 129 | DAIKIN | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM | DC7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 8 | 30.4095 | 208/1 | 41 | 45 | 129 | DAIKIN | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM | DC7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 10 | 38.0119 | 208/1 | 48.2 | 50 | 129 | DAIKIN | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM | DC7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT30BP1300 | 840 | 0.5 | Variable Speed ECM | 80 | 67 | 60.4233 | 24000 | 17760 | - | 15 | 57.0179 | 208/1 | 69.9 | 70 | 129 | DAIKIN | DC7TCA2410 | - | - | - | 208/1 | 15 | 20 | 95 | R32 | 18.0/13.0 (SEER2/EER2) | 214 | 2 | 2 | COOLING ONLY | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM | DC7TCA2410 | DMVT30BP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | - | - | 208/1 | 6.5 | 15 | 153 | DAIKIN | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM | DC7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 5 | 14.2545 | 208/1 | 28.2 | 35 | 153 | DAIKIN | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM | DC7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 6 | 17.1054 | 208/1 | 33.6 | 40 | 153 | DAIKIN | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM | DC7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 8 | 22.8071 | 208/1 | 42.6 | 50 | 153 | DAIKIN | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM | DC7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 10 | 28.5089 | 208/1 | 49.8 | 60 | 153 | DAIKIN | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM | DC7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 15 | 42.7634 | 208/1 | 71.5 | 80 | 153 | DAIKIN | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM | DC7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT42CP1300 | 1120 | 0.75 | Variable Speed ECM | 80 | 67 | 58.8773 | 35000 | 25550 | - | 19 | 54.167 | 208/1 | 93.2 | 100 | 153 | DAIKIN | DC7TCA3610 | - | - | - | 208/1 | 20.8 | 35 | 95 | R32 | 17.2/13.0 (SEER2/EER2) | 216 | 2 | 3 | COOLING ONLY | 17.2 SEER2 | 208/1 | 19 | 2 | Variable Speed ECM | DC7TCA3610 | DMVT42CP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM | DC7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 5 | 11.6533 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM | DC7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 6 | 13.9839 | 208/1 | 35.7 | 40 | 167 | DAIKIN | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM | DC7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 8 | 18.6453 | 208/1 | 44.7 | 45 | 167 | DAIKIN | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM | DC7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 10 | 23.3066 | 208/1 | 52 | 60 | 167 | DAIKIN | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM | DC7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 15 | 34.9599 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM | DC7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 20 | 46.6131 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 20 | 2 | Variable Speed ECM | DC7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1370 | 1 | Variable Speed ECM | 80 | 67 | 58.0819 | 47000 | 32430 | - | 25 | 58.2664 | 208/1 | 117 | 125 | 167 | DAIKIN | DC7TCA4810 | - | - | - | 208/1 | 31.6 | 50 | 95 | R32 | 17.2/12.5 (SEER2/EER2) | 276 | 2 | 4 | COOLING ONLY | 17.2 SEER2 | 208/1 | 25 | 2 | Variable Speed ECM | DC7TCA4810 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | - | 2 | Variable Speed ECM | DC7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 5 | 8.8694 | 208/1 | 30.3 | 35 | 167 | DAIKIN | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 5 | 2 | Variable Speed ECM | DC7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 6 | 10.6433 | 208/1 | 35.7 | 40 | 167 | DAIKIN | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 6 | 2 | Variable Speed ECM | DC7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 8 | 14.1911 | 208/1 | 44.7 | 45 | 167 | DAIKIN | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 8 | 2 | Variable Speed ECM | DC7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 10 | 17.7389 | 208/1 | 52 | 60 | 167 | DAIKIN | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 10 | 2 | Variable Speed ECM | DC7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 15 | 26.6083 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 15 | 2 | Variable Speed ECM | DC7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 20 | 35.4778 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 20 | 2 | Variable Speed ECM | DC7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DMVT60DP1300 | 1800 | 1 | Variable Speed ECM | 80 | 67 | 60.0103 | 58000 | 38860 | - | 25 | 44.3472 | 208/1 | 117 | 125 | 167 | DAIKIN | DC7TCA6010 | - | - | - | 208/1 | 36.4 | 60 | 95 | R32 | 16.2/12.0 (SEER2/EER2) | 283 | 2 | 5 | COOLING ONLY | 17.2 SEER2 | 208/1 | 25 | 2 | Variable Speed ECM | DC7TCA6010 | DMVT60DP1300 |  |  | ENGINEERING MANUAL - DC7TC | ENGINEERING MANUAL - DMVT |  | INSTALLATION MANUAL - DC7TC | INSTALLATION MANUAL - DMVT | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | - | - | 208/1 | 6.5 | 15 | 140 | DAIKIN | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC9VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA2410 |  |  | DC9VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 5 | 19.9563 | 208/1 | 28.1 | 30 | 140 | DAIKIN | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC9VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA2410 |  |  | DC9VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 6 | 23.9475 | 208/1 | 33.6 | 35 | 140 | DAIKIN | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC9VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA2410 |  |  | DC9VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 8 | 31.93 | 208/1 | 42.6 | 45 | 140 | DAIKIN | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC9VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA2410 |  |  | DC9VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 10 | 39.9125 | 208/1 | 49.9 | 50 | 140 | DAIKIN | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC9VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA2410 |  |  | DC9VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 15 | 59.8687 | 208/1 | 71.5 | 80 | 140 | DAIKIN | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC9VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA2410 |  |  | DC9VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE36CP1300 | 800 | 0.75 | Variable Speed ECM | 80 | 67 | 59.8611 | 23200 | 17400 | - | 19 | 75.8337 | 208/1 | 93.2 | 100 | 140 | DAIKIN | DC9VSA2410 | - | - | - | 208/1 | 22.4 | 25 | 95 | R32 | 19.0/11.0 (SEER2/EER2) | 129 | Inverter | 2 | COOLING ONLY | 19.0 SEER2 | 208/1 | 19 | Inverter | Variable Speed ECM | DC9VSA2410 | DFVE36CP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA2410 |  |  | DC9VSA2410 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | - | - | 208/1 | 6.5 | 15 | 150 | DAIKIN | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC9VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA3610 |  |  | DC9VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 5 | 12.6706 | 208/1 | 28.1 | 30 | 150 | DAIKIN | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC9VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA3610 |  |  | DC9VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 6 | 15.2048 | 208/1 | 33.6 | 35 | 150 | DAIKIN | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC9VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA3610 |  |  | DC9VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 8 | 20.273 | 208/1 | 42.6 | 45 | 150 | DAIKIN | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC9VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA3610 |  |  | DC9VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 10 | 25.3413 | 208/1 | 49.9 | 50 | 150 | DAIKIN | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC9VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA3610 |  |  | DC9VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 15 | 38.0119 | 208/1 | 71.5 | 80 | 150 | DAIKIN | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC9VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA3610 |  |  | DC9VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE48DP1300 | 1260 | 0.75 | Variable Speed ECM | 80 | 67 | 59.6811 | 35000 | 27650 | - | 20 | 50.6825 | 208/1 | 93.2 | 100 | 150 | DAIKIN | DC9VSA3610 | - | - | - | 208/1 | 31.8 | 35 | 95 | R32 | 19.0/10.5 (SEER2/EER2) | 163 | Inverter | 3 | COOLING ONLY | 19.0 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DC9VSA3610 | DFVE48DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA3610 |  |  | DC9VSA3610 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC9VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA4810 |  |  | DC9VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 5 | 11.5688 | 208/1 | 30.2 | 35 | 167 | DAIKIN | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC9VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA4810 |  |  | DC9VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 6 | 13.8826 | 208/1 | 35.8 | 40 | 167 | DAIKIN | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC9VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA4810 |  |  | DC9VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 8 | 18.5101 | 208/1 | 44.8 | 45 | 167 | DAIKIN | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC9VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA4810 |  |  | DC9VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 10 | 23.1377 | 208/1 | 52 | 60 | 167 | DAIKIN | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC9VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA4810 |  |  | DC9VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 15 | 34.7065 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC9VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA4810 |  |  | DC9VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 20 | 46.2754 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DC9VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA4810 |  |  | DC9VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1380 | 1 | Variable Speed ECM | 80 | 67 | 57.5362 | 46500 | 33480 | - | 25 | 57.8442 | 208/1 | 117 | 125 | 167 | DAIKIN | DC9VSA4810 | - | - | - | 208/1 | 37.5 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 174 | Inverter | 4 | COOLING ONLY | 19.0 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM | DC9VSA4810 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA4810 |  |  | DC9VSA4810 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | - | - | 208/1 | 8.6 | 15 | 167 | DAIKIN | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | - | Inverter | Variable Speed ECM | DC9VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA6010 |  |  | DC9VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 5 | 9.7348 | 208/1 | 30.2 | 35 | 167 | DAIKIN | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 5 | Inverter | Variable Speed ECM | DC9VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA6010 |  |  | DC9VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 6 | 11.6817 | 208/1 | 35.8 | 40 | 167 | DAIKIN | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 6 | Inverter | Variable Speed ECM | DC9VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA6010 |  |  | DC9VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 8 | 15.5756 | 208/1 | 44.8 | 45 | 167 | DAIKIN | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 8 | Inverter | Variable Speed ECM | DC9VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA6010 |  |  | DC9VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 10 | 19.4695 | 208/1 | 52 | 60 | 167 | DAIKIN | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 10 | Inverter | Variable Speed ECM | DC9VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA6010 |  |  | DC9VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 15 | 29.2043 | 208/1 | 73.6 | 80 | 167 | DAIKIN | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 15 | Inverter | Variable Speed ECM | DC9VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA6010 |  |  | DC9VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 20 | 38.939 | 208/1 | 95.3 | 100 | 167 | DAIKIN | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 20 | Inverter | Variable Speed ECM | DC9VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA6010 |  |  | DC9VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DFVE60DP1300 | 1640 | 1 | Variable Speed ECM | 80 | 67 | 57.4729 | 57000 | 39900 | - | 25 | 48.6738 | 208/1 | 117 | 125 | 167 | DAIKIN | DC9VSA6010 | - | - | - | 208/1 | 34.4 | 40 | 95 | R32 | 17.0/10.0 (SEER2/EER2) | 236 | Inverter | 5 | COOLING ONLY | 19.0 SEER2 | 208/1 | 25 | Inverter | Variable Speed ECM | DC9VSA6010 | DFVE60DP1300 |  |  | ENGINEERING MANUAL - DC9VS | ENGINEERING MANUAL - DFVE |  | INSTALLATION MANUAL - DC9VS | INSTALLATION MANUAL - DFVE |  | DC9VSA6010 |  |  | DC9VSA6010 |  |  |  |  | - | - | - | - | - | - | - | - | - | -
DAIKIN | DAQ09033 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | - | - | 208/3 | 15.5 | 20 | 430 | DAIKIN | DC6TE09030 | - | - | - | 208/3 | 38.7 | 50 | 95 | R32 | 16.4 IEER | 381 | 2 | 7.5 | COOLING ONLY | 16.4 IEER | 208/3 | - | 2 | ECM | DC6TE09030 | DAQ09033 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09033 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 15 | 12.6539 | 208/3 | 54.8 | 60 | 430 | DAIKIN | DC6TE09030 | - | - | - | 208/3 | 38.7 | 50 | 95 | R32 | 16.4 IEER | 381 | 2 | 7.5 | COOLING ONLY | 16.4 IEER | 208/3 | 15 | 2 | ECM | DC6TE09030 | DAQ09033 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09033 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 20 | 16.8719 | 208/3 | 67.3 | 70 | 430 | DAIKIN | DC6TE09030 | - | - | - | 208/3 | 38.7 | 50 | 95 | R32 | 16.4 IEER | 381 | 2 | 7.5 | COOLING ONLY | 16.4 IEER | 208/3 | 20 | 2 | ECM | DC6TE09030 | DAQ09033 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09033 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 30 | 25.3078 | 208/3 | 92.3 | 100 | 430 | DAIKIN | DC6TE09030 | - | - | - | 208/3 | 38.7 | 50 | 95 | R32 | 16.4 IEER | 381 | 2 | 7.5 | COOLING ONLY | 16.4 IEER | 208/3 | 30 | 2 | ECM | DC6TE09030 | DAQ09033 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | - | - | 208/3 | 15.5 | 20 | 430 | DAIKIN | DC6TE12030 | - | - | - | 208/3 | 45.9 | 60 | 95 | R32 | 16.4 IEER | 381 | 2 | 10 | COOLING ONLY | 16.4 IEER | 208/3 | - | 2 | ECM | DC6TE12030 | DAQ12033 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 15 | 12.6539 | 208/3 | 54.8 | 60 | 430 | DAIKIN | DC6TE12030 | - | - | - | 208/3 | 45.9 | 60 | 95 | R32 | 16.4 IEER | 381 | 2 | 10 | COOLING ONLY | 16.4 IEER | 208/3 | 15 | 2 | ECM | DC6TE12030 | DAQ12033 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 20 | 16.8719 | 208/3 | 67.3 | 70 | 430 | DAIKIN | DC6TE12030 | - | - | - | 208/3 | 45.9 | 60 | 95 | R32 | 16.4 IEER | 381 | 2 | 10 | COOLING ONLY | 16.4 IEER | 208/3 | 20 | 2 | ECM | DC6TE12030 | DAQ12033 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12033 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 30 | 25.3078 | 208/3 | 92.3 | 100 | 430 | DAIKIN | DC6TE12030 | - | - | - | 208/3 | 45.9 | 60 | 95 | R32 | 16.4 IEER | 381 | 2 | 10 | COOLING ONLY | 16.4 IEER | 208/3 | 30 | 2 | ECM | DC6TE12030 | DAQ12033 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ09034 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | - | - | 460/3 | 5.2 | 15 | 430 | DAIKIN | DC6TE09040 | - | - | - | 460/3 | 17.9 | 20 | 95 | R32 | 16.4 IEER | 381 | 2 | 7.5 | COOLING ONLY | 16.4 IEER | 460/3 | - | 2 | ECM | DC6TE09040 | DAQ09034 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09034 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 15 | 12.6539 | 460/3 | 27.4 | 30 | 430 | DAIKIN | DC6TE09040 | - | - | - | 460/3 | 17.9 | 20 | 95 | R32 | 16.4 IEER | 381 | 2 | 7.5 | COOLING ONLY | 16.4 IEER | 460/3 | 15 | 2 | ECM | DC6TE09040 | DAQ09034 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09034 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 20 | 16.8719 | 460/3 | 34.6 | 35 | 430 | DAIKIN | DC6TE09040 | - | - | - | 460/3 | 17.9 | 20 | 95 | R32 | 16.4 IEER | 381 | 2 | 7.5 | COOLING ONLY | 16.4 IEER | 460/3 | 20 | 2 | ECM | DC6TE09040 | DAQ09034 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ09034 | 3785 | 1 | ECM | 80 | 67 | 57.6 | 94999 | 66499 | - | 30 | 25.3078 | 460/3 | 49.1 | 50 | 430 | DAIKIN | DC6TE09040 | - | - | - | 460/3 | 17.9 | 20 | 95 | R32 | 16.4 IEER | 381 | 2 | 7.5 | COOLING ONLY | 16.4 IEER | 460/3 | 30 | 2 | ECM | DC6TE09040 | DAQ09034 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.54
DAIKIN | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | - | - | 460/3 | 5.2 | 15 | 430 | DAIKIN | DC6TE12040 | - | - | - | 460/3 | 20.8 | 25 | 95 | R32 | 16.4 IEER | 381 | 2 | 10 | COOLING ONLY | 16.4 IEER | 460/3 | - | 2 | ECM | DC6TE12040 | DAQ12034 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 15 | 12.6539 | 460/3 | 27.4 | 30 | 430 | DAIKIN | DC6TE12040 | - | - | - | 460/3 | 20.8 | 25 | 95 | R32 | 16.4 IEER | 381 | 2 | 10 | COOLING ONLY | 16.4 IEER | 460/3 | 15 | 2 | ECM | DC6TE12040 | DAQ12034 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 20 | 16.8719 | 460/3 | 34.6 | 35 | 430 | DAIKIN | DC6TE12040 | - | - | - | 460/3 | 20.8 | 25 | 95 | R32 | 16.4 IEER | 381 | 2 | 10 | COOLING ONLY | 16.4 IEER | 460/3 | 20 | 2 | ECM | DC6TE12040 | DAQ12034 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | DAQ12034 | 3785 | 1 | ECM | 80 | 67 | 58.6 | 117999 | 82599 | - | 30 | 25.3078 | 460/3 | 49.1 | 50 | 430 | DAIKIN | DC6TE12040 | - | - | - | 460/3 | 20.8 | 25 | 95 | R32 | 16.4 IEER | 381 | 2 | 10 | COOLING ONLY | 16.4 IEER | 460/3 | 30 | 2 | ECM | DC6TE12040 | DAQ12034 |  |  | ENGINEERING MANUAL - DC6TE | ENGINEERING MANUAL - DAQ |  | INSTALLATION MANUAL - DC6TE | INSTALLATION MANUAL - DAQ | [9 empty] | R-32 | 25 | - | 150 | 0.625 | 1.125 | 15 | 6.875 | 110 | 1.62
DAIKIN | AWVE12SU1300 | 450 | 0.25 | Variable Speed ECM | 80 | 67 | 61 | 11500 | 8740 | 12000 | - | - | 208/1 | 2.6 | 15 | 87 | DAIKIN | DH6VSA121M | 47 | 12000 | 8.5 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 16.5/11.0 (SEER2/EER2) | 123 | Inverter | 1 | HEAT PUMP | 16.5 SEER2 (Apt Style) | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA121M | AWVE12SU1300 |  |  | ENGINEERING MANUAL - DH6VSA (Apt Style) | ENGINEERING MANUAL - AWVE |  | INSTALLATION MANUAL - DH6VSA (Apt Style) | INSTALLATION MANUAL - AWVE | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | AWVE18SU1300 | 610 | 0.33 | Variable Speed ECM | 80 | 67 | 61 | 17000 | 12920 | 17200 | - | - | 208/1 | 3.5 | 15 | 100 | DAIKIN | DH6VSA181M | 47 | 17200 | 8.5 HSPF2 | 208/1 | 12.8 | 15 | 95 | R32 | 16.5/11.0 (SEER2/EER2) | 123 | Inverter | 1.5 | HEAT PUMP | 16.5 SEER2 (Apt Style) | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA181M | AWVE18SU1300 |  |  | ENGINEERING MANUAL - DH6VSA (Apt Style) | ENGINEERING MANUAL - AWVE |  | INSTALLATION MANUAL - DH6VSA (Apt Style) | INSTALLATION MANUAL - AWVE | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | AWVE24SU1300 | 830 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 21600 | 16632 | 21600 | - | - | 208/1 | 4.9 | 15 | 114 | DAIKIN | DH6VSA241M | 47 | 21600 | 8.5 HSPF2 | 208/1 | 16.8 | 20 | 95 | R32 | 16.5/9.8 (SEER2/EER2) | 124 | Inverter | 2 | HEAT PUMP | 16.5 SEER2 (Apt Style) | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA241M | AWVE24SU1300 |  |  | ENGINEERING MANUAL - DH6VSA (Apt Style) | ENGINEERING MANUAL - AWVE |  | INSTALLATION MANUAL - DH6VSA (Apt Style) | INSTALLATION MANUAL - AWVE | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | AWVE30LU1300 | 1000 | 0.5 | Variable Speed ECM | 80 | 67 | 60 | 28400 | 21584 | 25600 | - | - | 208/1 | 4.9 | 15 | 127 | DAIKIN | DH6VSA301M | 47 | 25600 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.5/9.8 (SEER2/EER2) | 133 | Inverter | 2.5 | HEAT PUMP | 16.5 SEER2 (Apt Style) | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA301M | AWVE30LU1300 |  |  | ENGINEERING MANUAL - DH6VSA (Apt Style) | ENGINEERING MANUAL - AWVE |  | INSTALLATION MANUAL - DH6VSA (Apt Style) | INSTALLATION MANUAL - AWVE | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | AWVE36LU1300 | 1150 | 0.5 | Variable Speed ECM | 80 | 67 | 59 | 34000 | 25840 | 34400 | - | - | 208/1 | 4.9 | 15 | 141 | DAIKIN | DH6VSA361M | 47 | 34400 | 8.5 HSPF2 | 208/1 | 22.4 | 25 | 95 | R32 | 16.5/9.8 (SEER2/EER2) | 127 | Inverter | 3 | HEAT PUMP | 16.5 SEER2 (Apt Style) | 208/1 | - | Inverter | Variable Speed ECM | DH6VSA361M | AWVE36LU1300 |  |  | ENGINEERING MANUAL - DH6VSA (Apt Style) | ENGINEERING MANUAL - AWVE |  | INSTALLATION MANUAL - DH6VSA (Apt Style) | INSTALLATION MANUAL - AWVE | [9 empty] | - | - | - | - | - | - | - | - | - | -
DAIKIN | ACST18MU1300 | 615 | 0.25 | ECM | 80 | 67 | - | 17000 | - | 17000 | - | - | 208/1 | 2.5 | 15 | 85 | DAIKIN | DH4SEA1810 | 47 | 17000 | 7.5 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 14.3/12.0 (SEER2/EER2) | 176 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | - | 1 | ECM | DH4SEA1810 | ACST18MU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | ACST24LU1300 | 740 | 0.25 | ECM | 80 | 67 | - | 21800 | - | 21800 | - | - | 208/1 | 2.5 | 15 | 97 | DAIKIN | DH4SEA2410 | 47 | 21800 | 7.5 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 177 | 1 | 2 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | - | 1 | ECM | DH4SEA2410 | ACST24LU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | ACST30LU1300 | 810 | 0.25 | ECM | 80 | 67 | - | 27000 | - | 27000 | - | - | 208/1 | 2.5 | 15 | 97 | DAIKIN | DH4SEA3010 | 47 | 27000 | 7.5 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.3/11.5 (SEER2/EER2) | 194 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | - | 1 | ECM | DH4SEA3010 | ACST30LU1300 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.88 | 78 | 0.55
DAIKIN | ACST18MU1305 | 615 | 0.25 | ECM | 80 | 67 | - | 17000 | - | 17000 | 5 | 25.9593 | 208/1 | 28.5 | 30 | 85 | DAIKIN | DH4SEA1810 | 47 | 17000 | 7.5 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 14.3/12.0 (SEER2/EER2) | 176 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 5 | 1 | ECM | DH4SEA1810 | ACST18MU1305 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | ACST18MU1308 | 615 | 0.25 | ECM | 80 | 67 | - | 17000 | - | 17000 | 8 | 41.535 | 208/1 | 44.2 | 45 | 85 | DAIKIN | DH4SEA1810 | 47 | 17000 | 7.5 HSPF2 | 208/1 | 11.4 | 15 | 95 | R32 | 14.3/12.0 (SEER2/EER2) | 176 | 1 | 1.5 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 8 | 1 | ECM | DH4SEA1810 | ACST18MU1308 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.4375 | 71 | 0.55
DAIKIN | ACST24LU1305 | 740 | 0.25 | ECM | 80 | 67 | - | 21800 | - | 21800 | 5 | 21.5743 | 208/1 | 28.5 | 30 | 97 | DAIKIN | DH4SEA2410 | 47 | 21800 | 7.5 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 177 | 1 | 2 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 5 | 1 | ECM | DH4SEA2410 | ACST24LU1305 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | ACST24LU1306 | 740 | 0.25 | ECM | 80 | 67 | - | 21800 | - | 21800 | 6 | 25.8892 | 208/1 | 33.8 | 35 | 97 | DAIKIN | DH4SEA2410 | 47 | 21800 | 7.5 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 177 | 1 | 2 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 6 | 1 | ECM | DH4SEA2410 | ACST24LU1306 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | ACST24LU1308 | 740 | 0.25 | ECM | 80 | 67 | - | 21800 | - | 21800 | 8 | 34.5189 | 208/1 | 44.2 | 45 | 97 | DAIKIN | DH4SEA2410 | 47 | 21800 | 7.5 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 177 | 1 | 2 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 8 | 1 | ECM | DH4SEA2410 | ACST24LU1308 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | ACST24LU1310 | 740 | 0.25 | ECM | 80 | 67 | - | 21800 | - | 21800 | 10 | 43.1486 | 208/1 | 54.6 | 60 | 97 | DAIKIN | DH4SEA2410 | 47 | 21800 | 7.5 HSPF2 | 208/1 | 13.8 | 20 | 95 | R32 | 14.3/11.7 (SEER2/EER2) | 177 | 1 | 2 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 10 | 1 | ECM | DH4SEA2410 | ACST24LU1310 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.375 | 70 | 0.55
DAIKIN | ACST30LU1305 | 810 | 0.25 | ECM | 80 | 67 | - | 27000 | - | 27000 | 5 | 19.7099 | 208/1 | 28.5 | 30 | 97 | DAIKIN | DH4SEA3010 | 47 | 27000 | 7.5 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.3/11.5 (SEER2/EER2) | 194 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 5 | 1 | ECM | DH4SEA3010 | ACST30LU1305 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | ACST30LU1306 | 810 | 0.25 | ECM | 80 | 67 | - | 27000 | - | 27000 | 6 | 23.6519 | 208/1 | 33.8 | 35 | 97 | DAIKIN | DH4SEA3010 | 47 | 27000 | 7.5 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.3/11.5 (SEER2/EER2) | 194 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 6 | 1 | ECM | DH4SEA3010 | ACST30LU1306 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | ACST30LU1308 | 810 | 0.25 | ECM | 80 | 67 | - | 27000 | - | 27000 | 8 | 31.5358 | 208/1 | 44.2 | 45 | 97 | DAIKIN | DH4SEA3010 | 47 | 27000 | 7.5 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.3/11.5 (SEER2/EER2) | 194 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 8 | 1 | ECM | DH4SEA3010 | ACST30LU1308 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55
DAIKIN | ACST30LU1310 | 810 | 0.25 | ECM | 80 | 67 | - | 27000 | - | 27000 | 10 | 39.4198 | 208/1 | 54.6 | 60 | 97 | DAIKIN | DH4SEA3010 | 47 | 27000 | 7.5 HSPF2 | 208/1 | 17 | 25 | 95 | R32 | 14.3/11.5 (SEER2/EER2) | 194 | 1 | 2.5 | HEAT PUMP | 14.3 SEER2 (Ceiling Mounted) | 208/1 | 10 | 1 | ECM | DH4SEA3010 | ACST30LU1310 |  |  | ENGINEERING MANUAL - DH4SEA SINGLE PHASE | ENGINEERING MANUAL - ACST |  | INSTALLATION MANUAL - DH4SEA SINGLE PHASE | INSTALLATION MANUAL - ACST | [9 empty] | R-32 | 79 | - | 200 | 0.375 | 0.75 | 15 | 4.875 | 78 | 0.55

## SCHEDULE NOTES
Provide with 7-day programmable thermostat
Provide with 7-day programmable BACnet thermostat
Provide with field installed disconnect. Disconnect shall be provided and installed by electrical contractor
Electric heat, if scheduled, shall be single point power. kW listed is at 240V
Heat pump heating capacity based on 70 F entering air temperature