## SCHEDULE
SCHEDULE RANGE | [21 empty] | FILTERS |  |  |  | DOCUMENTATION
AIR-COOLED CHILLERS | [21 empty] | SIZE | ELECTRICAL | COMPRESSOR TYPE | REFRIGERANT | SUBMITTAL | ENGINEERING MANUAL | INSTALLATION MANUAL
MAKE | MODEL NUMBER | STOCK UNIT | NOM TONS | COMPRESSOR | REFRIGERANT | Cooling Performance |  |  |  |  | Evaporator |  |  |  |  | Electrical Data |  |  | SOUND POWER dB(A) | Operating Weight (lbs) | DIMENSIONS L x W x H (IN)
[6 empty] | CAPACITY (TONS) | POWER INPUT (KW) | EER | IPLV | AMBIENT (°F) | EWT (°F) | LWT (°F) | GPM | EVAP WPD (FT) | MIN / MAX GPM | VOLT/PH | Unit MCA | Unit MOCP
QUANTECH | QTC3040THJ17XCB | QTC3040THJ17VSD | 40 | 4 SCROLL / 2 CKT | R-454B | 38.98 | 39.46 | 11.85 | 18.62 | 95 | 54 | 44 | 93.04 | 7.43 | 41 / 224 | 200-208/3 | 182 | 200 | 93 | 3825 | 101.4 x 88.3 x 94.2 | 40 | 200-208/3 | SCROLL | R-454B | QTC3040THJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3040THJ46XCB | QTC3040THJ46VSD | 40 | 4 SCROLL / 2 CKT | R-454B | 38.98 | 39.46 | 11.85 | 18.62 | 95 | 54 | 44 | 93.04 | 7.43 | 41 / 224 | 460/3 | 83 | 90 | 93 | 3825 | 101.4 x 88.3 x 94.2 | 40 | 460/3 | SCROLL | R-454B | QTC3040THJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3050THJ17XCB | QTC3050THJ17VSD | 50 | 4 SCROLL / 2 CKT | R-454B | 48.25 | 51.88 | 11.16 | 17.59 | 95 | 54 | 44 | 115.2 | 7.26 | 48 / 224 | 200-208/3 | 235 | 250 | 94 | 3704 | 101.4 x 88.3 x 94.2 | 50 | 200-208/3 | SCROLL | R-454B | QTC3050THJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3050THJ46XCB | QTC3050THJ46VSD | 50 | 4 SCROLL / 2 CKT | R-454B | 48.25 | 51.88 | 11.16 | 17.59 | 95 | 54 | 44 | 115.2 | 7.26 | 48 / 224 | 460/3 | 106 | 125 | 94 | 3704 | 101.4 x 88.3 x 94.2 | 50 | 460/3 | SCROLL | R-454B | QTC3050THJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3055THJ17XFB | QTC3055THJ17VSD | 55 | 4 SCROLL / 2 CKT | R-454B | 56.11 | 62.08 | 10.85 | 17.52 | 95 | 54 | 44 | 133.9 | 7.22 | 60 / 325 | 200-208/3 | 285 | 300 | 93 | 4026 | 101.4 x 88.3 x 94.2 | 55 | 200-208/3 | SCROLL | R-454B | QTC3055THJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3055THJ46XFB | QTC3055THJ46VSD | 55 | 4 SCROLL / 2 CKT | R-454B | 56.11 | 62.08 | 10.85 | 17.52 | 95 | 54 | 44 | 133.9 | 7.22 | 60 / 325 | 460/3 | 132 | 150 | 93 | 4026 | 101.4 x 88.3 x 94.2 | 55 | 460/3 | SCROLL | R-454B | QTC3055THJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3060THJ17XFB | QTC3060THJ17VSD | 60 | 5 SCROLL / 2 CKT | R-454B | 61.35 | 69.32 | 10.62 | 17.66 | 95 | 54 | 44 | 146.4 | 8.42 | 60 / 325 | 200-208/3 | 315 | 350 | 93 | 4220 | 101.4 x 88.3 x 94.2 | 60 | 200-208/3 | SCROLL | R-454B | QTC3060THJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3060THJ46XFB | QTC3060THJ46VSD | 60 | 5 SCROLL / 2 CKT | R-454B | 61.35 | 69.32 | 10.62 | 17.66 | 95 | 54 | 44 | 146.4 | 8.42 | 60 / 325 | 460/3 | 152 | 175 | 93 | 4220 | 101.4 x 88.3 x 94.2 | 60 | 460/3 | SCROLL | R-454B | QTC3060THJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3070TSJ46XFB | QTC3070TSJ46VSD | 70 | 6 SCROLL / 2 CKT | R-454B | 69.98 | 79.18 | 10.61 | 17.99 | 95 | 54 | 44 | 167 | 10.8 | 60 / 325 | 460/3 | 170 | 175 | 94 | 4464 | 116.1 x 88.3 x 94.2 | 70 | 460/3 | SCROLL | R-454B | QTC3070TSJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3075TSJ46XFB | QTC3075TSJ46VSD | 75 | 6 SCROLL / 2 CKT | R-454B | 76.64 | 88.91 | 10.34 | 17.26 | 95 | 54 | 44 | 183 | 8.92 | 100 / 350 | 460/3 | 179 | 200 | 94 | 4517 | 116.1 x 88.3 x 94.2 | 75 | 460/3 | SCROLL | R-454B | QTC3075TSJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3085TSJ17XFB | QTC3085TSJ17VSD | 85 | 6 SCROLL / 2 CKT | R-454B | 80.58 | 96.02 | 10.07 | 17.56 | 95 | 54 | 44 | 192.3 | 6.48 | 100 / 400 | 200-208/3 | 401 | 450 | 94 | 4610 | 116.1 x 88.3 x 94.2 | 85 | 200-208/3 | SCROLL | R-454B | QTC3085TSJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3085TSJ46XFB | QTC3085TSJ46VSD | 85 | 6 SCROLL / 2 CKT | R-454B | 80.58 | 96.02 | 10.07 | 17.56 | 95 | 54 | 44 | 192.3 | 6.48 | 100 / 400 | 460/3 | 186 | 200 | 94 | 4610 | 116.1 x 88.3 x 94.2 | 85 | 460/3 | SCROLL | R-454B | QTC3085TSJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3095TSJ17XFB | QTC3095TSJ17PC | 95 | 5 SCROLL / 2 CKT | R-454B | 95.04 | 114.8 | 9.935 | 17.03 | 95 | 54 | 44 | 226.9 | 8.89 | 100 / 400 | 200-208/3 | 460 | 500 | 95 | 5247 | 142.7 x 88.3 x 94.2 | 95 | 200-208/3 | SCROLL | R-454B | QTC3095TSJ17PC | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3095TSJ46XFB | QTC3095TSJ46VSD | 95 | 5 SCROLL / 2 CKT | R-454B | 95.04 | 114.8 | 9.935 | 17.03 | 95 | 54 | 44 | 226.9 | 8.89 | 100 / 400 | 460/3 | 222 | 250 | 95 | 5247 | 142.7 x 88.3 x 94.2 | 95 | 460/3 | SCROLL | R-454B | QTC3095TSJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3110TSJ17XFB | QTC3110TSJ17VSD | 110 | 4 SCROLL / 2 CKT | R-454B | 118.2 | 141.7 | 10.01 | 17.09 | 95 | 54 | 44 | 282.2 | 8.24 | 150 / 625 | 200-208/3 | 507 | 600 | 96 | 5695 | 142.7 x 88.3 x 94.2 | 110 | 200-208/3 | SCROLL | R-454B | QTC3110TSJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3110TSJ46XFB | QTC3110TSJ46VSD | 110 | 4 SCROLL / 2 CKT | R-454B | 118.2 | 141.7 | 10.01 | 17.09 | 95 | 54 | 44 | 282.2 | 8.24 | 150 / 625 | 460/3 | 250 | 300 | 96 | 5695 | 142.7 x 88.3 x 94.2 | 110 | 460/3 | SCROLL | R-454B | QTC3110TSJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3129THJ17XFB | QTC3129THJ17VSD | 129 | 5 SCROLL / 2 CKT | R-454B | 124.4 | 144.2 | 10.35 | 18.15 | 95 | 54 | 44 | 297 | 12.3 | 138 / 525 | 200-208/3 | 565 | 600 | 97 | 7194 | 187.7 x 88.3 x 94.2 | 129 | 200-208/3 | SCROLL | R-454B | QTC3129THJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3129THJ46XFB | QTC3129THJ46VSD | 129 | 5 SCROLL / 2 CKT | R-454B | 124.4 | 144.2 | 10.35 | 18.15 | 95 | 54 | 44 | 297 | 12.3 | 138 / 525 | 460/3 | 273 | 300 | 97 | 7194 | 187.7 x 88.3 x 94.2 | 129 | 460/3 | SCROLL | R-454B | QTC3129THJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3140TSJ17XFB | QTC3140TSJ17VSD | 140 | 5 SCROLL / 2 CKT | R-454B | 143.2 | 173 | 9.932 | 17.75 | 95 | 54 | 44 | 341.7 | 11.9 | 150 / 625 | 200-208/3 | 628 | 700 | 97 | 7154 | 187.7 x 88.3 x 94.2 | 140 | 200-208/3 | SCROLL | R-454B | QTC3140TSJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3140TSJ46XFB | QTC3140TSJ46VSD | 140 | 5 SCROLL / 2 CKT | R-454B | 143.2 | 173 | 9.932 | 17.75 | 95 | 54 | 44 | 341.7 | 11.9 | 150 / 625 | 460/3 | 310 | 350 | 97 | 7154 | 187.7 x 88.3 x 94.2 | 140 | 460/3 | SCROLL | R-454B | QTC3140TSJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC4150S | QTC4150SXXX46R | 150 | 2 VSD SCREW / 2 CKT | R-513A | 157.3 | 194.5 | 9.703 | 17.46 | 95 | 54 | 44 | 376.4 | 7.33 | 250 / 980 | 460/3 | 291.8 | 400 | 101 | 13078 | 203.3 x 88.3 x 94.6 | 150 | 460/3 | VSD SCREW | R-513A | QTC4150SXXX46R | Quantech QTC4 Engineering Guide QTC4-EG2 | Quantech QTC4 IOM QTC4-NM2
QUANTECH | QTC3160TSJ17XFB | QTC3160TSJ17VSD | 160 | 6 SCROLL / 2 CKT | R-454B | 167.6 | 202.3 | 9.942 | 17.49 | 95 | 54 | 44 | 400 | 21.4 | 150 / 625 | 200-208/3 | 749 | 800 | 98 | 8494 | 232.7 x 88.3 x 94.2 | 160 | 200-208/3 | SCROLL | R-454B | QTC3160TSJ17VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC3160TSJ46XFB | QTC3160TSJ46VSD | 160 | 6 SCROLL / 2 CKT | R-454B | 167.6 | 202.3 | 9.942 | 17.49 | 95 | 54 | 44 | 400 | 21.4 | 150 / 625 | 460/3 | 370 | 400 | 98 | 8494 | 232.7 x 88.3 x 94.2 | 160 | 460/3 | SCROLL | R-454B | QTC3160TSJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC4185S | QTC4185SXXX46R | 185 | 2 VSD SCREW / 2 CKT | R-513A | 186.8 | 227.8 | 9.84 | 18.32 | 95 | 54 | 44 | 447.1 | 15.2 | 200 / 790 | 460/3 | 346.4 | 500 | 102 | 13713 | 247 x 88.3 x 94.6 | 185 | 460/3 | VSD SCREW | R-513A | QTC4185SXXX46R | Quantech QTC4 Engineering Guide QTC4-EG2 | Quantech QTC4 IOM QTC4-NM2
QUANTECH | QTC3205THJ46XFB | QTC3205THJ46VSD | 205 | 6 SCROLL / 2 CKT | R-454B | 192.8 | 222.9 | 10.38 | 18.46 | 95 | 54 | 44 | 460.3 | 18.4 | 230 / 625 | 460/3 | 366 | 400 | 98 | 10119 | 274.8 x 88.3 x 94.2 | 205 | 460/3 | SCROLL | R-454B | QTC3205THJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC4210S | QTC4210SXXX46R | 210 | 2 VSD SCREW / 2 CKT | R-513A | 217.2 | 261.8 | 9.955 | 18.65 | 95 | 54 | 44 | 519.8 | 19.9 | 200 / 790 | 460/3 | 392.1 | 500 | 102 | 14599 | 291.2 x 88.3 x 94.6 | 210 | 460/3 | VSD SCREW | R-513A | QTC4210SXXX46R | Quantech QTC4 Engineering Guide QTC4-EG2 | Quantech QTC4 IOM QTC4-NM2
QUANTECH | QTC3225THJ46XIB | QTC3225THJ46VSD | 225 | 6 SCROLL / 2 CKT | R-454B | 216 | 241.6 | 10.73 | 18.53 | 95 | 54 | 44 | 515.5 | 18.3 | 230 / 650 | 460/3 | 470 | 500 | 100 | 10606 | 274.8 x 88.3 x 94.2 | 225 | 460/3 | SCROLL | R-454B | QTC3225THJ46VSD | Quantech QTC3 Engineering Guide QTC3-EG6 | Quantech QTC3 IOM QTC3-NM1
QUANTECH | QTC4230S | QTC4230SXXX46R | 230 | 2 VSD SCREW / 2 CKT | R-513A | 228 | 281.3 | 9.727 | 18.57 | 95 | 54 | 44 | 545.7 | 14.2 | 250 / 980 | 460/3 | 425 | 600 | 101 | 14991 | 291.2 x 88.3 x 94.6 | 230 | 460/3 | VSD SCREW | R-513A | QTC4230SXXX46R | Quantech QTC4 Engineering Guide QTC4-EG2 | Quantech QTC4 IOM QTC4-NM2
QUANTECH | QTC4270S | QTC4270SXXX46R | 270 | 2 VSD SCREW / 2 CKT | R-513A | 268.2 | 324 | 9.933 | 19.16 | 95 | 54 | 44 | 641.8 | 19.7 | 300 / 1170 | 460/3 | 484.9 | 600 | 103 | 18488 | 335.2 x 88.3 x 94.6 | 270 | 460/3 | VSD SCREW | R-513A | QTC4270SXXX46R | Quantech QTC4 Engineering Guide QTC4-EG2 | Quantech QTC4 IOM QTC4-NM2
QUANTECH | QTC4340S | QTC4340SXXX46R | 340 | 2 VSD SCREW / 2 CKT | R-513A | 351 | 429.3 | 9.81 | 18.79 | 95 | 54 | 44 | 840 | 17.7 | 410 / 1600 | 460/3 | 642.2 | 800 | 105 | 21632 | 423.1 x 88.3 x 94.6 | 340 | 460/3 | VSD SCREW | R-513A | QTC4340SXXX46R | Quantech QTC4 Engineering Guide QTC4-EG2 | Quantech QTC4 IOM QTC4-NM2

## SCHEDULE NOTES
Performance at AHRI 550/590 conditions: 54°F entering / 44°F leaving water, 95°F ambient, 0.0001 fouling factor, sea level.
Stocked unit - confirm availability with Hoffman & Hoffman before release.
Unit supplied with factory options per the stock unit submittal; refer to the submittal for the included option list.

## SOURCES
Source: Quantech selection reports / stock submittals in the quantech-cut-sheets R2 bucket (https://pub-80ab44a77b30432aa7f44a4ac131fe9e.r2.dev/), one file per stocked unit.
Report dates: 2023/05/16, 2025/05/05, 2025/05/19, 2026/04/21. QTC4 (VSD screw, R-513A) reports are from 2023 - confirm current performance before quoting.
All values as printed on the Performance Report pages: Model No., capacity, total power input, EER, IPLV.IP, A-weighted sound power, evaporator EWT/LWT/flow/evaporator pressure drop, min/max flow, MCA, max dual element fuse (QTC3) or max fuse/CB rating (QTC4) as MOCP, operating weight, length/width/height.
EVAP WPD is the evaporator pressure drop only. QTC3 reports also print strainer and extension-kit drops (total shown on the submittal); QTC4 reports print the evaporator drop only.
NOM TONS is the size in the model number (e.g. QTC3129 -> 129); CAPACITY is the rated capacity.
Left out - reports to re-run:
QTC3070TSJ17VSD: report CH-13 is named QTC3070TSJ17VSD but the selection is QTC3070TSJ46XFB (460/3/60).
QTC3075TSJ17VSD: report CH-16 is named QTC3075TSJ17VSD but the selection is QTC3040THJ17XCB (38.98 tons).