## SCHEDULE
SCHEDULE RANGE | [21 empty] | FILTERS | [5 empty] | DOCUMENTATION
WATER SOURCE HEAT PUMPS | [21 empty] | SIZE | SERIES | CABINET | ELECTRICAL | MOTOR TYPE | MOTOR HP | SUBMITTAL | ENGINEERING MANUAL
MAKE | MODEL NUMBER | SERIES | NOM TONS | CABINET | Fan Data |  |  | Cooling Performance |  |  |  | Heating Performance |  |  |  | Water Data |  | Electrical Data |  |  | Weight (lbs)
[5 empty] | CFM | MOTOR TYPE | MOTOR HP | TOTAL CAPACITY (BTU/h) | EER | EWT (°F) | EAT DB/WB (°F) | CAPACITY (BTU/h) | COP | EWT (°F) | EAT (°F) | GPM | WPD (FT) | VOLT/PH | Unit MCA | Unit MOCP
BOSCH | CL007-1VTC | CL | 0.5 | VERTICAL | 300 | CONSTANT TORQUE ECM | 0.25 | 6100 | 13.2 | 86 | 80.6/66.2 | 8900 | 4.6 | 68 | 68 | 2 | 4.6 | 208-230/1 | 5.9 | 15 | 106 | 0.5 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL007-2VTC | CL | 0.5 | VERTICAL | 300 | CONSTANT TORQUE ECM | 0.25 | 6100 | 13.2 | 86 | 80.6/66.2 | 8900 | 4.6 | 68 | 68 | 2 | 4.6 | 265/1 | 5.1 | 15 | 106 | 0.5 | CL - COMMERCIAL LIGHT | VERTICAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL007-1HZC | CL | 0.5 | HORIZONTAL | 300 | CONSTANT TORQUE ECM | 0.25 | 6100 | 13.2 | 86 | 80.6/66.2 | 8900 | 4.6 | 68 | 68 | 2 | 4.6 | 208-230/1 | 5.9 | 15 | 98 | 0.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL007-2HZC | CL | 0.5 | HORIZONTAL | 300 | CONSTANT TORQUE ECM | 0.25 | 6100 | 13.2 | 86 | 80.6/66.2 | 8900 | 4.6 | 68 | 68 | 2 | 4.6 | 265/1 | 5.1 | 15 | 98 | 0.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL009-1VTC | CL | 0.75 | VERTICAL | 300 | CONSTANT TORQUE ECM | 0.25 | 8200 | 12.4 | 86 | 80.6/66.2 | 10500 | 4.6 | 68 | 68 | 2.25 | 5.7 | 208-230/1 | 6.5 | 15 | 112 | 0.75 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL009-2VTC | CL | 0.75 | VERTICAL | 300 | CONSTANT TORQUE ECM | 0.25 | 8200 | 12.4 | 86 | 80.6/66.2 | 10500 | 4.6 | 68 | 68 | 2.25 | 5.7 | 265/1 | 5.7 | 15 | 112 | 0.75 | CL - COMMERCIAL LIGHT | VERTICAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL009-1HZC | CL | 0.75 | HORIZONTAL | 300 | CONSTANT TORQUE ECM | 0.25 | 8200 | 12.4 | 86 | 80.6/66.2 | 10500 | 4.6 | 68 | 68 | 2.25 | 5.7 | 208-230/1 | 6.5 | 15 | 106 | 0.75 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL009-2HZC | CL | 0.75 | HORIZONTAL | 300 | CONSTANT TORQUE ECM | 0.25 | 8200 | 12.4 | 86 | 80.6/66.2 | 10500 | 4.6 | 68 | 68 | 2.25 | 5.7 | 265/1 | 5.7 | 15 | 106 | 0.75 | CL - COMMERCIAL LIGHT | HORIZONTAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL012-1VTC | CL | 1 | VERTICAL | 400 | CONSTANT TORQUE ECM | 0.25 | 10900 | 12.2 | 86 | 80.6/66.2 | 14000 | 4.5 | 68 | 68 | 3 | 9.5 | 208-230/1 | 8.1 | 15 | 117 | 1 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL012-2VTC | CL | 1 | VERTICAL | 400 | CONSTANT TORQUE ECM | 0.25 | 10900 | 12.2 | 86 | 80.6/66.2 | 14000 | 4.5 | 68 | 68 | 3 | 9.5 | 265/1 | 7.2 | 15 | 117 | 1 | CL - COMMERCIAL LIGHT | VERTICAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL012-1HZC | CL | 1 | HORIZONTAL | 400 | CONSTANT TORQUE ECM | 0.25 | 10900 | 12.2 | 86 | 80.6/66.2 | 14000 | 4.5 | 68 | 68 | 3 | 9.5 | 208-230/1 | 8.1 | 15 | 114 | 1 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL012-2HZC | CL | 1 | HORIZONTAL | 400 | CONSTANT TORQUE ECM | 0.25 | 10900 | 12.2 | 86 | 80.6/66.2 | 14000 | 4.5 | 68 | 68 | 3 | 9.5 | 265/1 | 7.2 | 15 | 114 | 1 | CL - COMMERCIAL LIGHT | HORIZONTAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CL015-1VTC | CL | 1.25 | VERTICAL | 500 | CONSTANT AIRFLOW ECM | 0.33 | 14200 | 12.8 | 86 | 80.6/66.2 | 17000 | 4.7 | 68 | 68 | 3.75 | 14 | 208-230/1 | 11.7 | 15 | 146 | 1.25 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL015-2VTC | CL | 1.25 | VERTICAL | 500 | CONSTANT AIRFLOW ECM | 0.33 | 14200 | 12.8 | 86 | 80.6/66.2 | 17000 | 4.7 | 68 | 68 | 3.75 | 14 | 265/1 | 10.6 | 15 | 146 | 1.25 | CL - COMMERCIAL LIGHT | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL015-1HZC | CL | 1.25 | HORIZONTAL | 500 | CONSTANT AIRFLOW ECM | 0.33 | 14200 | 12.8 | 86 | 80.6/66.2 | 17000 | 4.7 | 68 | 68 | 3.75 | 14 | 208-230/1 | 11.7 | 15 | 147 | 1.25 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL015-2HZC | CL | 1.25 | HORIZONTAL | 500 | CONSTANT AIRFLOW ECM | 0.33 | 14200 | 12.8 | 86 | 80.6/66.2 | 17000 | 4.7 | 68 | 68 | 3.75 | 14 | 265/1 | 10.6 | 15 | 147 | 1.25 | CL - COMMERCIAL LIGHT | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL018-1VTC | CL | 1.5 | VERTICAL | 600 | CONSTANT AIRFLOW ECM | 0.33 | 18000 | 13.8 | 86 | 80.6/66.2 | 22000 | 4.6 | 68 | 68 | 4.5 | 10.4 | 208-230/1 | 13.5 | 20 | 170 | 1.5 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL018-2VTC | CL | 1.5 | VERTICAL | 600 | CONSTANT AIRFLOW ECM | 0.33 | 18000 | 13.8 | 86 | 80.6/66.2 | 22000 | 4.6 | 68 | 68 | 4.5 | 10.4 | 265/1 | 12 | 15 | 170 | 1.5 | CL - COMMERCIAL LIGHT | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL018-1HZC | CL | 1.5 | HORIZONTAL | 600 | CONSTANT AIRFLOW ECM | 0.33 | 18000 | 13.8 | 86 | 80.6/66.2 | 22000 | 4.6 | 68 | 68 | 4.5 | 10.4 | 208-230/1 | 13.5 | 20 | 155 | 1.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL018-2HZC | CL | 1.5 | HORIZONTAL | 600 | CONSTANT AIRFLOW ECM | 0.33 | 18000 | 13.8 | 86 | 80.6/66.2 | 22000 | 4.6 | 68 | 68 | 4.5 | 10.4 | 265/1 | 12 | 15 | 155 | 1.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL024-1VTC | CL | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24200 | 14 | 86 | 80.6/66.2 | 28300 | 4.7 | 68 | 68 | 6 | 10.9 | 208-230/1 | 16.4 | 25 | 191 | 2 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL024-2VTC | CL | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24200 | 14 | 86 | 80.6/66.2 | 28300 | 4.7 | 68 | 68 | 6 | 10.9 | 265/1 | 14.2 | 20 | 191 | 2 | CL - COMMERCIAL LIGHT | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL024-3VTC | CL | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24200 | 14 | 86 | 80.6/66.2 | 28300 | 4.7 | 68 | 68 | 6 | 10.9 | 208-230/3 | 14 | 20 | 191 | 2 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL024-4VTC | CL | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24200 | 14 | 86 | 80.6/66.2 | 28300 | 4.7 | 68 | 68 | 6 | 10.9 | 460/3 | 9.7 | 15 | 191 | 2 | CL - COMMERCIAL LIGHT | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL024-1HZC | CL | 2 | HORIZONTAL | 800 | CONSTANT AIRFLOW ECM | 0.5 | 24200 | 14 | 86 | 80.6/66.2 | 28300 | 4.7 | 68 | 68 | 6 | 10.9 | 208-230/1 | 17 | 25 | 183 | 2 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CL024-2HZC | CL | 2 | HORIZONTAL | 800 | CONSTANT AIRFLOW ECM | 0.5 | 24200 | 14 | 86 | 80.6/66.2 | 28300 | 4.7 | 68 | 68 | 6 | 10.9 | 265/1 | 14.5 | 20 | 183 | 2 | CL - COMMERCIAL LIGHT | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CL024-3HZC | CL | 2 | HORIZONTAL | 800 | CONSTANT AIRFLOW ECM | 0.5 | 24200 | 14 | 86 | 80.6/66.2 | 28300 | 4.7 | 68 | 68 | 6 | 10.9 | 208-230/3 | 14.6 | 20 | 183 | 2 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CL024-4HZC | CL | 2 | HORIZONTAL | 800 | CONSTANT AIRFLOW ECM | 0.5 | 24200 | 14 | 86 | 80.6/66.2 | 28300 | 4.7 | 68 | 68 | 6 | 10.9 | 460/3 | 10.1 | 15 | 183 | 2 | CL - COMMERCIAL LIGHT | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CL030-1VTC | CL | 2.5 | VERTICAL | 950 | CONSTANT AIRFLOW ECM | 0.33 | 27700 | 13.9 | 86 | 80.6/66.2 | 34600 | 4.5 | 68 | 68 | 7.5 | 8.6 | 208-230/1 | 15.2 | 20 | 191 | 2.5 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL030-2VTC | CL | 2.5 | VERTICAL | 950 | CONSTANT AIRFLOW ECM | 0.33 | 27700 | 13.9 | 86 | 80.6/66.2 | 34600 | 4.5 | 68 | 68 | 7.5 | 8.6 | 265/1 | 18.3 | 25 | 191 | 2.5 | CL - COMMERCIAL LIGHT | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL030-3VTC | CL | 2.5 | VERTICAL | 950 | CONSTANT AIRFLOW ECM | 0.33 | 27700 | 13.9 | 86 | 80.6/66.2 | 34600 | 4.5 | 68 | 68 | 7.5 | 8.6 | 208-230/3 | 14.8 | 20 | 191 | 2.5 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL030-4VTC | CL | 2.5 | VERTICAL | 950 | CONSTANT AIRFLOW ECM | 0.33 | 27700 | 13.9 | 86 | 80.6/66.2 | 34600 | 4.5 | 68 | 68 | 7.5 | 8.6 | 460/3 | 11.1 | 15 | 191 | 2.5 | CL - COMMERCIAL LIGHT | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CL030-1HZC | CL | 2.5 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 27700 | 13.9 | 86 | 80.6/66.2 | 34600 | 4.5 | 68 | 68 | 7.5 | 8.6 | 208-230/1 | 15.8 | 20 | 187 | 2.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CL030-2HZC | CL | 2.5 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 27700 | 13.9 | 86 | 80.6/66.2 | 34600 | 4.5 | 68 | 68 | 7.5 | 8.6 | 265/1 | 18.6 | 25 | 187 | 2.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CL030-3HZC | CL | 2.5 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 27700 | 13.9 | 86 | 80.6/66.2 | 34600 | 4.5 | 68 | 68 | 7.5 | 8.6 | 208-230/3 | 15.4 | 20 | 187 | 2.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CL030-4HZC | CL | 2.5 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 27700 | 13.9 | 86 | 80.6/66.2 | 34600 | 4.5 | 68 | 68 | 7.5 | 8.6 | 460/3 | 11.4 | 15 | 187 | 2.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CL036-1VTC | CL | 3 | VERTICAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 37700 | 13.6 | 86 | 80.6/66.2 | 40000 | 4.6 | 68 | 68 | 9 | 12 | 208-230/1 | 29.2 | 45 | 215 | 3 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL036-2VTC | CL | 3 | VERTICAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 37700 | 13.6 | 86 | 80.6/66.2 | 40000 | 4.6 | 68 | 68 | 9 | 12 | 265/1 | 24.3 | 35 | 215 | 3 | CL - COMMERCIAL LIGHT | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL036-3VTC | CL | 3 | VERTICAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 37700 | 13.6 | 86 | 80.6/66.2 | 40000 | 4.6 | 68 | 68 | 9 | 12 | 208-230/3 | 23.6 | 35 | 215 | 3 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL036-4VTC | CL | 3 | VERTICAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 37700 | 13.6 | 86 | 80.6/66.2 | 40000 | 4.6 | 68 | 68 | 9 | 12 | 460/3 | 15.1 | 20 | 215 | 3 | CL - COMMERCIAL LIGHT | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL036-1HZC | CL | 3 | HORIZONTAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 37700 | 13.6 | 86 | 80.6/66.2 | 40000 | 4.6 | 68 | 68 | 9 | 12 | 208-230/1 | 29.2 | 45 | 205 | 3 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL036-2HZC | CL | 3 | HORIZONTAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 37700 | 13.6 | 86 | 80.6/66.2 | 40000 | 4.6 | 68 | 68 | 9 | 12 | 265/1 | 24.3 | 35 | 205 | 3 | CL - COMMERCIAL LIGHT | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL036-3HZC | CL | 3 | HORIZONTAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 37700 | 13.6 | 86 | 80.6/66.2 | 40000 | 4.6 | 68 | 68 | 9 | 12 | 208-230/3 | 23.6 | 35 | 205 | 3 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL036-4HZC | CL | 3 | HORIZONTAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 37700 | 13.6 | 86 | 80.6/66.2 | 40000 | 4.6 | 68 | 68 | 9 | 12 | 460/3 | 15.1 | 20 | 205 | 3 | CL - COMMERCIAL LIGHT | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL042-1VTC | CL | 3.5 | VERTICAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 39300 | 14 | 86 | 80.6/66.2 | 47400 | 4.6 | 68 | 68 | 10.5 | 15.6 | 208-230/1 | 26.8 | 40 | 228 | 3.5 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL042-3VTC | CL | 3.5 | VERTICAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 39300 | 14 | 86 | 80.6/66.2 | 47400 | 4.6 | 68 | 68 | 10.5 | 15.6 | 208-230/3 | 23.6 | 35 | 228 | 3.5 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL042-4VTC | CL | 3.5 | VERTICAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 39300 | 14 | 86 | 80.6/66.2 | 47400 | 4.6 | 68 | 68 | 10.5 | 15.6 | 460/3 | 15.1 | 20 | 228 | 3.5 | CL - COMMERCIAL LIGHT | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL042-1HZC | CL | 3.5 | HORIZONTAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 39300 | 14.1 | 86 | 80.6/66.2 | 47400 | 4.6 | 68 | 68 | 10.5 | 15.6 | 208-230/1 | 26.8 | 40 | 213 | 3.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL042-3HZC | CL | 3.5 | HORIZONTAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 39300 | 14.1 | 86 | 80.6/66.2 | 47400 | 4.6 | 68 | 68 | 10.5 | 15.6 | 208-230/3 | 23.6 | 35 | 213 | 3.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL042-4HZC | CL | 3.5 | HORIZONTAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 39300 | 14.1 | 86 | 80.6/66.2 | 47400 | 4.6 | 68 | 68 | 10.5 | 15.6 | 460/3 | 15.1 | 20 | 213 | 3.5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL048-1VTC | CL | 4 | VERTICAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46900 | 14 | 86 | 80.6/66.2 | 54000 | 4.7 | 68 | 68 | 12 | 12 | 208-230/1 | 30 | 45 | 228 | 4 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL048-3VTC | CL | 4 | VERTICAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46900 | 14 | 86 | 80.6/66.2 | 54000 | 4.7 | 68 | 68 | 12 | 12 | 208-230/3 | 23.6 | 35 | 228 | 4 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL048-4VTC | CL | 4 | VERTICAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46900 | 14 | 86 | 80.6/66.2 | 54000 | 4.7 | 68 | 68 | 12 | 12 | 460/3 | 15.8 | 20 | 228 | 4 | CL - COMMERCIAL LIGHT | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL048-1HZC | CL | 4 | HORIZONTAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46900 | 14 | 86 | 80.6/66.2 | 54000 | 4.7 | 68 | 68 | 12 | 12 | 208-230/1 | 30 | 45 | 267 | 4 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL048-3HZC | CL | 4 | HORIZONTAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46900 | 14 | 86 | 80.6/66.2 | 54000 | 4.7 | 68 | 68 | 12 | 12 | 208-230/3 | 23.6 | 35 | 267 | 4 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL048-4HZC | CL | 4 | HORIZONTAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46900 | 14 | 86 | 80.6/66.2 | 54000 | 4.7 | 68 | 68 | 12 | 12 | 460/3 | 15.8 | 20 | 267 | 4 | CL - COMMERCIAL LIGHT | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CL060-1VTC | CL | 5 | VERTICAL | 1900 | CONSTANT AIRFLOW ECM | 1 | 59500 | 13.6 | 86 | 80.6/66.2 | 74000 | 4.6 | 68 | 68 | 15 | 10.9 | 208-230/1 | 41.2 | 60 | 275 | 5 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL060-3VTC | CL | 5 | VERTICAL | 1900 | CONSTANT AIRFLOW ECM | 1 | 59500 | 13.6 | 86 | 80.6/66.2 | 74000 | 4.6 | 68 | 68 | 15 | 10.9 | 208-230/3 | 32.3 | 50 | 275 | 5 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL060-4VTC | CL | 5 | VERTICAL | 1900 | CONSTANT AIRFLOW ECM | 1 | 59500 | 13.6 | 86 | 80.6/66.2 | 74000 | 4.6 | 68 | 68 | 15 | 10.9 | 460/3 | 19.6 | 25 | 275 | 5 | CL - COMMERCIAL LIGHT | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL060-1HZC | CL | 5 | HORIZONTAL | 1900 | CONSTANT AIRFLOW ECM | 1 | 59500 | 13.6 | 86 | 80.6/66.2 | 74000 | 4.6 | 68 | 68 | 15 | 10.9 | 208-230/1 | 41.2 | 60 | 285 | 5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL060-3HZC | CL | 5 | HORIZONTAL | 1900 | CONSTANT AIRFLOW ECM | 1 | 59500 | 13.6 | 86 | 80.6/66.2 | 74000 | 4.6 | 68 | 68 | 15 | 10.9 | 208-230/3 | 32.3 | 50 | 285 | 5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL060-4HZC | CL | 5 | HORIZONTAL | 1900 | CONSTANT AIRFLOW ECM | 1 | 59500 | 13.6 | 86 | 80.6/66.2 | 74000 | 4.6 | 68 | 68 | 15 | 10.9 | 460/3 | 19.6 | 25 | 285 | 5 | CL - COMMERCIAL LIGHT | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL070-1VTC | CL | 6 | VERTICAL | 2030 | CONSTANT AIRFLOW ECM | 1 | 64000 | 13.3 | 86 | 80.6/66.2 | 73500 | 4.5 | 68 | 68 | 16 | 12.4 | 208-230/1 | 43.6 | 70 | 338 | 6 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL070-3VTC | CL | 6 | VERTICAL | 2030 | CONSTANT AIRFLOW ECM | 1 | 64000 | 13.3 | 86 | 80.6/66.2 | 73500 | 4.5 | 68 | 68 | 16 | 12.4 | 208-230/3 | 33.1 | 50 | 338 | 6 | CL - COMMERCIAL LIGHT | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL070-4VTC | CL | 6 | VERTICAL | 2030 | CONSTANT AIRFLOW ECM | 1 | 64000 | 13.3 | 86 | 80.6/66.2 | 73500 | 4.5 | 68 | 68 | 16 | 12.4 | 460/3 | 20.3 | 25 | 338 | 6 | CL - COMMERCIAL LIGHT | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL070-1HZC | CL | 6 | HORIZONTAL | 2030 | CONSTANT AIRFLOW ECM | 1 | 64000 | 13.3 | 86 | 80.6/66.2 | 73500 | 4.5 | 68 | 68 | 16 | 12.4 | 208-230/1 | 43.6 | 70 | 296 | 6 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL070-3HZC | CL | 6 | HORIZONTAL | 2030 | CONSTANT AIRFLOW ECM | 1 | 64000 | 13.3 | 86 | 80.6/66.2 | 73500 | 4.5 | 68 | 68 | 16 | 12.4 | 208-230/3 | 33.1 | 50 | 296 | 6 | CL - COMMERCIAL LIGHT | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CL070-4HZC | CL | 6 | HORIZONTAL | 2030 | CONSTANT AIRFLOW ECM | 1 | 64000 | 13.3 | 86 | 80.6/66.2 | 73500 | 4.5 | 68 | 68 | 16 | 12.4 | 460/3 | 20.3 | 25 | 296 | 6 | CL - COMMERCIAL LIGHT | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF007-1VTC | CF | 0.5 | VERTICAL | 300 | CONSTANT TORQUE ECM | 0.25 | 7000 | 16 | 86 | 80.6/66.2 | 8500 | 5.5 | 68 | 68 | 2 | 4.2 | 208-230/1 | 5.7 | 15 | 136 | 0.5 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF007-2VTC | CF | 0.5 | VERTICAL | 300 | CONSTANT TORQUE ECM | 0.25 | 7000 | 16 | 86 | 80.6/66.2 | 8500 | 5.5 | 68 | 68 | 2 | 4.2 | 265/1 | 5.1 | 15 | 136 | 0.5 | CF - COMMERCIAL FLEX | VERTICAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF007-1HZC | CF | 0.5 | HORIZONTAL | 300 | CONSTANT TORQUE ECM | 0.25 | 7000 | 16 | 86 | 80.6/66.2 | 8500 | 5.5 | 68 | 68 | 2 | 4.2 | 208-230/1 | 5.7 | 15 | 144 | 0.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF007-2HZC | CF | 0.5 | HORIZONTAL | 300 | CONSTANT TORQUE ECM | 0.25 | 7000 | 16 | 86 | 80.6/66.2 | 8500 | 5.5 | 68 | 68 | 2 | 4.2 | 265/1 | 5.1 | 15 | 144 | 0.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF009-1VTC | CF | 0.75 | VERTICAL | 330 | CONSTANT TORQUE ECM | 0.25 | 8900 | 15 | 86 | 80.6/66.2 | 10500 | 5.5 | 68 | 68 | 2.5 | 9.2 | 208-230/1 | 6.4 | 15 | 134 | 0.75 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF009-2VTC | CF | 0.75 | VERTICAL | 330 | CONSTANT TORQUE ECM | 0.25 | 8900 | 15 | 86 | 80.6/66.2 | 10500 | 5.5 | 68 | 68 | 2.5 | 9.2 | 265/1 | 5.7 | 15 | 134 | 0.75 | CF - COMMERCIAL FLEX | VERTICAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF009-1HZC | CF | 0.75 | HORIZONTAL | 330 | CONSTANT TORQUE ECM | 0.25 | 8900 | 15 | 86 | 80.6/66.2 | 10500 | 5.5 | 68 | 68 | 2.5 | 9.2 | 208-230/1 | 6.4 | 15 | 136 | 0.75 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF009-2HZC | CF | 0.75 | HORIZONTAL | 330 | CONSTANT TORQUE ECM | 0.25 | 8900 | 15 | 86 | 80.6/66.2 | 10500 | 5.5 | 68 | 68 | 2.5 | 9.2 | 265/1 | 5.7 | 15 | 136 | 0.75 | CF - COMMERCIAL FLEX | HORIZONTAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF012-1VTC | CF | 1 | VERTICAL | 400 | CONSTANT TORQUE ECM | 0.25 | 12000 | 15 | 86 | 80.6/66.2 | 14500 | 5 | 68 | 68 | 3 | 8.8 | 208-230/1 | 8.2 | 15 | 145 | 1 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF012-2VTC | CF | 1 | VERTICAL | 400 | CONSTANT TORQUE ECM | 0.25 | 12000 | 15 | 86 | 80.6/66.2 | 14500 | 5 | 68 | 68 | 3 | 8.8 | 265/1 | 6.9 | 15 | 145 | 1 | CF - COMMERCIAL FLEX | VERTICAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF012-1HZC | CF | 1 | HORIZONTAL | 400 | CONSTANT TORQUE ECM | 0.25 | 12000 | 15 | 86 | 80.6/66.2 | 14500 | 5 | 68 | 68 | 3 | 8.8 | 208-230/1 | 8.2 | 15 | 153 | 1 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF012-2HZC | CF | 1 | HORIZONTAL | 400 | CONSTANT TORQUE ECM | 0.25 | 12000 | 15 | 86 | 80.6/66.2 | 14500 | 5 | 68 | 68 | 3 | 8.8 | 265/1 | 6.9 | 15 | 153 | 1 | CF - COMMERCIAL FLEX | HORIZONTAL | 265/1 | CONSTANT TORQUE ECM | 0.25
BOSCH | CF015-1VTC | CF | 1.25 | VERTICAL | 500 | CONSTANT AIRFLOW ECM | 0.33 | 14900 | 15.5 | 86 | 80.6/66.2 | 17000 | 5.2 | 68 | 68 | 3.75 | 9.7 | 208-230/1 | 11.7 | 15 | 152 | 1.25 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF015-2VTC | CF | 1.25 | VERTICAL | 500 | CONSTANT AIRFLOW ECM | 0.33 | 14900 | 15.5 | 86 | 80.6/66.2 | 17000 | 5.2 | 68 | 68 | 3.75 | 9.7 | 265/1 | 10.6 | 15 | 152 | 1.25 | CF - COMMERCIAL FLEX | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF015-1HZC | CF | 1.25 | HORIZONTAL | 500 | CONSTANT AIRFLOW ECM | 0.33 | 14900 | 15.5 | 86 | 80.6/66.2 | 17000 | 5.2 | 68 | 68 | 3.75 | 9.7 | 208-230/1 | 11.7 | 15 | 155 | 1.25 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF015-2HZC | CF | 1.25 | HORIZONTAL | 500 | CONSTANT AIRFLOW ECM | 0.33 | 14900 | 15.5 | 86 | 80.6/66.2 | 17000 | 5.2 | 68 | 68 | 3.75 | 9.7 | 265/1 | 10.6 | 15 | 155 | 1.25 | CF - COMMERCIAL FLEX | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF018-1VTC | CF | 1.5 | VERTICAL | 600 | CONSTANT AIRFLOW ECM | 0.33 | 19000 | 15.5 | 86 | 80.6/66.2 | 21300 | 5 | 68 | 68 | 4.75 | 7.9 | 208-230/1 | 13.7 | 20 | 177 | 1.5 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF018-2VTC | CF | 1.5 | VERTICAL | 600 | CONSTANT AIRFLOW ECM | 0.33 | 19000 | 15.5 | 86 | 80.6/66.2 | 21300 | 5 | 68 | 68 | 4.75 | 7.9 | 265/1 | 14.2 | 20 | 177 | 1.5 | CF - COMMERCIAL FLEX | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF018-1HZC | CF | 1.5 | HORIZONTAL | 600 | CONSTANT AIRFLOW ECM | 0.33 | 19000 | 15.5 | 86 | 80.6/66.2 | 21300 | 5 | 68 | 68 | 4.75 | 7.9 | 208-230/1 | 13.7 | 20 | 173 | 1.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF018-2HZC | CF | 1.5 | HORIZONTAL | 600 | CONSTANT AIRFLOW ECM | 0.33 | 19000 | 15.5 | 86 | 80.6/66.2 | 21300 | 5 | 68 | 68 | 4.75 | 7.9 | 265/1 | 14.2 | 20 | 173 | 1.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-1VTC | CF | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24000 | 15.5 | 86 | 80.6/66.2 | 28000 | 5 | 68 | 68 | 6 | 8.3 | 208-230/1 | 17.2 | 25 | 197 | 2 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-2VTC | CF | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24000 | 15.5 | 86 | 80.6/66.2 | 28000 | 5 | 68 | 68 | 6 | 8.3 | 265/1 | 14.5 | 20 | 197 | 2 | CF - COMMERCIAL FLEX | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-3VTC | CF | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24000 | 15.5 | 86 | 80.6/66.2 | 28000 | 5 | 68 | 68 | 6 | 8.3 | 208-230/3 | 12.3 | 15 | 197 | 2 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-4VTC | CF | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24000 | 15.5 | 86 | 80.6/66.2 | 28000 | 5 | 68 | 68 | 6 | 8.3 | 460/3 | 9.7 | 15 | 197 | 2 | CF - COMMERCIAL FLEX | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-1HZC | CF | 2 | HORIZONTAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24000 | 15.5 | 86 | 80.6/66.2 | 28000 | 5 | 68 | 68 | 6 | 8.3 | 208-230/1 | 17.2 | 25 | 194 | 2 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-2HZC | CF | 2 | HORIZONTAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24000 | 15.5 | 86 | 80.6/66.2 | 28000 | 5 | 68 | 68 | 6 | 8.3 | 265/1 | 14.5 | 20 | 194 | 2 | CF - COMMERCIAL FLEX | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-3HZC | CF | 2 | HORIZONTAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24000 | 15.5 | 86 | 80.6/66.2 | 28000 | 5 | 68 | 68 | 6 | 8.3 | 208-230/3 | 12.3 | 15 | 194 | 2 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-4HZC | CF | 2 | HORIZONTAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 24000 | 15.5 | 86 | 80.6/66.2 | 28000 | 5 | 68 | 68 | 6 | 8.3 | 460/3 | 9.7 | 15 | 194 | 2 | CF - COMMERCIAL FLEX | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-1CFC | CF | 2 | COUNTERFLOW | 800 | CONSTANT AIRFLOW ECM | 0.33 | 23200 | 15 | 86 | 80.6/66.2 | 27200 | 4.8 | 68 | 68 | 6 | 8.3 | 208-230/1 | 17.2 | 25 | 193 | 2 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-2CFC | CF | 2 | COUNTERFLOW | 800 | CONSTANT AIRFLOW ECM | 0.33 | 23200 | 15 | 86 | 80.6/66.2 | 27200 | 4.8 | 68 | 68 | 6 | 8.3 | 265/1 | 14.5 | 20 | 193 | 2 | CF - COMMERCIAL FLEX | COUNTERFLOW | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-3CFC | CF | 2 | COUNTERFLOW | 800 | CONSTANT AIRFLOW ECM | 0.33 | 23200 | 15 | 86 | 80.6/66.2 | 27200 | 4.8 | 68 | 68 | 6 | 8.3 | 208-230/3 | 12.3 | 15 | 193 | 2 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF024-4CFC | CF | 2 | COUNTERFLOW | 800 | CONSTANT AIRFLOW ECM | 0.33 | 23200 | 15 | 86 | 80.6/66.2 | 27200 | 4.8 | 68 | 68 | 6 | 8.3 | 460/3 | 9.7 | 15 | 193 | 2 | CF - COMMERCIAL FLEX | COUNTERFLOW | 460/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CF030-1VTC | CF | 2.5 | VERTICAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 30000 | 15 | 86 | 80.6/66.2 | 34000 | 5 | 68 | 68 | 7.5 | 12.5 | 208-230/1 | 23.2 | 35 | 212 | 2.5 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-2VTC | CF | 2.5 | VERTICAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 30000 | 15 | 86 | 80.6/66.2 | 34000 | 5 | 68 | 68 | 7.5 | 12.5 | 265/1 | 15.4 | 20 | 212 | 2.5 | CF - COMMERCIAL FLEX | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-3VTC | CF | 2.5 | VERTICAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 30000 | 15 | 86 | 80.6/66.2 | 34000 | 5 | 68 | 68 | 7.5 | 12.5 | 208-230/3 | 14.9 | 20 | 212 | 2.5 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-4VTC | CF | 2.5 | VERTICAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 30000 | 15 | 86 | 80.6/66.2 | 34000 | 5 | 68 | 68 | 7.5 | 12.5 | 460/3 | 11.1 | 15 | 212 | 2.5 | CF - COMMERCIAL FLEX | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-1HZC | CF | 2.5 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 30000 | 15 | 86 | 80.6/66.2 | 34000 | 5 | 68 | 68 | 7.5 | 12.5 | 208-230/1 | 23.2 | 35 | 204 | 2.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-2HZC | CF | 2.5 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 30000 | 15 | 86 | 80.6/66.2 | 34000 | 5 | 68 | 68 | 7.5 | 12.5 | 265/1 | 15.4 | 20 | 204 | 2.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-3HZC | CF | 2.5 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 30000 | 15 | 86 | 80.6/66.2 | 34000 | 5 | 68 | 68 | 7.5 | 12.5 | 208-230/3 | 14.9 | 20 | 204 | 2.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-4HZC | CF | 2.5 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.5 | 30000 | 15 | 86 | 80.6/66.2 | 34000 | 5 | 68 | 68 | 7.5 | 12.5 | 460/3 | 11.1 | 15 | 204 | 2.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-1CFC | CF | 2.5 | COUNTERFLOW | 950 | CONSTANT AIRFLOW ECM | 0.5 | 29000 | 14.6 | 86 | 80.6/66.2 | 33000 | 4.8 | 68 | 68 | 7.5 | 12.5 | 208-230/1 | 23.2 | 35 | 204 | 2.5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-2CFC | CF | 2.5 | COUNTERFLOW | 950 | CONSTANT AIRFLOW ECM | 0.5 | 29000 | 14.6 | 86 | 80.6/66.2 | 33000 | 4.8 | 68 | 68 | 7.5 | 12.5 | 265/1 | 15.4 | 20 | 204 | 2.5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 265/1 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-3CFC | CF | 2.5 | COUNTERFLOW | 950 | CONSTANT AIRFLOW ECM | 0.5 | 29000 | 14.6 | 86 | 80.6/66.2 | 33000 | 4.8 | 68 | 68 | 7.5 | 12.5 | 208-230/3 | 14.9 | 20 | 204 | 2.5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF030-4CFC | CF | 2.5 | COUNTERFLOW | 950 | CONSTANT AIRFLOW ECM | 0.5 | 29000 | 14.6 | 86 | 80.6/66.2 | 33000 | 4.8 | 68 | 68 | 7.5 | 12.5 | 460/3 | 11.1 | 15 | 204 | 2.5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 460/3 | CONSTANT AIRFLOW ECM | 0.5
BOSCH | CF036-1VTC | CF | 3 | VERTICAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 36000 | 15 | 86 | 80.6/66.2 | 42000 | 5 | 68 | 68 | 9 | 16.6 | 208-230/1 | 26.6 | 40 | 233 | 3 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-2VTC | CF | 3 | VERTICAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 36000 | 15 | 86 | 80.6/66.2 | 42000 | 5 | 68 | 68 | 9 | 16.6 | 265/1 | 23.2 | 35 | 233 | 3 | CF - COMMERCIAL FLEX | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-3VTC | CF | 3 | VERTICAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 36000 | 15 | 86 | 80.6/66.2 | 42000 | 5 | 68 | 68 | 9 | 16.6 | 208-230/3 | 20.7 | 30 | 233 | 3 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-4VTC | CF | 3 | VERTICAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 36000 | 15 | 86 | 80.6/66.2 | 42000 | 5 | 68 | 68 | 9 | 16.6 | 460/3 | 14.2 | 20 | 233 | 3 | CF - COMMERCIAL FLEX | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-1HZC | CF | 3 | HORIZONTAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 36000 | 15 | 86 | 80.6/66.2 | 42000 | 5 | 68 | 68 | 9 | 16.6 | 208-230/1 | 26.6 | 40 | 205 | 3 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-2HZC | CF | 3 | HORIZONTAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 36000 | 15 | 86 | 80.6/66.2 | 42000 | 5 | 68 | 68 | 9 | 16.6 | 265/1 | 23.2 | 35 | 205 | 3 | CF - COMMERCIAL FLEX | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-3HZC | CF | 3 | HORIZONTAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 36000 | 15 | 86 | 80.6/66.2 | 42000 | 5 | 68 | 68 | 9 | 16.6 | 208-230/3 | 20.7 | 30 | 205 | 3 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-4HZC | CF | 3 | HORIZONTAL | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 36000 | 15 | 86 | 80.6/66.2 | 42000 | 5 | 68 | 68 | 9 | 16.6 | 460/3 | 14.2 | 20 | 205 | 3 | CF - COMMERCIAL FLEX | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-1CFC | CF | 3 | COUNTERFLOW | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 35000 | 14.6 | 86 | 80.6/66.2 | 40800 | 4.8 | 68 | 68 | 9 | 16.6 | 208-230/1 | 26.6 | 40 | 226 | 3 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-2CFC | CF | 3 | COUNTERFLOW | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 35000 | 14.6 | 86 | 80.6/66.2 | 40800 | 4.8 | 68 | 68 | 9 | 16.6 | 265/1 | 23.2 | 35 | 226 | 3 | CF - COMMERCIAL FLEX | COUNTERFLOW | 265/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-3CFC | CF | 3 | COUNTERFLOW | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 35000 | 14.6 | 86 | 80.6/66.2 | 40800 | 4.8 | 68 | 68 | 9 | 16.6 | 208-230/3 | 20.7 | 30 | 226 | 3 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF036-4CFC | CF | 3 | COUNTERFLOW | 1200 | CONSTANT AIRFLOW ECM | 0.75 | 35000 | 14.6 | 86 | 80.6/66.2 | 40800 | 4.8 | 68 | 68 | 9 | 16.6 | 460/3 | 14.2 | 20 | 226 | 3 | CF - COMMERCIAL FLEX | COUNTERFLOW | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-1VTC | CF | 3.5 | VERTICAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 42000 | 15 | 86 | 80.6/66.2 | 50000 | 5 | 68 | 68 | 10.5 | 15.5 | 208-230/1 | 31.2 | 45 | 271 | 3.5 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-3VTC | CF | 3.5 | VERTICAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 42000 | 15 | 86 | 80.6/66.2 | 50000 | 5 | 68 | 68 | 10.5 | 15.5 | 208-230/3 | 22.7 | 30 | 271 | 3.5 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-4VTC | CF | 3.5 | VERTICAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 42000 | 15 | 86 | 80.6/66.2 | 50000 | 5 | 68 | 68 | 10.5 | 15.5 | 460/3 | 15.8 | 20 | 271 | 3.5 | CF - COMMERCIAL FLEX | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-1HZC | CF | 3.5 | HORIZONTAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 42000 | 15 | 86 | 80.6/66.2 | 50000 | 5 | 68 | 68 | 10.5 | 15.5 | 208-230/1 | 31.2 | 45 | 281 | 3.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-3HZC | CF | 3.5 | HORIZONTAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 42000 | 15 | 86 | 80.6/66.2 | 50000 | 5 | 68 | 68 | 10.5 | 15.5 | 208-230/3 | 22.7 | 30 | 281 | 3.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-4HZC | CF | 3.5 | HORIZONTAL | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 42000 | 15 | 86 | 80.6/66.2 | 50000 | 5 | 68 | 68 | 10.5 | 15.5 | 460/3 | 15.8 | 20 | 281 | 3.5 | CF - COMMERCIAL FLEX | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-1CFC | CF | 3.5 | COUNTERFLOW | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 40500 | 14.6 | 86 | 80.6/66.2 | 48500 | 4.8 | 68 | 68 | 10.5 | 15.5 | 208-230/1 | 31.2 | 45 | 274 | 3.5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-3CFC | CF | 3.5 | COUNTERFLOW | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 40500 | 14.6 | 86 | 80.6/66.2 | 48500 | 4.8 | 68 | 68 | 10.5 | 15.5 | 208-230/3 | 22.7 | 30 | 274 | 3.5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF042-4CFC | CF | 3.5 | COUNTERFLOW | 1400 | CONSTANT AIRFLOW ECM | 0.75 | 40500 | 14.6 | 86 | 80.6/66.2 | 48500 | 4.8 | 68 | 68 | 10.5 | 15.5 | 460/3 | 15.8 | 20 | 274 | 3.5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-1VTC | CF | 4 | VERTICAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 48000 | 15 | 86 | 80.6/66.2 | 58000 | 5 | 68 | 68 | 12 | 9.2 | 208-230/1 | 31.3 | 45 | 276 | 4 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-3VTC | CF | 4 | VERTICAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 48000 | 15 | 86 | 80.6/66.2 | 58000 | 5 | 68 | 68 | 12 | 9.2 | 208-230/3 | 23.3 | 35 | 276 | 4 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-4VTC | CF | 4 | VERTICAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 48000 | 15 | 86 | 80.6/66.2 | 58000 | 5 | 68 | 68 | 12 | 9.2 | 460/3 | 16.2 | 20 | 276 | 4 | CF - COMMERCIAL FLEX | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-1HZC | CF | 4 | HORIZONTAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 48000 | 15 | 86 | 80.6/66.2 | 58000 | 5 | 68 | 68 | 12 | 9.2 | 208-230/1 | 31.3 | 45 | 292 | 4 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-3HZC | CF | 4 | HORIZONTAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 48000 | 15 | 86 | 80.6/66.2 | 58000 | 5 | 68 | 68 | 12 | 9.2 | 208-230/3 | 23.3 | 35 | 292 | 4 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-4HZC | CF | 4 | HORIZONTAL | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 48000 | 15 | 86 | 80.6/66.2 | 58000 | 5 | 68 | 68 | 12 | 9.2 | 460/3 | 16.2 | 20 | 292 | 4 | CF - COMMERCIAL FLEX | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-1CFC | CF | 4 | COUNTERFLOW | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46500 | 14.6 | 86 | 80.6/66.2 | 56500 | 4.8 | 68 | 68 | 12 | 9.2 | 208-230/1 | 31.3 | 45 | 286 | 4 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-3CFC | CF | 4 | COUNTERFLOW | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46500 | 14.6 | 86 | 80.6/66.2 | 56500 | 4.8 | 68 | 68 | 12 | 9.2 | 208-230/3 | 23.3 | 35 | 286 | 4 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF048-4CFC | CF | 4 | COUNTERFLOW | 1600 | CONSTANT AIRFLOW ECM | 0.75 | 46500 | 14.6 | 86 | 80.6/66.2 | 56500 | 4.8 | 68 | 68 | 12 | 9.2 | 460/3 | 16.2 | 20 | 286 | 4 | CF - COMMERCIAL FLEX | COUNTERFLOW | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CF060-1VTC | CF | 5 | VERTICAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 60000 | 14.5 | 86 | 80.6/66.2 | 69000 | 5 | 68 | 68 | 15 | 14.1 | 208-230/1 | 40.6 | 60 | 347 | 5 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF060-3VTC | CF | 5 | VERTICAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 60000 | 14.5 | 86 | 80.6/66.2 | 69000 | 5 | 68 | 68 | 15 | 14.1 | 208-230/3 | 26.3 | 40 | 347 | 5 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF060-4VTC | CF | 5 | VERTICAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 60000 | 14.5 | 86 | 80.6/66.2 | 69000 | 5 | 68 | 68 | 15 | 14.1 | 460/3 | 18.2 | 25 | 347 | 5 | CF - COMMERCIAL FLEX | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF060-1HZC | CF | 5 | HORIZONTAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 60000 | 14.5 | 86 | 80.6/66.2 | 69000 | 5 | 68 | 68 | 15 | 14.1 | 208-230/1 | 40.6 | 60 | 319 | 5 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF060-3HZC | CF | 5 | HORIZONTAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 60000 | 14.5 | 86 | 80.6/66.2 | 69000 | 5 | 68 | 68 | 15 | 14.1 | 208-230/3 | 26.3 | 40 | 319 | 5 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF060-4HZC | CF | 5 | HORIZONTAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 60000 | 14.5 | 86 | 80.6/66.2 | 69000 | 5 | 68 | 68 | 15 | 14.1 | 460/3 | 18.2 | 25 | 319 | 5 | CF - COMMERCIAL FLEX | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF060-1CFC | CF | 5 | COUNTERFLOW | 2000 | CONSTANT AIRFLOW ECM | 1 | 58000 | 14.1 | 86 | 80.6/66.2 | 67000 | 4.8 | 68 | 68 | 15 | 14.1 | 208-230/1 | 40.6 | 60 | 343 | 5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF060-3CFC | CF | 5 | COUNTERFLOW | 2000 | CONSTANT AIRFLOW ECM | 1 | 58000 | 14.1 | 86 | 80.6/66.2 | 67000 | 4.8 | 68 | 68 | 15 | 14.1 | 208-230/3 | 26.3 | 40 | 343 | 5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF060-4CFC | CF | 5 | COUNTERFLOW | 2000 | CONSTANT AIRFLOW ECM | 1 | 58000 | 14.1 | 86 | 80.6/66.2 | 67000 | 4.8 | 68 | 68 | 15 | 14.1 | 460/3 | 18.2 | 25 | 343 | 5 | CF - COMMERCIAL FLEX | COUNTERFLOW | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-1VTC | CF | 6 | VERTICAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 68000 | 14 | 86 | 80.6/66.2 | 80000 | 4.9 | 68 | 68 | 17 | 17.6 | 208-230/1 | 44.1 | 70 | 323 | 6 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-3VTC | CF | 6 | VERTICAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 68000 | 14 | 86 | 80.6/66.2 | 80000 | 4.9 | 68 | 68 | 17 | 17.6 | 208-230/3 | 32.7 | 50 | 323 | 6 | CF - COMMERCIAL FLEX | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-4VTC | CF | 6 | VERTICAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 68000 | 14 | 86 | 80.6/66.2 | 80000 | 4.9 | 68 | 68 | 17 | 17.6 | 460/3 | 20.5 | 25 | 323 | 6 | CF - COMMERCIAL FLEX | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-1HZC | CF | 6 | HORIZONTAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 65000 | 13.5 | 86 | 80.6/66.2 | 80000 | 4.3 | 68 | 68 | 17 | 17.6 | 208-230/1 | 44.1 | 70 | 321 | 6 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-3HZC | CF | 6 | HORIZONTAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 65000 | 13.5 | 86 | 80.6/66.2 | 80000 | 4.3 | 68 | 68 | 17 | 17.6 | 208-230/3 | 32.7 | 50 | 321 | 6 | CF - COMMERCIAL FLEX | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-4HZC | CF | 6 | HORIZONTAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 65000 | 13.5 | 86 | 80.6/66.2 | 80000 | 4.3 | 68 | 68 | 17 | 17.6 | 460/3 | 20.5 | 25 | 321 | 6 | CF - COMMERCIAL FLEX | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-1CFC | CF | 6 | COUNTERFLOW | 2100 | CONSTANT AIRFLOW ECM | 1 | 66000 | 13.6 | 86 | 80.6/66.2 | 77000 | 4.8 | 68 | 68 | 17 | 17.6 | 208-230/1 | 44.1 | 70 | 326 | 6 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-3CFC | CF | 6 | COUNTERFLOW | 2100 | CONSTANT AIRFLOW ECM | 1 | 66000 | 13.6 | 86 | 80.6/66.2 | 77000 | 4.8 | 68 | 68 | 17 | 17.6 | 208-230/3 | 32.7 | 50 | 326 | 6 | CF - COMMERCIAL FLEX | COUNTERFLOW | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CF070-4CFC | CF | 6 | COUNTERFLOW | 2100 | CONSTANT AIRFLOW ECM | 1 | 66000 | 13.6 | 86 | 80.6/66.2 | 77000 | 4.8 | 68 | 68 | 17 | 17.6 | 460/3 | 20.5 | 25 | 326 | 6 | CF - COMMERCIAL FLEX | COUNTERFLOW | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP024-1VTC | CP | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 25000 | 16.5 | 86 | 80.6/66.2 | 28500 | 5.6 | 68 | 68 | 6 | 8.5 | 208-230/1 | 17.2 | 25 | 219 | 2 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CP024-2VTC | CP | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 25000 | 16.5 | 86 | 80.6/66.2 | 28500 | 5.6 | 68 | 68 | 6 | 8.5 | 265/1 | 14.5 | 20 | 219 | 2 | CP - COMMERCIAL PREMIUM | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CP024-3VTC | CP | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 25000 | 16.5 | 86 | 80.6/66.2 | 28500 | 5.6 | 68 | 68 | 6 | 8.5 | 208-230/3 | 12.3 | 15 | 219 | 2 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CP024-4VTC | CP | 2 | VERTICAL | 800 | CONSTANT AIRFLOW ECM | 0.33 | 25000 | 16.5 | 86 | 80.6/66.2 | 28500 | 5.6 | 68 | 68 | 6 | 8.5 | 460/3 | 9.7 | 15 | 219 | 2 | CP - COMMERCIAL PREMIUM | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CP024-1HZC | CP | 2 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.33 | 25000 | 16.5 | 86 | 80.6/66.2 | 28500 | 5.6 | 68 | 68 | 6.5 | 9.8 | 208-230/1 | 17.2 | 25 | 213 | 2 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CP024-2HZC | CP | 2 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.33 | 25000 | 16.5 | 86 | 80.6/66.2 | 28500 | 5.6 | 68 | 68 | 6.5 | 9.8 | 265/1 | 14.5 | 20 | 213 | 2 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CP024-3HZC | CP | 2 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.33 | 25000 | 16.5 | 86 | 80.6/66.2 | 28500 | 5.6 | 68 | 68 | 6.5 | 9.8 | 208-230/3 | 12.3 | 15 | 213 | 2 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CP024-4HZC | CP | 2 | HORIZONTAL | 950 | CONSTANT AIRFLOW ECM | 0.33 | 25000 | 16.5 | 86 | 80.6/66.2 | 28500 | 5.6 | 68 | 68 | 6.5 | 9.8 | 460/3 | 9.7 | 15 | 213 | 2 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.33
BOSCH | CP036-1VTC | CP | 3 | VERTICAL | 1300 | CONSTANT AIRFLOW ECM | 0.75 | 37500 | 16 | 86 | 80.6/66.2 | 44000 | 5.6 | 68 | 68 | 10 | 7.5 | 208-230/1 | 26.6 | 40 | 255 | 3 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP036-2VTC | CP | 3 | VERTICAL | 1300 | CONSTANT AIRFLOW ECM | 0.75 | 37500 | 16 | 86 | 80.6/66.2 | 44000 | 5.6 | 68 | 68 | 10 | 7.5 | 265/1 | 23.2 | 35 | 255 | 3 | CP - COMMERCIAL PREMIUM | VERTICAL | 265/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP036-3VTC | CP | 3 | VERTICAL | 1300 | CONSTANT AIRFLOW ECM | 0.75 | 37500 | 16 | 86 | 80.6/66.2 | 44000 | 5.6 | 68 | 68 | 10 | 7.5 | 208-230/3 | 20.7 | 30 | 255 | 3 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP036-4VTC | CP | 3 | VERTICAL | 1300 | CONSTANT AIRFLOW ECM | 0.75 | 37500 | 16 | 86 | 80.6/66.2 | 44000 | 5.6 | 68 | 68 | 10 | 7.5 | 460/3 | 14.2 | 20 | 255 | 3 | CP - COMMERCIAL PREMIUM | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP036-1HZC | CP | 3 | HORIZONTAL | 1300 | CONSTANT AIRFLOW ECM | 0.75 | 37500 | 16 | 86 | 80.6/66.2 | 44000 | 5.6 | 68 | 68 | 10 | 7.5 | 208-230/1 | 26.6 | 40 | 263 | 3 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP036-2HZC | CP | 3 | HORIZONTAL | 1300 | CONSTANT AIRFLOW ECM | 0.75 | 37500 | 16 | 86 | 80.6/66.2 | 44000 | 5.6 | 68 | 68 | 10 | 7.5 | 265/1 | 23.2 | 35 | 263 | 3 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 265/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP036-3HZC | CP | 3 | HORIZONTAL | 1300 | CONSTANT AIRFLOW ECM | 0.75 | 37500 | 16 | 86 | 80.6/66.2 | 44000 | 5.6 | 68 | 68 | 10 | 7.5 | 208-230/3 | 20.7 | 30 | 263 | 3 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP036-4HZC | CP | 3 | HORIZONTAL | 1300 | CONSTANT AIRFLOW ECM | 0.75 | 37500 | 16 | 86 | 80.6/66.2 | 44000 | 5.6 | 68 | 68 | 10 | 7.5 | 460/3 | 14.2 | 20 | 263 | 3 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP048-1VTC | CP | 4 | VERTICAL | 1700 | CONSTANT AIRFLOW ECM | 0.75 | 49500 | 16 | 86 | 80.6/66.2 | 58000 | 5.6 | 68 | 68 | 12 | 9 | 208-230/1 | 31.3 | 45 | 324 | 4 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP048-3VTC | CP | 4 | VERTICAL | 1700 | CONSTANT AIRFLOW ECM | 0.75 | 49500 | 16 | 86 | 80.6/66.2 | 58000 | 5.6 | 68 | 68 | 12 | 9 | 208-230/3 | 23.3 | 35 | 324 | 4 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP048-4VTC | CP | 4 | VERTICAL | 1700 | CONSTANT AIRFLOW ECM | 0.75 | 49500 | 16 | 86 | 80.6/66.2 | 58000 | 5.6 | 68 | 68 | 12 | 9 | 460/3 | 16.2 | 20 | 324 | 4 | CP - COMMERCIAL PREMIUM | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP048-1HZC | CP | 4 | HORIZONTAL | 1700 | CONSTANT AIRFLOW ECM | 0.75 | 49500 | 16 | 86 | 80.6/66.2 | 58000 | 5.6 | 68 | 68 | 12 | 9 | 208-230/1 | 31.3 | 45 | 319 | 4 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP048-3HZC | CP | 4 | HORIZONTAL | 1700 | CONSTANT AIRFLOW ECM | 0.75 | 49500 | 16 | 86 | 80.6/66.2 | 58000 | 5.6 | 68 | 68 | 12 | 9 | 208-230/3 | 23.3 | 35 | 319 | 4 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP048-4HZC | CP | 4 | HORIZONTAL | 1700 | CONSTANT AIRFLOW ECM | 0.75 | 49500 | 16 | 86 | 80.6/66.2 | 58000 | 5.6 | 68 | 68 | 12 | 9 | 460/3 | 16.2 | 20 | 319 | 4 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 0.75
BOSCH | CP060-1VTC | CP | 5 | VERTICAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 61500 | 16 | 86 | 80.6/66.2 | 75000 | 5.6 | 68 | 68 | 15 | 8.1 | 208-230/1 | 40.6 | 60 | 397 | 5 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP060-3VTC | CP | 5 | VERTICAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 61500 | 16 | 86 | 80.6/66.2 | 75000 | 5.6 | 68 | 68 | 15 | 8.1 | 208-230/3 | 26.3 | 40 | 397 | 5 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP060-4VTC | CP | 5 | VERTICAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 61500 | 16 | 86 | 80.6/66.2 | 75000 | 5.6 | 68 | 68 | 15 | 8.1 | 460/3 | 18.2 | 25 | 397 | 5 | CP - COMMERCIAL PREMIUM | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP060-1HZC | CP | 5 | HORIZONTAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 61500 | 16 | 86 | 80.6/66.2 | 75000 | 5.6 | 68 | 68 | 15 | 8.1 | 208-230/1 | 40.6 | 60 | 366 | 5 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP060-3HZC | CP | 5 | HORIZONTAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 61500 | 16 | 86 | 80.6/66.2 | 75000 | 5.6 | 68 | 68 | 15 | 8.1 | 208-230/3 | 26.3 | 40 | 366 | 5 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP060-4HZC | CP | 5 | HORIZONTAL | 2000 | CONSTANT AIRFLOW ECM | 1 | 61500 | 16 | 86 | 80.6/66.2 | 75000 | 5.6 | 68 | 68 | 15 | 8.1 | 460/3 | 18.2 | 25 | 366 | 5 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP070-1VTC | CP | 6 | VERTICAL | 2150 | CONSTANT AIRFLOW ECM | 1 | 68000 | 15 | 86 | 80.6/66.2 | 86000 | 5.1 | 68 | 68 | 18 | 11.1 | 208-230/1 | 44.1 | 70 | 401 | 6 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP070-3VTC | CP | 6 | VERTICAL | 2150 | CONSTANT AIRFLOW ECM | 1 | 68000 | 15 | 86 | 80.6/66.2 | 86000 | 5.1 | 68 | 68 | 18 | 11.1 | 208-230/3 | 32.7 | 50 | 401 | 6 | CP - COMMERCIAL PREMIUM | VERTICAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP070-4VTC | CP | 6 | VERTICAL | 2150 | CONSTANT AIRFLOW ECM | 1 | 68000 | 15 | 86 | 80.6/66.2 | 86000 | 5.1 | 68 | 68 | 18 | 11.1 | 460/3 | 20.5 | 25 | 401 | 6 | CP - COMMERCIAL PREMIUM | VERTICAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP070-1HZC | CP | 6 | HORIZONTAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 68000 | 15 | 86 | 80.6/66.2 | 86000 | 5.1 | 68 | 68 | 18 | 11.1 | 208-230/1 | 44.1 | 70 | 414 | 6 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/1 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP070-3HZC | CP | 6 | HORIZONTAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 68000 | 15 | 86 | 80.6/66.2 | 86000 | 5.1 | 68 | 68 | 18 | 11.1 | 208-230/3 | 32.7 | 50 | 414 | 6 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 208-230/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | CP070-4HZC | CP | 6 | HORIZONTAL | 2100 | CONSTANT AIRFLOW ECM | 1 | 68000 | 15 | 86 | 80.6/66.2 | 86000 | 5.1 | 68 | 68 | 18 | 11.1 | 460/3 | 20.5 | 25 | 414 | 6 | CP - COMMERCIAL PREMIUM | HORIZONTAL | 460/3 | CONSTANT AIRFLOW ECM | 1
BOSCH | EC072-1VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 1 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/1 | 44.6 | 60 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/1 | BELT DRIVE | 1
BOSCH | EC072-1VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 1.5 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/1 | 46.1 | 60 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/1 | BELT DRIVE | 1.5
BOSCH | EC072-1VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 2 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/1 | 47.4 | 60 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/1 | BELT DRIVE | 2
BOSCH | EC072-3VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 1 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/3 | 31.1 | 40 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 1
BOSCH | EC072-3VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 1.5 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/3 | 32.3 | 40 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 1.5
BOSCH | EC072-3VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 2 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/3 | 33.7 | 45 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC072-3VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 3 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/3 | 35.5 | 45 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC072-4VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 1 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 460/3 | 14.9 | 20 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 1
BOSCH | EC072-4VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 1.5 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 460/3 | 15.5 | 20 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 1.5
BOSCH | EC072-4VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 2 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 460/3 | 16.2 | 20 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 2
BOSCH | EC072-4VTC | EC | 6 | VERTICAL | 2400 | BELT DRIVE | 3 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 460/3 | 17 | 20 | 670 | 6 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 3
BOSCH | EC072-1HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 1 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/1 | 44.6 | 60 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/1 | BELT DRIVE | 1
BOSCH | EC072-1HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 1.5 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/1 | 46.1 | 60 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/1 | BELT DRIVE | 1.5
BOSCH | EC072-1HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 2 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/1 | 47.4 | 60 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/1 | BELT DRIVE | 2
BOSCH | EC072-3HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 1 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/3 | 31.1 | 40 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 1
BOSCH | EC072-3HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 1.5 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/3 | 32.3 | 40 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 1.5
BOSCH | EC072-3HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 2 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/3 | 33.7 | 45 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC072-3HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 3 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 208-230/3 | 35.5 | 45 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC072-4HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 1 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 460/3 | 14.9 | 20 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 1
BOSCH | EC072-4HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 1.5 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 460/3 | 15.5 | 20 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 1.5
BOSCH | EC072-4HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 2 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 460/3 | 16.2 | 20 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 2
BOSCH | EC072-4HZC | EC | 6 | HORIZONTAL | 2400 | BELT DRIVE | 3 | 77500 | 16.25 | 86 | 80.6/66.2 | 86500 | 5.35 | 68 | 68 | 18 | 17.3 | 460/3 | 17 | 20 | 670 | 6 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 3
BOSCH | EC096-1VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 1.5 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/1 | 58.9 | 80 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/1 | BELT DRIVE | 1.5
BOSCH | EC096-1VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 2 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/1 | 60.2 | 80 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/1 | BELT DRIVE | 2
BOSCH | EC096-3VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 1.5 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/3 | 33.6 | 45 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 1.5
BOSCH | EC096-3VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 2 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/3 | 35 | 45 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC096-3VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 3 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/3 | 36.8 | 45 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC096-4VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 1.5 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 460/3 | 15.9 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 1.5
BOSCH | EC096-4VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 2 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 460/3 | 16.6 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 2
BOSCH | EC096-4VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 3 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 460/3 | 17.4 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 3
BOSCH | EC096-5VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 1.5 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 575/3 | 14.8 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 1.5
BOSCH | EC096-5VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 2 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 575/3 | 15.4 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 2
BOSCH | EC096-5VTC | EC | 8 | VERTICAL | 2820 | BELT DRIVE | 3 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 575/3 | 16.5 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 3
BOSCH | EC096-1HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 1.5 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/1 | 58.9 | 80 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/1 | BELT DRIVE | 1.5
BOSCH | EC096-1HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 2 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/1 | 60.2 | 80 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/1 | BELT DRIVE | 2
BOSCH | EC096-3HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 1.5 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/3 | 33.6 | 45 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 1.5
BOSCH | EC096-3HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 2 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/3 | 35 | 45 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC096-3HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 3 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 208-230/3 | 36.8 | 45 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC096-4HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 1.5 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 460/3 | 15.9 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 1.5
BOSCH | EC096-4HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 2 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 460/3 | 16.6 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 2
BOSCH | EC096-4HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 3 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 460/3 | 17.4 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 3
BOSCH | EC096-5HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 1.5 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 575/3 | 14.8 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 1.5
BOSCH | EC096-5HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 2 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 575/3 | 15.4 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 2
BOSCH | EC096-5HZC | EC | 8 | HORIZONTAL | 2820 | BELT DRIVE | 3 | 101300 | 16.5 | 86 | 80.6/66.2 | 126200 | 5.25 | 68 | 68 | 21 | 15.6 | 575/3 | 16.5 | 20 | 702 | 8 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 3
BOSCH | EC120-1VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 2 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 208-230/1 | 67.4 | 90 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/1 | BELT DRIVE | 2
BOSCH | EC120-3VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 2 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 208-230/3 | 48.1 | 60 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC120-3VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 3 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 208-230/3 | 49.9 | 60 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC120-3VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 5 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 208-230/3 | 55.3 | 70 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC120-4VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 2 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 460/3 | 21.8 | 30 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 2
BOSCH | EC120-4VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 3 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 460/3 | 22.6 | 30 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 3
BOSCH | EC120-4VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 5 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 460/3 | 25.3 | 30 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 5
BOSCH | EC120-5VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 2 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 575/3 | 19.9 | 25 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 2
BOSCH | EC120-5VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 3 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 575/3 | 21 | 25 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 3
BOSCH | EC120-5VTC | EC | 10 | VERTICAL | 4000 | BELT DRIVE | 5 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 575/3 | 22.7 | 30 | 935 | 10 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 5
BOSCH | EC120-3HZC | EC | 10 | HORIZONTAL | 4000 | BELT DRIVE | 3 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 208-230/3 | 49.9 | 60 | 935 | 10 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC120-3HZC | EC | 10 | HORIZONTAL | 4000 | BELT DRIVE | 5 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 208-230/3 | 55.3 | 70 | 935 | 10 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC120-4HZC | EC | 10 | HORIZONTAL | 4000 | BELT DRIVE | 3 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 460/3 | 22.6 | 30 | 935 | 10 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 3
BOSCH | EC120-4HZC | EC | 10 | HORIZONTAL | 4000 | BELT DRIVE | 5 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 460/3 | 25.3 | 30 | 935 | 10 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 5
BOSCH | EC120-5HZC | EC | 10 | HORIZONTAL | 4000 | BELT DRIVE | 3 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 575/3 | 21 | 25 | 935 | 10 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 3
BOSCH | EC120-5HZC | EC | 10 | HORIZONTAL | 4000 | BELT DRIVE | 5 | 125700 | 13.4 | 86 | 80.6/66.2 | 157600 | 4.4 | 68 | 68 | 28 | 13.3 | 575/3 | 22.7 | 30 | 935 | 10 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 5
BOSCH | EC150-3HZC | EC | 12.5 | HORIZONTAL | 5000 | BELT DRIVE | 3 | 148800 | 17.7 | 86 | 80.6/66.2 | 167600 | 6 | 68 | 68 | 35 | 9 | 208-230/3 | 52.4 | 70 | 1060 | 12.5 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC150-3HZC | EC | 12.5 | HORIZONTAL | 5000 | BELT DRIVE | 5 | 148800 | 17.7 | 86 | 80.6/66.2 | 167600 | 6 | 68 | 68 | 35 | 9 | 208-230/3 | 56.6 | 70 | 1060 | 12.5 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC150-4HZC | EC | 12.5 | HORIZONTAL | 5000 | BELT DRIVE | 3 | 148800 | 17.7 | 86 | 80.6/66.2 | 167600 | 6 | 68 | 68 | 35 | 9 | 460/3 | 24.6 | 30 | 1060 | 12.5 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 3
BOSCH | EC150-4HZC | EC | 12.5 | HORIZONTAL | 5000 | BELT DRIVE | 5 | 148800 | 17.7 | 86 | 80.6/66.2 | 167600 | 6 | 68 | 68 | 35 | 9 | 460/3 | 26.9 | 35 | 1060 | 12.5 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 5
BOSCH | EC150-5HZC | EC | 12.5 | HORIZONTAL | 5000 | BELT DRIVE | 3 | 148800 | 17.7 | 86 | 80.6/66.2 | 167600 | 6 | 68 | 68 | 35 | 9 | 575/3 | 21 | 25 | 1060 | 12.5 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 3
BOSCH | EC150-5HZC | EC | 12.5 | HORIZONTAL | 5000 | BELT DRIVE | 5 | 148800 | 17.7 | 86 | 80.6/66.2 | 167600 | 6 | 68 | 68 | 35 | 9 | 575/3 | 22.7 | 30 | 1060 | 12.5 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 5
BOSCH | EC151-3VTC | EC | 12.5 | VERTICAL | 5000 | BELT DRIVE | 3 | 148900 | 17.75 | 86 | 80.6/66.2 | 163000 | 5.3 | 68 | 68 | 35 | 9 | 208-230/3 | 51.2 | 70 | 1050 | 12.5 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC151-3VTC | EC | 12.5 | VERTICAL | 5000 | BELT DRIVE | 5 | 148900 | 17.75 | 86 | 80.6/66.2 | 163000 | 5.3 | 68 | 68 | 35 | 9 | 208-230/3 | 56.6 | 70 | 1050 | 12.5 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC151-4VTC | EC | 12.5 | VERTICAL | 5000 | BELT DRIVE | 3 | 148900 | 17.75 | 86 | 80.6/66.2 | 163000 | 5.3 | 68 | 68 | 35 | 9 | 460/3 | 24.2 | 30 | 1050 | 12.5 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 3
BOSCH | EC151-4VTC | EC | 12.5 | VERTICAL | 5000 | BELT DRIVE | 5 | 148900 | 17.75 | 86 | 80.6/66.2 | 163000 | 5.3 | 68 | 68 | 35 | 9 | 460/3 | 26.9 | 35 | 1050 | 12.5 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 5
BOSCH | EC151-5VTC | EC | 12.5 | VERTICAL | 5000 | BELT DRIVE | 3 | 148900 | 17.75 | 86 | 80.6/66.2 | 163000 | 5.3 | 68 | 68 | 35 | 9 | 575/3 | 21 | 25 | 1050 | 12.5 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 3
BOSCH | EC151-5VTC | EC | 12.5 | VERTICAL | 5000 | BELT DRIVE | 5 | 148900 | 17.75 | 86 | 80.6/66.2 | 163000 | 5.3 | 68 | 68 | 35 | 9 | 575/3 | 22.7 | 30 | 1050 | 12.5 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 5
BOSCH | EC180-3HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 2 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 208-230/3 | 62.6 | 80 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC180-3HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 3 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 208-230/3 | 66.2 | 80 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC180-3HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 5 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 208-230/3 | 77 | 90 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC180-4HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 2 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 460/3 | 26 | 30 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 2
BOSCH | EC180-4HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 3 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 460/3 | 27.6 | 35 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 3
BOSCH | EC180-4HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 5 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 460/3 | 33 | 40 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 5
BOSCH | EC180-5HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 2 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 575/3 | 21.2 | 25 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 2
BOSCH | EC180-5HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 3 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 575/3 | 23.4 | 30 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 3
BOSCH | EC180-5HZC | EC | 15 | HORIZONTAL | 6000 | BELT DRIVE | 5 | 173100 | 16.35 | 86 | 80.6/66.2 | 182300 | 5.55 | 68 | 68 | 42 | 12.5 | 575/3 | 26.8 | 30 | 1530 | 15 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 5
BOSCH | EC181-3VTC | EC | 15 | VERTICAL | 6000 | BELT DRIVE | 5 | 170700 | 14 | 86 | 80.6/66.2 | 180500 | 4.9 | 68 | 68 | 42 | 12.5 | 208-230/3 | 63.6 | 80 | 1090 | 15 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC181-4VTC | EC | 15 | VERTICAL | 6000 | BELT DRIVE | 5 | 170700 | 14 | 86 | 80.6/66.2 | 180500 | 4.9 | 68 | 68 | 42 | 12.5 | 460/3 | 26.4 | 35 | 1090 | 15 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 5
BOSCH | EC181-5VTC | EC | 15 | VERTICAL | 6000 | BELT DRIVE | 5 | 170700 | 14 | 86 | 80.6/66.2 | 180500 | 4.9 | 68 | 68 | 42 | 12.5 | 575/3 | 21.4 | 25 | 1090 | 15 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 5
BOSCH | EC210-3VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 1.5 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 208-230/3 | 74 | 100 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 1.5
BOSCH | EC210-3VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 2 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 208-230/3 | 76.8 | 100 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC210-3VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 3 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 208-230/3 | 80.4 | 100 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC210-3VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 5 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 208-230/3 | 91.2 | 110 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC210-4VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 1.5 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 460/3 | 32.7 | 45 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 1.5
BOSCH | EC210-4VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 2 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 460/3 | 34.1 | 45 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 2
BOSCH | EC210-4VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 3 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 460/3 | 35.7 | 45 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 3
BOSCH | EC210-4VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 5 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 460/3 | 41.1 | 50 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 5
BOSCH | EC210-5VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 1.5 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 575/3 | 24 | 30 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 1.5
BOSCH | EC210-5VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 2 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 575/3 | 25.2 | 30 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 2
BOSCH | EC210-5VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 3 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 575/3 | 27.4 | 35 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 3
BOSCH | EC210-5VTC | EC | 17.5 | VERTICAL | 7000 | BELT DRIVE | 5 | 214800 | 15.05 | 86 | 80.6/66.2 | 257200 | 5.05 | 68 | 68 | 50 | 14.9 | 575/3 | 30.8 | 35 | 1090 | 17.5 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 5
BOSCH | EC240-3VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 2 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 208-230/3 | 76.5 | 100 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC240-3VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 3 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 208-230/3 | 80.1 | 100 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC240-3VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 5 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 208-230/3 | 90.9 | 110 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC240-4VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 2 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 460/3 | 36.4 | 45 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 2
BOSCH | EC240-4VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 3 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 460/3 | 38 | 50 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 3
BOSCH | EC240-4VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 5 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 460/3 | 43.4 | 50 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 5
BOSCH | EC240-5VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 2 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 575/3 | 29.3 | 35 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 2
BOSCH | EC240-5VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 3 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 575/3 | 31.5 | 40 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 3
BOSCH | EC240-5VTC | EC | 20 | VERTICAL | 8000 | BELT DRIVE | 5 | 248800 | 15.6 | 86 | 80.6/66.2 | 323600 | 4.9 | 68 | 68 | 60 | 12.9 | 575/3 | 34.9 | 45 | 1310 | 20 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 5
BOSCH | EC242-3HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 2 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 208-230/3 | 71.9 | 100 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 2
BOSCH | EC242-3HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 3 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 208-230/3 | 80.1 | 100 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC242-3HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 5 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 208-230/3 | 90.9 | 110 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC242-4HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 2 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 460/3 | 36.4 | 45 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 2
BOSCH | EC242-4HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 3 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 460/3 | 38 | 50 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 3
BOSCH | EC242-4HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 5 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 460/3 | 43.4 | 50 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 460/3 | BELT DRIVE | 5
BOSCH | EC242-5HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 2 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 575/3 | 29.3 | 35 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 2
BOSCH | EC242-5HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 3 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 575/3 | 31.5 | 40 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 3
BOSCH | EC242-5HZC | EC | 20 | HORIZONTAL | 8000 | BELT DRIVE | 5 | 237100 | 13.9 | 86 | 80.6/66.2 | 304600 | 4.6 | 68 | 68 | 60 | 12.9 | 575/3 | 34.9 | 45 | 1655 | 20 | EC - LARGE COMMERCIAL | HORIZONTAL | 575/3 | BELT DRIVE | 5
BOSCH | EC300-3VTC | EC | 25 | VERTICAL | 10000 | BELT DRIVE | 3 | 310900 | 14.6 | 86 | 80.6/66.2 | 403300 | 4.45 | 68 | 68 | 75 | 19.2 | 208-230/3 | 107.6 | 125 | 1530 | 25 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 3
BOSCH | EC300-3VTC | EC | 25 | VERTICAL | 10000 | BELT DRIVE | 5 | 310900 | 14.6 | 86 | 80.6/66.2 | 403300 | 4.45 | 68 | 68 | 75 | 19.2 | 208-230/3 | 118.4 | 150 | 1530 | 25 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC300-4VTC | EC | 25 | VERTICAL | 10000 | BELT DRIVE | 3 | 310900 | 14.6 | 86 | 80.6/66.2 | 403300 | 4.45 | 68 | 68 | 75 | 19.2 | 460/3 | 51.5 | 70 | 1530 | 25 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 3
BOSCH | EC300-4VTC | EC | 25 | VERTICAL | 10000 | BELT DRIVE | 5 | 310900 | 14.6 | 86 | 80.6/66.2 | 403300 | 4.45 | 68 | 68 | 75 | 19.2 | 460/3 | 56.9 | 70 | 1530 | 25 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 5
BOSCH | EC300-5VTC | EC | 25 | VERTICAL | 10000 | BELT DRIVE | 3 | 310900 | 14.6 | 86 | 80.6/66.2 | 403300 | 4.45 | 68 | 68 | 75 | 19.2 | 575/3 | 38.2 | 50 | 1530 | 25 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 3
BOSCH | EC300-5VTC | EC | 25 | VERTICAL | 10000 | BELT DRIVE | 5 | 310900 | 14.6 | 86 | 80.6/66.2 | 403300 | 4.45 | 68 | 68 | 75 | 19.2 | 575/3 | 41.6 | 50 | 1530 | 25 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 5
BOSCH | EC360-3VTC | EC | 30 | VERTICAL | 12000 | BELT DRIVE | 5 | 386000 | 13.3 | 86 | 80.6/66.2 | 458900 | 4.2 | 68 | 68 | 90 | 24.4 | 208-230/3 | 136.8 | 175 | 1650 | 30 | EC - LARGE COMMERCIAL | VERTICAL | 208-230/3 | BELT DRIVE | 5
BOSCH | EC360-4VTC | EC | 30 | VERTICAL | 12000 | BELT DRIVE | 5 | 386000 | 13.3 | 86 | 80.6/66.2 | 458900 | 4.2 | 68 | 68 | 90 | 24.4 | 460/3 | 67 | 90 | 1650 | 30 | EC - LARGE COMMERCIAL | VERTICAL | 460/3 | BELT DRIVE | 5
BOSCH | EC360-5VTC | EC | 30 | VERTICAL | 12000 | BELT DRIVE | 5 | 386000 | 13.3 | 86 | 80.6/66.2 | 458900 | 4.2 | 68 | 68 | 90 | 24.4 | 575/3 | 54 | 70 | 1650 | 30 | EC - LARGE COMMERCIAL | VERTICAL | 575/3 | BELT DRIVE | 5

## SCHEDULE NOTES
Performance at AHRI/ISO 13256-1 water loop heat pump conditions: cooling 86°F EWT, 80.6°F DB / 66.2°F WB EAT; heating 68°F EWT, 68°F EAT.
Provide with copper coaxial water-to-refrigerant coil.
Provide with constant airflow ECM blower motor (1.25 - 6 ton).
Provide with constant torque ECM blower motor (0.5 - 1 ton).
Provide with MERV 8, 2" 4-sided filter rack (CL / CF / CP).
Provide with factory DDC controller, multi-protocol (BACnet, Modbus, N2), for building automation system integration.

## SOURCES
Source documents (Bosch engineering submittal sheets, Sept 2026)
CL: btc771008301d_bosch_cl_ess_09.2026.pdf · CF: btc771408301e_bosch_cf_ess_09.2026.pdf · CP: btc771608301c_bosch_cp_ess_09.2026.pdf · EC: btc771008301h_bosch_ec_r454b_ess_09.2026.pdf
Scope: water-loop ratings only; copper coax; constant airflow ECM on CL/CF/CP 015-070 and constant torque ECM on CL/CF 007-012 (the 0.5 - 1 ton sizes do not offer the constant airflow ECM); standard belt drive on EC (one row per motor HP); two-stage units (CF, CP) at full load.
Model number = the configuration part of the Bosch model string (series, size, voltage code, cabinet, copper coax), e.g. CL024-1VTC. The remaining characters (water connections, return/discharge, filters, controls, options) are chosen at order entry.
CFM, GPM, cooling capacity/EER, heating capacity/COP: AHRI Ratings (13256-1), copper water coil, ECM (CL p.4, CF p.3, CP p.3) or belt drive (EC p.3), water loop columns.
MCA / MOCP / motor HP: Electrical Data - Constant Airflow ECM, single point power (CL p.15, CF p.16, CP p.13); 007-012: Electrical Data - Constant Torque ECM (CL p.14, CF p.15); EC Electrical Data - Belt Drive Motor (pp.14-15), max fuse. Cabinet-specific rows used where printed.
Weight: Physical Data, operating weight for the cabinet (CL pp.24-25, CF pp.25-26, CP p.20, EC pp.22-23). A cabinet printed "-" is not built in that size and has no rows.
WPD: Waterside Pressure Drop without internal valve (CL p.12, CF p.14, CP p.11 in PSI x 2.31 = ft; EC p.13 in ft). 248 rows use a printed flow; 69 rows are interpolated (log-log) between the two printed flows that bracket the rated GPM.
VOLT/PH follows the model voltage code. Catalog notes: the nomenclature lists code 2 as 277/60/1 but every electrical table rates it 265/1/60 (scheduled as 265/1); EC120 code 3 is printed 200-230/3/60 (scheduled as 208-230/3).
CL ECM ratings print identical to the CL PSC ratings in the catalog.