## SCHEDULE
SCHEDULE RANGE | [29 empty] | FILTERS | [7 empty] | DOCUMENTATION
PACKAGED HEAT PUMPS | [29 empty] | SIZE | ELECTRICAL | EFFICIENCY | SERIES | ELECTRIC HEAT | HGRH | BLOWER | COOLING STAGES | SUBMITTAL | ENGINEERING MANUAL
MAKE | MODEL NUMBER | NOM TONS | Fan Data |  |  |  | Cooling Performance | [7 empty] | Heat Pump Heating | [5 empty] | Electric Heat |  |  | MODULATING HOT GAS REHEAT | COOLING STAGES | Electrical Data |  |  | Weight (lbs)
|  |  | CFM | BLOWER | ESP (IWG) | INDOOR MOTOR HP | TOTAL CAPACITY (BTU/h) | SENSIBLE CAPACITY (BTU/h) | EFFICIENCY (AT AHRI) | EDB (°F) | EWB (°F) | LDB (°F) | LWB (°F) | AMBIENT (°F) | CAPACITY @ 47°F (BTU/h) | COP @ 47°F | CAPACITY @ 17°F (BTU/h) | COP @ 17°F | EAT (°F) | LAT @ 47°F (°F) | KW | STAGES | HEATER KIT |  |  | VOLT/PH | Unit MCA | Unit MOCP
TEMPMASTER | WQE04A1A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 208/1 | 29.5 | 45 | 529 | 3 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A1A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 63.1 | 70 | 529 | 3 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A1A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 84 | 90 | 529 | 3 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A1B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 1.5 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 208/1 | 30.5 | 45 | 529 | 3 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A1B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 1.5 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 64.1 | 70 | 529 | 3 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A1B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 1.5 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 85 | 90 | 529 | 3 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 208/3 | 23.9 | 35 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 43.1 | 50 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 55.2 | 60 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 71.7 | 80 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 208/3 | 22.8 | 30 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 42.3 | 50 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 54.4 | 60 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 70.9 | 80 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 208/3 | 22.8 | 30 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 42.3 | 50 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 54.4 | 60 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A2C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 70.9 | 80 | 529 | 3 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 460/3 | 11.8 | 15 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.8 | 25 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 29.1 | 30 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.8 | 35 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 460/3 | 11.2 | 15 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.2 | 25 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 28.5 | 30 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.2 | 35 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 460/3 | 11.2 | 15 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.2 | 25 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 28.5 | 30 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A4C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.2 | 35 | 529 | 3 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 575/3 | 9 | 15 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 20.1 | 25 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 9.2 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 25.6 | 30 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 575/3 | 8.6 | 15 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 19.7 | 20 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 9.2 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 25.2 | 30 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | - | - | - | NO | 1 | 575/3 | 8.6 | 15 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 19.7 | 20 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 9.2 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE04A5C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37800 | 28000 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.4 | 57 | 95 | 34500 | 3.5 | 19500 | 2.1 | 70 | 96.6 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 25.2 | 30 | 529 | 3 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A1A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 208/1 | 29.5 | 45 | 535 | 3 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A1A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 63.1 | 70 | 535 | 3 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A1A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 84 | 90 | 535 | 3 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A1B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 1.5 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 208/1 | 30.5 | 45 | 535 | 3 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A1B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 1.5 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 64.1 | 70 | 535 | 3 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A1B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 1.5 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 85 | 90 | 535 | 3 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 208/3 | 23.9 | 35 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 43.1 | 50 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 55.2 | 60 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 71.7 | 80 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 208/3 | 22.8 | 30 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 42.3 | 50 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 54.4 | 60 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 70.9 | 80 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 208/3 | 22.8 | 30 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 42.3 | 50 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 54.4 | 60 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A2C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 70.9 | 80 | 535 | 3 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 460/3 | 11.8 | 15 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.8 | 25 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 29.1 | 30 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.8 | 35 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 460/3 | 11.2 | 15 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.2 | 25 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 28.5 | 30 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.2 | 35 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 460/3 | 11.2 | 15 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.2 | 25 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 28.5 | 30 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A4C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.2 | 35 | 535 | 3 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 575/3 | 9 | 15 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 20.1 | 25 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 9.2 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5A1AA5A111A1 | 3 | 1200 | STANDARD STATIC | - | 0.75 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 25.6 | 30 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 575/3 | 8.6 | 15 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 19.7 | 20 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 9.2 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5B1AA5A111A1 | 3 | 1200 | MEDIUM STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 25.2 | 30 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | - | - | - | NO | 1 | 575/3 | 8.6 | 15 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 19.7 | 20 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 9.2 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE04A5C1AA5A111A1 | 3 | 1200 | HIGH STATIC | - | 2.4 | 37200 | 27200 | 14.5 SEER2/12.2 EER2/7.1 HSPF2 | 80 | 67 | 59 | 57.2 | 95 | 35000 | 3.5 | 20000 | 2.2 | 70 | 97 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 25.2 | 30 | 535 | 3 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A1A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 208/1 | 34.7 | 50 | 554 | 4 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A1A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 68.1 | 80 | 554 | 4 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A1A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 89 | 90 | 554 | 4 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A1B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 1.5 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 208/1 | 33.9 | 50 | 554 | 4 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A1B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 1.5 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 67.5 | 80 | 554 | 4 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A1B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 1.5 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 88.4 | 90 | 554 | 4 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 208/3 | 25.4 | 35 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 44.4 | 50 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 56.5 | 60 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 73 | 80 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 208/3 | 22.5 | 30 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 42 | 50 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 54.1 | 60 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 70.6 | 80 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 208/3 | 22.5 | 30 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 42 | 50 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 54.1 | 60 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A2C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 70.6 | 80 | 554 | 4 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 460/3 | 13.2 | 15 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 22.2 | 25 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 30.5 | 35 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 34.2 | 35 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 460/3 | 11.8 | 15 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.8 | 25 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 29.1 | 30 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.8 | 35 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 460/3 | 11.8 | 15 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.8 | 25 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 29.1 | 30 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A4C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.8 | 35 | 554 | 4 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 575/3 | 9.5 | 15 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 20.6 | 25 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 9.2 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 26.1 | 30 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 575/3 | 8.5 | 15 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 19.6 | 20 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 9.2 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 25.1 | 30 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | - | - | - | NO | 1 | 575/3 | 8.5 | 15 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 19.6 | 20 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 9.2 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE05A5C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 52100 | 37700 | 14.0 SEER2/12.2 EER2/6.7 HSPF2 | 80 | 67 | 58.2 | 56.7 | 95 | 45600 | 3.5 | 24600 | 2.15 | 70 | 96.4 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 25.1 | 30 | 554 | 4 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A1A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 208/1 | 38.4 | 60 | 614 | 4 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A1A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 71.8 | 80 | 614 | 4 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A1A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 92.7 | 100 | 614 | 4 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A1B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 1.5 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 208/1 | 37.6 | 60 | 614 | 4 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A1B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 1.5 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 71.2 | 80 | 614 | 4 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A1B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 1.5 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 92.1 | 100 | 614 | 4 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 208/3 | 26.4 | 35 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 45.4 | 50 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 57.5 | 60 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 74 | 80 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 208/3 | 23.5 | 35 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 43 | 50 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 55.1 | 60 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 71.6 | 80 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 208/3 | 23.5 | 35 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 43 | 50 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 55.1 | 60 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A2C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 71.6 | 80 | 614 | 4 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 460/3 | 12.8 | 15 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 21.8 | 25 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 30.1 | 35 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 33.8 | 35 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 460/3 | 11.4 | 15 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.4 | 25 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 28.7 | 30 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.4 | 35 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 460/3 | 11.4 | 15 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 20.4 | 25 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 28.7 | 30 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A4C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 32.4 | 35 | 614 | 4 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 575/3 | 11.3 | 15 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 22.4 | 25 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 9.2 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5A1AA5A111A1 | 4 | 1600 | STANDARD STATIC | - | 1 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 27.9 | 30 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 575/3 | 10.3 | 15 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 21.4 | 25 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 9.2 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5B1AA5A111A1 | 4 | 1600 | MEDIUM STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 26.9 | 30 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | - | - | - | NO | 1 | 575/3 | 10.3 | 15 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 9.2 | 1 | 2EK04511058 | NO | 1 | 575/3 | 21.4 | 25 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 9.2 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE05A5C1AA5A111A1 | 4 | 1600 | HIGH STATIC | - | 2.4 | 51400 | 37800 | 14.4 SEER2/12.2 EER2/7.3 HSPF2 | 80 | 67 | 58.1 | 56.8 | 95 | 46000 | 3.5 | 26000 | 2.25 | 70 | 96.6 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 26.9 | 30 | 614 | 4 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A1A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 208/1 | 38.5 | 60 | 627 | 5 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A1A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 71.9 | 80 | 627 | 5 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A1A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 92.8 | 100 | 627 | 5 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A1B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 1.5 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 208/1 | 36.9 | 50 | 627 | 5 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A1B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 1.5 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 70.5 | 80 | 627 | 5 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A1B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 1.5 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 91.4 | 100 | 627 | 5 | 208/1 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 208/3 | 26.8 | 35 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 45.8 | 50 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 57.9 | 60 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 74.4 | 80 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 208/3 | 25.9 | 35 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 45.4 | 50 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 57.5 | 60 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 74 | 80 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 208/3 | 27.3 | 40 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 46.4 | 50 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 58.5 | 60 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 10.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A2C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 75 | 80 | 627 | 5 | 208/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 16 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 460/3 | 13.6 | 20 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 22.6 | 25 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 30.9 | 35 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 34.6 | 35 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 460/3 | 13.2 | 15 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 22.2 | 25 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 30.5 | 35 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 34.2 | 35 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 460/3 | 13.7 | 20 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 22.7 | 25 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 6 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 31 | 35 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 11.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A4C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 34.7 | 35 | 627 | 5 | 460/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 14 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 575/3 | 10 | 15 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 26.6 | 30 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 23 | 1 | 2EK04512358 | NO | 1 | 575/3 | 37.6 | 40 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 23 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 575/3 | 9.5 | 15 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 26.1 | 30 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 23 | 1 | 2EK04512358 | NO | 1 | 575/3 | 37.1 | 40 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 23 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | - | - | - | NO | 1 | 575/3 | 10.2 | 15 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 26.8 | 30 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 13.8 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WQE06A5C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 62500 | 45700 | 14.0 SEER2/11.8 EER2/6.7 HSPF2 | 80 | 67 | 58.8 | 57.1 | 95 | 53000 | 3.5 | 29000 | 2.15 | 70 | 94.5 | 23 | 1 | 2EK04512358 | NO | 1 | 575/3 | 37.8 | 40 | 627 | 5 | 575/3 | STANDARD | WQ - OMNI CORE STANDARD EFF | 23 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A1A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 208/1 | 40 | 60 | 653 | 5 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A1A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 73.4 | 90 | 653 | 5 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A1A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 94.3 | 100 | 653 | 5 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A1B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 1.5 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 208/1 | 38.4 | 60 | 653 | 5 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A1B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 1.5 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/1 | 72 | 80 | 653 | 5 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A1B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 1.5 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/1 | 92.9 | 100 | 653 | 5 | 208/1 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 208/3 | 30.4 | 45 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 49.4 | 60 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 61.5 | 70 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 78 | 80 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 208/3 | 29.5 | 45 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 49 | 60 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 61.1 | 70 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 77.6 | 80 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 208/3 | 30.9 | 45 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 6.5 | 1 | 2EK04510625 | NO | 1 | 208/3 | 50 | 60 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 10.5 | 1 | 2EK04511125 | NO | 1 | 208/3 | 62.1 | 70 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 10.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A2C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 16 | 1 | 2EK04511625 | NO | 1 | 208/3 | 78.6 | 80 | 653 | 5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 460/3 | 14.2 | 20 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 23.2 | 25 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 31.5 | 35 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 35.2 | 40 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 460/3 | 13.8 | 20 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 22.8 | 25 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 31.1 | 35 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 34.8 | 35 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 460/3 | 14.3 | 20 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 6 | 1 | 2EK04510646 | NO | 1 | 460/3 | 23.3 | 25 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 11.5 | 1 | 2EK04511146 | NO | 1 | 460/3 | 31.6 | 35 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 11.5 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A4C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 14 | 1 | 2EK04511446 | NO | 1 | 460/3 | 35.3 | 40 | 653 | 5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 14 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 575/3 | 12 | 15 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 28.6 | 30 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5A1AA5A111A1 | 5 | 2000 | STANDARD STATIC | - | 1 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 23 | 1 | 2EK04512358 | NO | 1 | 575/3 | 39.6 | 40 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 23 | NO | STANDARD STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 575/3 | 11.5 | 15 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 28.1 | 30 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5B1AA5A111A1 | 5 | 2000 | MEDIUM STATIC | - | 2.4 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 23 | 1 | 2EK04512358 | NO | 1 | 575/3 | 39.1 | 40 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 23 | NO | MEDIUM STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | - | - | - | NO | 1 | 575/3 | 12.2 | 15 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 13.8 | 1 | 2EK04511458 | NO | 1 | 575/3 | 28.8 | 30 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 13.8 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE06A5C1AA5A111A1 | 5 | 2000 | HIGH STATIC | - | 2.9 | 66500 | 47100 | 14.3 SEER2/12.0 EER2/6.9 HSPF2 | 80 | 67 | 58.2 | 56.4 | 95 | 56000 | 3.6 | 30000 | 2.2 | 70 | 95.9 | 23 | 1 | 2EK04512358 | NO | 1 | 575/3 | 39.8 | 40 | 653 | 5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 23 | NO | HIGH STATIC | 1 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 208/3 | 37.4 | 50 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 6.5 | 1 | 2EK04510725 | NO | 2 | 208/3 | 56.9 | 70 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 85.5 | 90 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 112 | 125 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 25 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 208/3 | 41.6 | 60 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 6.5 | 1 | 2EK04510725 | NO | 2 | 208/3 | 61.1 | 70 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 89.7 | 90 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 116.2 | 125 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 25 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 208/3 | 41.6 | 60 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 6.5 | 1 | 2EK04510725 | NO | 2 | 208/3 | 61.1 | 70 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 6.5 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 89.7 | 90 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A2C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 116.2 | 125 | 895 | 6 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 25 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 460/3 | 21 | 30 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 6 | 1 | 2EK04510746 | NO | 2 | 460/3 | 30 | 35 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 45.8 | 50 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 26 | 1 | 2EK04512646 | NO | 2 | 460/3 | 59.4 | 60 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 26 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 460/3 | 22.5 | 30 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 6 | 1 | 2EK04510746 | NO | 2 | 460/3 | 31.5 | 35 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 47.3 | 50 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 26 | 1 | 2EK04512646 | NO | 2 | 460/3 | 60.9 | 70 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 26 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 460/3 | 22.5 | 30 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 6 | 1 | 2EK04510746 | NO | 2 | 460/3 | 31.5 | 35 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 6 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 47.3 | 50 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A4C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 26 | 1 | 2EK04512646 | NO | 2 | 460/3 | 60.9 | 70 | 895 | 6 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 26 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 575/3 | 20.1 | 25 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 40.6 | 45 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 26 | 1 | 2EK04512658 | NO | 2 | 575/3 | 51 | 60 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 26 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 575/3 | 21.5 | 25 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 42 | 45 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 26 | 1 | 2EK04512658 | NO | 2 | 575/3 | 52.4 | 60 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 26 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | - | - | - | NO | 2 | 575/3 | 24.3 | 30 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 44.8 | 45 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYEA7A5C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 78200 | 55600 | 12.0 EER2/17.0 IEER | 80 | 67 | 58.5 | 56.7 | 95 | 67000 | 3.4 | 38000 | 2.4 | 70 | 95.8 | 26 | 1 | 2EK04512658 | NO | 2 | 575/3 | 55.2 | 60 | 895 | 6 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 26 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 208/3 | 35.3 | 50 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 6.5 | 1 | 2EK04510625 | NO | 2 | 208/3 | 54.8 | 70 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 6.5 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 11 | 1 | 2EK04511125 | NO | 2 | 208/3 | 66.9 | 70 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 11 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 16 | 1 | 2EK04511625 | NO | 2 | 208/3 | 83.4 | 90 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 208/3 | 39.5 | 50 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 6.5 | 1 | 2EK04510625 | NO | 2 | 208/3 | 59 | 70 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 6.5 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 11 | 1 | 2EK04511125 | NO | 2 | 208/3 | 71.1 | 80 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 11 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 16 | 1 | 2EK04511625 | NO | 2 | 208/3 | 87.6 | 90 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 208/3 | 39.5 | 50 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 6.5 | 1 | 2EK04510625 | NO | 2 | 208/3 | 59 | 70 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 6.5 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 11 | 1 | 2EK04511125 | NO | 2 | 208/3 | 71.1 | 80 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 11 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A2C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 16 | 1 | 2EK04511625 | NO | 2 | 208/3 | 87.6 | 90 | 652 | 6 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 460/3 | 17.3 | 25 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 6 | 1 | 2EK04510646 | NO | 2 | 460/3 | 26.3 | 30 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 6 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 12 | 1 | 2EK04511146 | NO | 2 | 460/3 | 34.6 | 40 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 12 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 14 | 1 | 2EK04511446 | NO | 2 | 460/3 | 38.3 | 40 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 14 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 460/3 | 18.8 | 25 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 6 | 1 | 2EK04510646 | NO | 2 | 460/3 | 27.8 | 35 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 6 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 12 | 1 | 2EK04511146 | NO | 2 | 460/3 | 36.1 | 40 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 12 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 14 | 1 | 2EK04511446 | NO | 2 | 460/3 | 39.8 | 40 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 14 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 460/3 | 18.8 | 25 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 6 | 1 | 2EK04510646 | NO | 2 | 460/3 | 27.8 | 35 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 6 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 12 | 1 | 2EK04511146 | NO | 2 | 460/3 | 36.1 | 40 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 12 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A4C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | 14 | 1 | 2EK04511446 | NO | 2 | 460/3 | 39.8 | 40 | 652 | 6 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 14 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A5A3AA5A111A1 | 6 | 2400 | STANDARD STATIC | - | 2.4 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 575/3 | 12.3 | 15 | 652 | 6 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A5B3AA5A111A1 | 6 | 2400 | MEDIUM STATIC | - | 2.9 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 575/3 | 13.7 | 15 | 652 | 6 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXEA7A5C3AA5A111A1 | 6 | 2400 | HIGH STATIC | - | 3.7 | 75600 | 54900 | 11.0 EER/15.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 65000 | 3.5 | 38000 | 2.3 | 70 | 95.1 | - | - | - | NO | 2 | 575/3 | 16.5 | 20 | 652 | 6 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00P2A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 208/3 | 33.9 | 40 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09P2A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | NO | 2 | 208/3 | 61 | 70 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18P2A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 88 | 90 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24P2A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 106 | 110 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36P2A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 136.2 | 150 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00P2A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | YES | 2 | 208/3 | 33.9 | 40 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09P2A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | YES | 2 | 208/3 | 61 | 70 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18P2A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 88 | 90 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24P2A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 106 | 110 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36P2A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 136.2 | 150 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00R2A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 208/3 | 33.9 | 40 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09R2A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | NO | 2 | 208/3 | 61 | 70 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18R2A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 88 | 90 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24R2A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 106 | 110 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36R2A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 136.2 | 150 | 1080 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00R2A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | YES | 2 | 208/3 | 33.9 | 40 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09R2A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | YES | 2 | 208/3 | 61 | 70 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18R2A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 88 | 90 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24R2A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 106 | 110 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36R2A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 136.2 | 150 | 1100 | 6.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00P4A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 460/3 | 17.8 | 20 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09P4A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | NO | 2 | 460/3 | 31.3 | 35 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18P4A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 44.9 | 45 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24P4A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 53.9 | 60 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36P4A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 68.9 | 70 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00P4A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | YES | 2 | 460/3 | 17.8 | 20 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09P4A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | YES | 2 | 460/3 | 31.3 | 35 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18P4A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 44.9 | 45 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24P4A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 53.9 | 60 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36P4A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 68.9 | 70 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00R4A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 460/3 | 17.8 | 20 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09R4A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | NO | 2 | 460/3 | 31.3 | 35 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18R4A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 44.9 | 45 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24R4A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 53.9 | 60 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36R4A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 68.9 | 70 | 1080 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00R4A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | YES | 2 | 460/3 | 17.8 | 20 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09R4A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | YES | 2 | 460/3 | 31.3 | 35 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18R4A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 44.9 | 45 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24R4A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 53.9 | 60 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36R4A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 68.9 | 70 | 1100 | 6.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00P5A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 575/3 | 13.1 | 15 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09P5A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | NO | 2 | 575/3 | 24 | 25 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18P5A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | NO | 2 | 575/3 | 34.7 | 35 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24P5A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | NO | 2 | 575/3 | 42 | 45 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36P5A1AAAA1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | NO | 2 | 575/3 | 54 | 60 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00P5A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | YES | 2 | 575/3 | 13.1 | 15 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09P5A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | YES | 2 | 575/3 | 24 | 25 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18P5A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | YES | 2 | 575/3 | 34.7 | 35 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24P5A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | YES | 2 | 575/3 | 42 | 45 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36P5A1AAAE1A1 | 6.5 | 2600 | STANDARD STATIC | - | 1.5 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | YES | 2 | 575/3 | 54 | 60 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00R5A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 575/3 | 13.1 | 15 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09R5A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | NO | 2 | 575/3 | 24 | 25 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18R5A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | NO | 2 | 575/3 | 34.7 | 35 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24R5A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | NO | 2 | 575/3 | 42 | 45 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36R5A1AAAA1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | NO | 2 | 575/3 | 54 | 60 | 1080 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078C00R5A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | - | - | - | YES | 2 | 575/3 | 13.1 | 15 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E09R5A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 9 | 1 | FACTORY | YES | 2 | 575/3 | 24 | 25 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E18R5A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 18 | 2 | FACTORY | YES | 2 | 575/3 | 34.7 | 35 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E24R5A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 24 | 2 | FACTORY | YES | 2 | 575/3 | 42 | 45 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP078E36R5A1AAAE1A1 | 6.5 | 2600 | HIGH STATIC | - | 2 | 88800 | 62400 | 12.2 EER/15.8 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 75000 | 3.5 | 42000 | 2.25 | 70 | 96.7 | 34 | 2 | FACTORY | YES | 2 | 575/3 | 54 | 60 | 1100 | 6.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 208/3 | 43 | 50 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 90.5 | 100 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 117 | 125 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 25 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 138.7 | 150 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 32 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 138.8 | 150 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 42 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 208/3 | 43 | 50 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 90.5 | 100 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 117 | 125 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 25 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 138.7 | 150 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 32 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 138.8 | 150 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 42 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 208/3 | 47.2 | 60 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 94.7 | 100 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 16 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 121.2 | 125 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 25 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 142.9 | 150 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 32 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A2C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 144 | 150 | 1060 | 7.5 | 208/3 | HIGH | WY - OMNI CORE HIGH EFF | 42 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 460/3 | 21.3 | 25 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 46.1 | 50 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 63.1 | 70 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 28 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 70.9 | 80 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 33 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 68.5 | 70 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 42 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 460/3 | 21.3 | 25 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 46.1 | 50 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 63.1 | 70 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 28 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 70.9 | 80 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 33 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 68.5 | 70 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 42 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 460/3 | 22.8 | 25 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 47.6 | 50 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 64.6 | 70 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 28 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 72.4 | 80 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 33 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A4C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 70.4 | 80 | 1060 | 7.5 | 460/3 | HIGH | WY - OMNI CORE HIGH EFF | 42 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 575/3 | 17.2 | 20 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 37.7 | 40 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5A3AA5A111A1 | 7.5 | 2850 | STANDARD STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 58.1 | 60 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 575/3 | 17.2 | 20 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 37.7 | 40 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5B3AA5A111A1 | 7.5 | 2850 | MEDIUM STATIC | - | 2.4 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 58.1 | 60 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 34 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | - | - | - | NO | 2 | 575/3 | 21.4 | 25 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 41.9 | 45 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WYE08A5C3AA5A111A1 | 7.5 | 2850 | HIGH STATIC | - | 3.7 | 93000 | - | 12.1 EER2/16.0 IEER | 80 | 67 | - | - | 95 | 85000 | 3.5 | 49000 | 2.35 | 70 | 97.6 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 62.3 | 70 | 1060 | 7.5 | 575/3 | HIGH | WY - OMNI CORE HIGH EFF | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 208/3 | 41.1 | 50 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 89.2 | 90 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 115.7 | 125 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 137.4 | 150 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 138.8 | 150 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 208/3 | 41.1 | 50 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 89.2 | 90 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 115.7 | 125 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 137.4 | 150 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 138.8 | 150 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 208/3 | 45.3 | 50 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 93.4 | 100 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 119.9 | 125 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 141.6 | 150 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A2C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 144 | 150 | 976 | 7.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 460/3 | 21.6 | 25 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 46.4 | 50 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 63.4 | 70 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 71.2 | 80 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 68.5 | 70 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 460/3 | 21.6 | 25 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 46.4 | 50 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 63.4 | 70 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 71.2 | 80 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 68.5 | 70 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 460/3 | 23.1 | 25 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 47.9 | 50 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 64.9 | 70 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 72.7 | 80 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A4C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 70.4 | 80 | 976 | 7.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 575/3 | 17 | 20 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 37.5 | 40 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5A3AA5A111A1 | 7.5 | 3000 | STANDARD STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 57.9 | 60 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 575/3 | 17 | 20 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 37.5 | 40 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5B3AA5A111A1 | 7.5 | 3000 | MEDIUM STATIC | - | 2.4 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 57.9 | 60 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 575/3 | 21.2 | 25 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 41.7 | 45 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE08A5C3AA5A111A1 | 7.5 | 3000 | HIGH STATIC | - | 3.7 | 100400 | 72200 | 11.5 EER/15.4 IEER | 80 | 67 | 57.7 | 56.3 | 95 | 85000 | 3.5 | 49000 | 2.25 | 70 | 96.2 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 62.1 | 70 | 976 | 7.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00P2A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | NO | 2 | 208/3 | 39.3 | 50 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09P2A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | NO | 2 | 208/3 | 66.4 | 70 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18P2A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 93.4 | 100 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24P2A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 111.4 | 125 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36P2A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 141.6 | 150 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00P2A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | YES | 2 | 208/3 | 39.3 | 50 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09P2A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | YES | 2 | 208/3 | 66.4 | 70 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18P2A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 93.4 | 100 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24P2A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 111.4 | 125 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36P2A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 141.6 | 150 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00R2A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | NO | 2 | 208/3 | 43.8 | 50 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09R2A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | NO | 2 | 208/3 | 70.9 | 80 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18R2A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 97.9 | 100 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24R2A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 115.9 | 125 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36R2A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 146.1 | 150 | 1090 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00R2A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | YES | 2 | 208/3 | 43.8 | 50 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09R2A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | YES | 2 | 208/3 | 70.9 | 80 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18R2A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 97.9 | 100 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24R2A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 115.9 | 125 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36R2A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 146.1 | 150 | 1140 | 7.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00P4A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | NO | 2 | 460/3 | 21 | 25 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09P4A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | NO | 2 | 460/3 | 34.5 | 35 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18P4A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 48.1 | 50 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24P4A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 57.1 | 60 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36P4A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 72.1 | 80 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00P4A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | YES | 2 | 460/3 | 21 | 25 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09P4A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | YES | 2 | 460/3 | 34.5 | 35 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18P4A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 48.1 | 50 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24P4A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 57.1 | 60 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36P4A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 72.1 | 80 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00R4A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | NO | 2 | 460/3 | 22.5 | 25 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09R4A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | NO | 2 | 460/3 | 36 | 40 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18R4A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 49.6 | 50 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24R4A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 58.6 | 60 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36R4A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 73.6 | 80 | 1090 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00R4A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | YES | 2 | 460/3 | 22.5 | 25 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09R4A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | YES | 2 | 460/3 | 36 | 40 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18R4A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 49.6 | 50 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24R4A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 58.6 | 60 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36R4A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 73.6 | 80 | 1140 | 7.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00P5A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | NO | 2 | 575/3 | 14.7 | 15 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09P5A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | NO | 2 | 575/3 | 25.6 | 30 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18P5A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | NO | 2 | 575/3 | 36.3 | 40 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24P5A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | NO | 2 | 575/3 | 43.6 | 45 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36P5A1AAAA1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | NO | 2 | 575/3 | 55.6 | 60 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00P5A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | YES | 2 | 575/3 | 14.7 | 15 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09P5A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | YES | 2 | 575/3 | 25.6 | 30 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18P5A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | YES | 2 | 575/3 | 36.3 | 40 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24P5A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | YES | 2 | 575/3 | 43.6 | 45 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36P5A1AAAE1A1 | 7.5 | 3000 | STANDARD STATIC | - | 1.5 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | YES | 2 | 575/3 | 55.6 | 60 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00R5A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | NO | 2 | 575/3 | 16.2 | 20 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09R5A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | NO | 2 | 575/3 | 27.1 | 30 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18R5A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | NO | 2 | 575/3 | 37.8 | 40 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24R5A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | NO | 2 | 575/3 | 45.1 | 50 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36R5A1AAAA1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | NO | 2 | 575/3 | 57.1 | 60 | 1090 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090C00R5A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | - | - | - | YES | 2 | 575/3 | 16.2 | 20 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E09R5A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 9 | 1 | FACTORY | YES | 2 | 575/3 | 27.1 | 30 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E18R5A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 18 | 2 | FACTORY | YES | 2 | 575/3 | 37.8 | 40 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E24R5A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 24 | 2 | FACTORY | YES | 2 | 575/3 | 45.1 | 50 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP090E36R5A1AAAE1A1 | 7.5 | 3000 | HIGH STATIC | - | 3 | 102200 | 71900 | 12.2 EER/16.0 IEER | 80 | 67 | 57.8 | 56.1 | 95 | 87000 | 3.5 | 51000 | 2.25 | 70 | 96.9 | 34 | 2 | FACTORY | YES | 2 | 575/3 | 57.1 | 60 | 1140 | 7.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 208/3 | 44 | 50 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 92.1 | 100 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 118.6 | 125 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 140.3 | 150 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 138.8 | 150 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 208/3 | 44 | 50 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 92.1 | 100 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 118.6 | 125 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 140.3 | 150 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 138.8 | 150 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 208/3 | 48.2 | 60 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 96.3 | 100 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 122.8 | 125 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 144.5 | 150 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A2C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 144 | 150 | 1040 | 8.5 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 460/3 | 21.6 | 25 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 46.4 | 50 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 63.4 | 70 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 71.2 | 80 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 68.5 | 70 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 460/3 | 21.6 | 25 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 46.4 | 50 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 63.4 | 70 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 71.2 | 80 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 68.5 | 70 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 460/3 | 23.1 | 25 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 47.9 | 50 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 64.9 | 70 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 72.7 | 80 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A4C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 70.4 | 80 | 1040 | 8.5 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 575/3 | 17 | 20 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 37.5 | 40 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5A3AA5A111A1 | 8.5 | 3400 | STANDARD STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 57.9 | 60 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 575/3 | 17 | 20 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 37.5 | 40 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5B3AA5A111A1 | 8.5 | 3400 | MEDIUM STATIC | - | 2.4 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 57.9 | 60 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | - | - | - | NO | 2 | 575/3 | 21.2 | 25 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 41.7 | 45 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE09A5C3AA5A111A1 | 8.5 | 3400 | HIGH STATIC | - | 3.7 | 113500 | 80100 | 11.8 EER/15.4 IEER | 80 | 67 | 58.2 | 56.4 | 95 | 98000 | 3.4 | 56000 | 2.25 | 70 | 96.7 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 62.1 | 70 | 1040 | 8.5 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00P2A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | NO | 2 | 208/3 | 42 | 50 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09P2A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | NO | 2 | 208/3 | 69.1 | 70 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18P2A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 96.1 | 100 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24P2A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 114.1 | 125 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36P2A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 144.3 | 150 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00P2A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | YES | 2 | 208/3 | 42 | 50 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09P2A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | YES | 2 | 208/3 | 69.1 | 70 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18P2A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 96.1 | 100 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24P2A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 114.1 | 125 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36P2A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 144.3 | 150 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00R2A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | NO | 2 | 208/3 | 46.2 | 50 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09R2A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | NO | 2 | 208/3 | 73.3 | 80 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18R2A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 100.3 | 110 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24R2A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 118.3 | 125 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36R2A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 148.5 | 150 | 1137 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00R2A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | YES | 2 | 208/3 | 46.2 | 50 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09R2A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | YES | 2 | 208/3 | 73.3 | 80 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18R2A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 100.3 | 110 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24R2A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 118.3 | 125 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36R2A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 148.5 | 150 | 1140 | 8.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00P4A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | NO | 2 | 460/3 | 20.8 | 25 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09P4A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | NO | 2 | 460/3 | 34.3 | 35 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18P4A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 47.9 | 50 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24P4A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 56.9 | 60 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36P4A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 71.9 | 80 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00P4A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | YES | 2 | 460/3 | 20.8 | 25 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09P4A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | YES | 2 | 460/3 | 34.3 | 35 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18P4A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 47.9 | 50 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24P4A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 56.9 | 60 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36P4A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 71.9 | 80 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00R4A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | NO | 2 | 460/3 | 22.3 | 25 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09R4A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | NO | 2 | 460/3 | 35.8 | 40 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18R4A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 49.4 | 50 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24R4A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 58.4 | 60 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36R4A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 73.4 | 80 | 1137 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00R4A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | YES | 2 | 460/3 | 22.3 | 25 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09R4A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | YES | 2 | 460/3 | 35.8 | 40 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18R4A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 49.4 | 50 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24R4A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 58.4 | 60 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36R4A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 73.4 | 80 | 1140 | 8.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00P5A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | NO | 2 | 575/3 | 17.2 | 20 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09P5A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | NO | 2 | 575/3 | 28.1 | 30 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18P5A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | NO | 2 | 575/3 | 38.8 | 40 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24P5A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | NO | 2 | 575/3 | 46.1 | 50 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36P5A1AAAA1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | NO | 2 | 575/3 | 58.1 | 60 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00P5A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | YES | 2 | 575/3 | 17.2 | 20 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09P5A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | YES | 2 | 575/3 | 28.1 | 30 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18P5A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | YES | 2 | 575/3 | 38.8 | 40 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24P5A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | YES | 2 | 575/3 | 46.1 | 50 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36P5A1AAAE1A1 | 8.5 | 3400 | STANDARD STATIC | - | 2 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | YES | 2 | 575/3 | 58.1 | 60 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00R5A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | NO | 2 | 575/3 | 18.6 | 20 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09R5A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | NO | 2 | 575/3 | 29.5 | 30 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18R5A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | NO | 2 | 575/3 | 40.2 | 45 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24R5A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | NO | 2 | 575/3 | 47.5 | 50 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36R5A1AAAA1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | NO | 2 | 575/3 | 59.5 | 60 | 1137 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102C00R5A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | - | - | - | YES | 2 | 575/3 | 18.6 | 20 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E09R5A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 9 | 1 | FACTORY | YES | 2 | 575/3 | 29.5 | 30 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 9 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E18R5A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 18 | 2 | FACTORY | YES | 2 | 575/3 | 40.2 | 45 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E24R5A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 24 | 2 | FACTORY | YES | 2 | 575/3 | 47.5 | 50 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP102E36R5A1AAAE1A1 | 8.5 | 3400 | HIGH STATIC | - | 3 | 107600 | 78000 | 11.5 EER/16.0 IEER | 80 | 67 | 58.8 | 57 | 95 | 92000 | 3.5 | 53000 | 2.25 | 70 | 95.1 | 34 | 2 | FACTORY | YES | 2 | 575/3 | 59.5 | 60 | 1140 | 8.5 | 575/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 208/3 | 54.1 | 70 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 101.6 | 110 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 128.1 | 150 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 149.8 | 150 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 138.8 | 150 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 208/3 | 58.3 | 70 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 105.8 | 110 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 132.3 | 150 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 154 | 175 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 144 | 150 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 208/3 | 65.5 | 80 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 16 | 1 | 2EK04511725 | NO | 2 | 208/3 | 113 | 125 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 16 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 25 | 1 | 2EK04512525 | NO | 2 | 208/3 | 139.5 | 150 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 25 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 32 | 1 | 2EK04513225 | NO | 2 | 208/3 | 161.2 | 175 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 32 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A2C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514225 | NO | 2 | 208/3 | 153 | 175 | 1060 | 10 | 208/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 460/3 | 25 | 30 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 49.8 | 50 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 66.8 | 70 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 74.6 | 80 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 68.5 | 70 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 460/3 | 26.5 | 30 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 51.3 | 60 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 68.3 | 70 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 76.1 | 80 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 70.4 | 80 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 460/3 | 30.3 | 35 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511746 | NO | 2 | 460/3 | 55.1 | 60 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 28 | 1 | 2EK04512846 | NO | 2 | 460/3 | 72.1 | 80 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 28 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 33 | 1 | 2EK04513346 | NO | 2 | 460/3 | 79.9 | 80 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 33 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A4C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 42 | 2 | 2EK04514246 | NO | 2 | 460/3 | 75.1 | 80 | 1060 | 10 | 460/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 42 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 575/3 | 21.7 | 25 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 42.2 | 45 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5A3AA5A111A1 | 10 | 4000 | STANDARD STATIC | - | 2.4 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 62.6 | 70 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 575/3 | 25.9 | 30 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 46.4 | 50 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5B3AA5A111A1 | 10 | 4000 | MEDIUM STATIC | - | 3.7 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 66.8 | 70 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | MEDIUM STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | - | - | - | NO | 2 | 575/3 | 25.9 | 30 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 17 | 1 | 2EK04511758 | NO | 2 | 575/3 | 46.4 | 50 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 17 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WXE12A5C3AA5A111A1 | 10 | 4000 | HIGH STATIC | - | 5.25 | 128000 | - | 11.2 EER/14.4 IEER | 80 | 67 | - | - | 95 | 113000 | 3.4 | 65000 | 2.25 | 70 | 96.2 | 34 | 1 | 2EK04513458 | NO | 2 | 575/3 | 66.8 | 70 | 1060 | 10 | 575/3 | STANDARD | WX - OMNI CORE STANDARD EFF | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Core WQ-WY-WX 3-10 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00P2A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | NO | 2 | 208/3 | 48.3 | 60 | 1135 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18P2A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 102.4 | 110 | 1135 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24P2A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 120.4 | 125 | 1135 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36P2A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 150.6 | 175 | 1135 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00P2A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | YES | 2 | 208/3 | 48.3 | 60 | 1160 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18P2A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 102.4 | 110 | 1160 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24P2A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 120.4 | 125 | 1160 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36P2A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 150.6 | 175 | 1160 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00R2A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | NO | 2 | 208/3 | 52.5 | 60 | 1135 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18R2A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 106.6 | 110 | 1135 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24R2A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 124.6 | 125 | 1135 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36R2A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 154.8 | 175 | 1135 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00R2A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | YES | 2 | 208/3 | 52.5 | 60 | 1160 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18R2A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 106.6 | 110 | 1160 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24R2A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 124.6 | 125 | 1160 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36R2A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 154.8 | 175 | 1160 | 10 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00P4A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | NO | 2 | 460/3 | 22.8 | 25 | 1135 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18P4A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 49.9 | 50 | 1135 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24P4A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 58.9 | 60 | 1135 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36P4A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 73.9 | 80 | 1135 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00P4A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | YES | 2 | 460/3 | 22.8 | 25 | 1160 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18P4A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 49.9 | 50 | 1160 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24P4A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 58.9 | 60 | 1160 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36P4A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 73.9 | 80 | 1160 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00R4A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | NO | 2 | 460/3 | 24.3 | 30 | 1135 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18R4A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 51.4 | 60 | 1135 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24R4A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 60.4 | 70 | 1135 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36R4A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 75.4 | 80 | 1135 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00R4A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | YES | 2 | 460/3 | 24.3 | 30 | 1160 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18R4A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 51.4 | 60 | 1160 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24R4A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 60.4 | 70 | 1160 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36R4A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 75.4 | 80 | 1160 | 10 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00P5A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | NO | 2 | 575/3 | 19.2 | 25 | 1135 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18P5A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | NO | 2 | 575/3 | 40.8 | 45 | 1135 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24P5A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | NO | 2 | 575/3 | 48.1 | 50 | 1135 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36P5A1AAAA1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | NO | 2 | 575/3 | 60.1 | 70 | 1135 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00P5A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | YES | 2 | 575/3 | 19.2 | 25 | 1160 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18P5A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | YES | 2 | 575/3 | 40.8 | 45 | 1160 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24P5A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | YES | 2 | 575/3 | 48.1 | 50 | 1160 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36P5A1AAAE1A1 | 10 | 4000 | STANDARD STATIC | - | 2 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | YES | 2 | 575/3 | 60.1 | 70 | 1160 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00R5A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | NO | 2 | 575/3 | 20.6 | 25 | 1135 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18R5A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | NO | 2 | 575/3 | 42.2 | 45 | 1135 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24R5A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | NO | 2 | 575/3 | 49.5 | 50 | 1135 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36R5A1AAAA1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | NO | 2 | 575/3 | 61.5 | 70 | 1135 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120C00R5A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | - | - | - | YES | 2 | 575/3 | 20.6 | 25 | 1160 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E18R5A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 18 | 2 | FACTORY | YES | 2 | 575/3 | 42.2 | 45 | 1160 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E24R5A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 24 | 2 | FACTORY | YES | 2 | 575/3 | 49.5 | 50 | 1160 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP120E36R5A1AAAE1A1 | 10 | 4000 | HIGH STATIC | - | 3 | 128700 | 91300 | 11.2 EER/15.2 IEER | 80 | 67 | 58.9 | 56.8 | 95 | 104000 | 3.5 | 60000 | 2.25 | 70 | 94.1 | 34 | 2 | FACTORY | YES | 2 | 575/3 | 61.5 | 70 | 1160 | 10 | 575/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150C00P2A1AAAA1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | - | - | - | NO | 2 | 208/3 | 77.6 | 100 | 1403 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E18P2A1AAAA1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 131.7 | 150 | 1403 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E24P2A1AAAA1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 149.7 | 150 | 1403 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E36P2A1AAAA1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 179.9 | 200 | 1403 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150C00P2A1AAAE1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | - | - | - | YES | 2 | 208/3 | 77.6 | 100 | 1470 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E18P2A1AAAE1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 131.7 | 150 | 1470 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E24P2A1AAAE1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 149.7 | 150 | 1470 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E36P2A1AAAE1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 179.9 | 200 | 1470 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150C00R2A1AAAA1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | - | - | - | NO | 2 | 208/3 | 84.8 | 100 | 1403 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E18R2A1AAAA1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 18 | 2 | FACTORY | NO | 2 | 208/3 | 138.9 | 150 | 1403 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E24R2A1AAAA1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 24 | 2 | FACTORY | NO | 2 | 208/3 | 156.9 | 175 | 1403 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E36R2A1AAAA1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 34 | 2 | FACTORY | NO | 2 | 208/3 | 187.1 | 200 | 1403 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150C00R2A1AAAE1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | - | - | - | YES | 2 | 208/3 | 84.8 | 100 | 1470 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E18R2A1AAAE1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 18 | 2 | FACTORY | YES | 2 | 208/3 | 138.9 | 150 | 1470 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E24R2A1AAAE1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 24 | 2 | FACTORY | YES | 2 | 208/3 | 156.9 | 175 | 1470 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E36R2A1AAAE1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 34 | 2 | FACTORY | YES | 2 | 208/3 | 187.1 | 200 | 1470 | 12.5 | 208/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150C00P4A1AAAA1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | - | - | - | NO | 2 | 460/3 | 32.3 | 40 | 1403 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E18P4A1AAAA1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 59.4 | 60 | 1403 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E24P4A1AAAA1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 68.4 | 70 | 1403 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E36P4A1AAAA1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 83.4 | 90 | 1403 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150C00P4A1AAAE1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | - | - | - | YES | 2 | 460/3 | 32.3 | 40 | 1470 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E18P4A1AAAE1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 59.4 | 60 | 1470 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E24P4A1AAAE1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 68.4 | 70 | 1470 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E36P4A1AAAE1A1 | 12.5 | 5000 | STANDARD STATIC | - | 3 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 83.4 | 90 | 1470 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | STANDARD STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150C00R4A1AAAA1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | - | - | - | NO | 2 | 460/3 | 36.4 | 45 | 1403 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E18R4A1AAAA1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 18 | 2 | FACTORY | NO | 2 | 460/3 | 63.5 | 70 | 1403 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E24R4A1AAAA1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 24 | 2 | FACTORY | NO | 2 | 460/3 | 72.5 | 80 | 1403 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E36R4A1AAAA1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 34 | 2 | FACTORY | NO | 2 | 460/3 | 87.5 | 90 | 1403 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | NO | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150C00R4A1AAAE1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | - | - | - | YES | 2 | 460/3 | 36.4 | 45 | 1470 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 0 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E18R4A1AAAE1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 18 | 2 | FACTORY | YES | 2 | 460/3 | 63.5 | 70 | 1470 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 18 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E24R4A1AAAE1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 24 | 2 | FACTORY | YES | 2 | 460/3 | 72.5 | 80 | 1470 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 24 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | WP150E36R4A1AAAE1A1 | 12.5 | 5000 | HIGH STATIC | - | 5 | 158000 | 110500 | 10.8 EER/15.2 IEER | 80 | 67 | 59.5 | 57 | 95 | 148000 | 3.3 | 84000 | 2.15 | 70 | 97.4 | 34 | 2 | FACTORY | YES | 2 | 460/3 | 87.5 | 90 | 1470 | 12.5 | 460/3 | STANDARD | WP - OMNI PRO | 34 | YES | HIGH STATIC | 2 |  | TempMaster Omni Pro WP 6.5-12.5 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP2A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 208/3 | 66.8 | 80 | 1750 | 12.5 | 208/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP2A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502525 | NO | 2 | 208/3 | 138.1 | 150 | 1750 | 12.5 | 208/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP2A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505025 | NO | 2 | 208/3 | 161.1 | 175 | 1750 | 12.5 | 208/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP2A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507525 | NO | 2 | 208/3 | 187.2 | 200 | 1750 | 12.5 | 208/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP2A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 208/3 | 69.4 | 90 | 1750 | 12.5 | 208/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP2A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502525 | NO | 2 | 208/3 | 140.5 | 150 | 1750 | 12.5 | 208/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP2A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505025 | NO | 2 | 208/3 | 163.5 | 175 | 1750 | 12.5 | 208/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP2A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507525 | NO | 2 | 208/3 | 190.2 | 200 | 1750 | 12.5 | 208/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP4A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 460/3 | 31.2 | 40 | 1750 | 12.5 | 460/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP4A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502546 | NO | 2 | 460/3 | 67.3 | 70 | 1750 | 12.5 | 460/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP4A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505046 | NO | 2 | 460/3 | 79.3 | 80 | 1750 | 12.5 | 460/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP4A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507546 | NO | 2 | 460/3 | 93.7 | 100 | 1750 | 12.5 | 460/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP4A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 460/3 | 32.2 | 40 | 1750 | 12.5 | 460/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP4A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502546 | NO | 2 | 460/3 | 68.3 | 70 | 1750 | 12.5 | 460/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP4A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505046 | NO | 2 | 460/3 | 80.5 | 90 | 1750 | 12.5 | 460/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP4A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507546 | NO | 2 | 460/3 | 94.9 | 100 | 1750 | 12.5 | 460/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP5A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 575/3 | 26.5 | 35 | 1750 | 12.5 | 575/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP5A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502558 | NO | 2 | 575/3 | 55.3 | 60 | 1750 | 12.5 | 575/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP5A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505058 | NO | 2 | 575/3 | 65.3 | 70 | 1750 | 12.5 | 575/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0EP5A1AAA81A1 | 12.5 | 5000 | STANDARD STATIC | - | 2 x 2.69 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507558 | NO | 2 | 575/3 | 76.9 | 80 | 1750 | 12.5 | 575/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP5A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 575/3 | 26.7 | 35 | 1750 | 12.5 | 575/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP5A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502558 | NO | 2 | 575/3 | 55.5 | 60 | 1750 | 12.5 | 575/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP5A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505058 | NO | 2 | 575/3 | 65.5 | 70 | 1750 | 12.5 | 575/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV13C0FP5A1AAA81A1 | 12.5 | 5000 | HIGH STATIC | - | 2 x 3.24 | 150600 | 113000 | 10.9 EER/14.2 IEER | 80 | 67 | 59.1 | 57.5 | 95 | 136000 | 3.3 | 80000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507558 | NO | 2 | 575/3 | 77.1 | 80 | 1750 | 12.5 | 575/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP2A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | - | - | - | NO | 2 | 208/3 | 82.9 | 110 | 1985 | 15 | 208/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP2A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 23 | 1 | 2EL04502525 | NO | 2 | 208/3 | 155.1 | 175 | 1985 | 15 | 208/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP2A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 45.9 | 2 | 2EL04505025 | NO | 2 | 208/3 | 178.1 | 200 | 1985 | 15 | 208/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP2A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 68.9 | 2 | 2EL04507525 | NO | 2 | 208/3 | 190.9 | 200 | 1985 | 15 | 208/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP2A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | - | - | - | NO | 2 | 208/3 | 85.3 | 110 | 1985 | 15 | 208/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP2A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 23 | 1 | 2EL04502525 | NO | 2 | 208/3 | 157.5 | 175 | 1985 | 15 | 208/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP2A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 45.9 | 2 | 2EL04505025 | NO | 2 | 208/3 | 180.5 | 200 | 1985 | 15 | 208/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP2A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 68.9 | 2 | 2EL04507525 | NO | 2 | 208/3 | 193.3 | 200 | 1985 | 15 | 208/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP4A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | - | - | - | NO | 2 | 460/3 | 36.9 | 45 | 1985 | 15 | 460/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP4A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 23 | 1 | 2EL04502546 | NO | 2 | 460/3 | 73 | 80 | 1985 | 15 | 460/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP4A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 45.9 | 2 | 2EL04505046 | NO | 2 | 460/3 | 84.4 | 90 | 1985 | 15 | 460/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP4A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 68.9 | 2 | 2EL04507546 | NO | 2 | 460/3 | 93.7 | 100 | 1985 | 15 | 460/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP4A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | - | - | - | NO | 2 | 460/3 | 37.9 | 45 | 1985 | 15 | 460/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP4A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 23 | 1 | 2EL04502546 | NO | 2 | 460/3 | 74 | 80 | 1985 | 15 | 460/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP4A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 45.9 | 2 | 2EL04505046 | NO | 2 | 460/3 | 85.4 | 90 | 1985 | 15 | 460/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP4A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 68.9 | 2 | 2EL04507546 | NO | 2 | 460/3 | 94.9 | 100 | 1985 | 15 | 460/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP5A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | - | - | - | NO | 2 | 575/3 | 30.5 | 35 | 1985 | 15 | 575/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP5A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 23 | 1 | 2EL04502558 | NO | 2 | 575/3 | 59.3 | 60 | 1985 | 15 | 575/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP5A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 45.9 | 2 | 2EL04505058 | NO | 2 | 575/3 | 68.5 | 70 | 1985 | 15 | 575/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0EP5A1AAA81A1 | 15 | 6000 | STANDARD STATIC | - | 2 x 2.69 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 68.9 | 2 | 2EL04507558 | NO | 2 | 575/3 | 76.9 | 80 | 1985 | 15 | 575/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP5A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | - | - | - | NO | 2 | 575/3 | 30.7 | 35 | 1985 | 15 | 575/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP5A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 23 | 1 | 2EL04502558 | NO | 2 | 575/3 | 59.5 | 60 | 1985 | 15 | 575/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP5A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 45.9 | 2 | 2EL04505058 | NO | 2 | 575/3 | 68.7 | 70 | 1985 | 15 | 575/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV15C0FP5A1AAA81A1 | 15 | 6000 | HIGH STATIC | - | 2 x 3.24 | 190100 | 143600 | 10.9 EER/13.8 IEER | 80 | 67 | 57.8 | 57 | 95 | 172000 | 3.3 | 100000 | 2.05 | 70 | 96.5 | 68.9 | 2 | 2EL04507558 | NO | 2 | 575/3 | 77.1 | 80 | 1985 | 15 | 575/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP2A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 208/3 | 99.7 | 125 | 2270 | 20 | 208/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP2A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502525 | NO | 2 | 208/3 | 171.5 | 175 | 2270 | 20 | 208/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP2A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505025 | NO | 2 | 208/3 | 194.5 | 200 | 2270 | 20 | 208/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP2A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507525 | NO | 2 | 208/3 | 207.3 | 225 | 2270 | 20 | 208/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP2A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 208/3 | 102.1 | 125 | 2270 | 20 | 208/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP2A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502525 | NO | 2 | 208/3 | 173.3 | 175 | 2270 | 20 | 208/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP2A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505025 | NO | 2 | 208/3 | 196.3 | 200 | 2270 | 20 | 208/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP2A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507525 | NO | 2 | 208/3 | 209.1 | 225 | 2270 | 20 | 208/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP4A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 460/3 | 47.8 | 60 | 2270 | 20 | 460/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP4A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502546 | NO | 2 | 460/3 | 83.9 | 90 | 2270 | 20 | 460/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP4A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505046 | NO | 2 | 460/3 | 95.3 | 100 | 2270 | 20 | 460/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP4A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507546 | NO | 2 | 460/3 | 101.8 | 110 | 2270 | 20 | 460/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP4A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 460/3 | 49.4 | 60 | 2270 | 20 | 460/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP4A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502546 | NO | 2 | 460/3 | 85.5 | 90 | 2270 | 20 | 460/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP4A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505046 | NO | 2 | 460/3 | 96.9 | 100 | 2270 | 20 | 460/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP4A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507546 | NO | 2 | 460/3 | 103.4 | 110 | 2270 | 20 | 460/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP5A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 575/3 | 39.6 | 50 | 2270 | 20 | 575/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP5A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502558 | NO | 2 | 575/3 | 68.5 | 70 | 2270 | 20 | 575/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP5A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505058 | NO | 2 | 575/3 | 77.6 | 80 | 2270 | 20 | 575/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0EP5A1AAA81A1 | 20 | 8000 | STANDARD STATIC | - | 2 x 4.82 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507558 | NO | 2 | 575/3 | 82.8 | 90 | 2270 | 20 | 575/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP5A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | - | - | - | NO | 2 | 575/3 | 40.4 | 50 | 2270 | 20 | 575/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP5A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 23 | 1 | 2EL04502558 | NO | 2 | 575/3 | 69.3 | 70 | 2270 | 20 | 575/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP5A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 45.9 | 2 | 2EL04505058 | NO | 2 | 575/3 | 78.4 | 80 | 2270 | 20 | 575/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV20C0FP5A1AAA81A1 | 20 | 8000 | HIGH STATIC | - | 2 x 5.66 | 251200 | 188400 | 10.9 EER/13.8 IEER | 80 | 67 | 58.2 | 57.1 | 95 | 218000 | 3.2 | 126000 | 2.05 | 70 | 95.2 | 68.9 | 2 | 2EL04507558 | NO | 2 | 575/3 | 83.6 | 90 | 2270 | 20 | 575/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP2A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | - | - | - | NO | 2 | 208/3 | 121.8 | 150 | 2450 | 25 | 208/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP2A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 23 | 1 | 2EL04502525 | NO | 2 | 208/3 | 192.3 | 200 | 2450 | 25 | 208/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP2A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 45.9 | 2 | 2EL04505025 | NO | 2 | 208/3 | 215.3 | 225 | 2450 | 25 | 208/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP2A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 68.9 | 2 | 2EL04507525 | NO | 2 | 208/3 | 228.2 | 250 | 2450 | 25 | 208/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP2A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | - | - | - | NO | 2 | 208/3 | 124.2 | 150 | 2450 | 25 | 208/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP2A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 23 | 1 | 2EL04502525 | NO | 2 | 208/3 | 194.1 | 200 | 2450 | 25 | 208/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP2A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 45.9 | 2 | 2EL04505025 | NO | 2 | 208/3 | 217.1 | 225 | 2450 | 25 | 208/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP2A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 68.9 | 2 | 2EL04507525 | NO | 2 | 208/3 | 230 | 250 | 2450 | 25 | 208/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP4A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | - | - | - | NO | 2 | 460/3 | 57.9 | 70 | 2450 | 25 | 460/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP4A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 23 | 1 | 2EL04502546 | NO | 2 | 460/3 | 94 | 100 | 2450 | 25 | 460/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP4A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 45.9 | 2 | 2EL04505046 | NO | 2 | 460/3 | 105.4 | 110 | 2450 | 25 | 460/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP4A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 68.9 | 2 | 2EL04507546 | NO | 2 | 460/3 | 111.9 | 125 | 2450 | 25 | 460/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP4A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | - | - | - | NO | 2 | 460/3 | 59.5 | 70 | 2450 | 25 | 460/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP4A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 23 | 1 | 2EL04502546 | NO | 2 | 460/3 | 95.6 | 100 | 2450 | 25 | 460/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP4A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 45.9 | 2 | 2EL04505046 | NO | 2 | 460/3 | 107 | 110 | 2450 | 25 | 460/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP4A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 68.9 | 2 | 2EL04507546 | NO | 2 | 460/3 | 113.5 | 125 | 2450 | 25 | 460/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP5A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | - | - | - | NO | 2 | 575/3 | 43.2 | 50 | 2450 | 25 | 575/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP5A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 23 | 1 | 2EL04502558 | NO | 2 | 575/3 | 72.1 | 80 | 2450 | 25 | 575/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP5A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 45.9 | 2 | 2EL04505058 | NO | 2 | 575/3 | 81.2 | 90 | 2450 | 25 | 575/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0EP5A1AAA81A1 | 25 | 10000 | STANDARD STATIC | - | 2 x 4.82 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 68.9 | 2 | 2EL04507558 | NO | 2 | 575/3 | 86.4 | 90 | 2450 | 25 | 575/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | STANDARD STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP5A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | - | - | - | NO | 2 | 575/3 | 44 | 50 | 2450 | 25 | 575/3 | STANDARD | MV - OMNI CHOICE | 0 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP5A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 23 | 1 | 2EL04502558 | NO | 2 | 575/3 | 72.9 | 80 | 2450 | 25 | 575/3 | STANDARD | MV - OMNI CHOICE | 23 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP5A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 45.9 | 2 | 2EL04505058 | NO | 2 | 575/3 | 82 | 90 | 2450 | 25 | 575/3 | STANDARD | MV - OMNI CHOICE | 45.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide
TEMPMASTER | MV25C0FP5A1AAA81A1 | 25 | 10000 | HIGH STATIC | - | 2 x 5.66 | 293300 | 225800 | 10.2 EER/13.6 IEER | 80 | 67 | 59.1 | 57.8 | 95 | 278000 | 3.2 | 162000 | 2.05 | 70 | 95.7 | 68.9 | 2 | 2EL04507558 | NO | 2 | 575/3 | 87.2 | 90 | 2450 | 25 | 575/3 | STANDARD | MV - OMNI CHOICE | 68.9 | NO | HIGH STATIC | 2 |  | TempMaster Omni Choice MV 12.5-25 Ton Heat Pump Technical Guide

## SCHEDULE NOTES
Provide with factory installed refrigerant detection system (RDS) as required for R-454B.
Provide with economizer with enthalpy sensor
Provide with factory installed disconnect
Provide with factory installed, field powered 115V GFCI outlet
Provide with 7-day programmable thermostat
Provide with 7-day programmable BACnet thermostat
Provide with factory installed DDC controller with BAS input and 7-day programmable thermostat
Provide with 24" factory roofcurb

## SOURCES
Rows generated from the TempMaster R-454B heat pump technical guides (downloaded 2026-10-21) - not hand-run selections:
Omni Core WQ/WY/WX 3-10 ton Heat Pump; Omni Pro WP 6.5-12.5 ton Standard Efficiency Heat Pump; Omni Choice MV 12.5-25 ton Standard Efficiency Heat Pump.
One row per cabinet x voltage x blower option x hot gas reheat (WP only) x electric heat option. The site folds the electric heat options into a kW dropdown.
Cooling: 80F DB / 67F WB entering air, 95F ambient, at 400 CFM/ton (a printed point in every capacity table). Gross total and sensible (80F return DB column) as published.
LDB = 80 - sensible / (1.08 x CFM); LWB from the total/sensible capacity at sea level (standard psychrometrics). The guides do not print either.
Heat pump heating: AHRI 47F and 17F capacity and COP from the physical data tables (heat pump / electric heat values, not dual fuel), 70F EAT. LAT @ 47F = 70 + capacity / (1.08 x CFM) at the scheduled CFM (the AHRI rating CFM differs slightly).
Efficiency: AHRI ratings - 3-5 ton WQ/WY SEER2/EER2/HSPF2; 6 ton and up EER (EER2 as printed for WY) / IEER (IntelliSpeed).
Electric heat: WQ/WY/WX and MV are field-installed heater kits (kit number shown; the unit model number does not change). WP heaters are factory installed (E09-E54 in the model number).
kW is the 230 V (nameplate) rating for 208/230 V units; MCA / MOCP are the larger of the 208 V and 230 V rows (max fuse / breaker) from the electrical tables without powered convenience outlet or power exhaust.
Electrical tables used: WQ guide tables 81, 83, 85, 87, 88, 91, 92, 95, 96, 99, 101, 103 (6-10 ton: VFD IntelliSpeed); WP tables 35, 36; MV tables 47 (standard static), 53 (high static).
Indoor motor: direct drive HP (3-5 ton standard static); belt drive motors are shown as the max BHP printed in the physical data (1.5 HP for the single-phase medium static motor). WP: motor HP from table 30. MV: two plenum fans, HP each.
Weight: operating weight from the physical data / weight tables (WP with MagnaDry hot gas reheat from table 40).
ESP: not determined by the catalog ratings - set per job from the blower tables.
Model numbers: base configuration with no factory options other than the refrigerant detection system (WQ/WY/WX sensor digit 5, WP RDS digit A, MV refrigeration digit 8). WQ/WY/WX airflow A/B/C = standard/medium/high static, 6-10 ton option 3 = VFD IntelliSpeed; WP blower P/R = IntelliSpeed standard/high static, refrigeration E = hot gas reheat; MV blower E/F = standard/high static, air volume P = IntelliSpeed 2-stage. Confirm in the selection software before ordering.
Not included: dual fuel (gas heat) WP/MV configurations; MV medium static (VFD) blower - same model blower code as standard static; 575 V WP150 (no electrical table printed); 1-phase high static (3-phase only).
Catalog problems found:
WYE08 cooling table (guide table 15, p.37) is scrambled - capacity rises as entering WB falls and runs ~20% over the AHRI rating. Scheduled at the AHRI A point instead: 93,000 Btu/h gross at 2,850 CFM; sensible / LDB / LWB left blank.
WXE12 cooling table (guide table 29, p.51) prints sensible at 67F WB equal across return DB columns (or equal to total). Total used as printed; sensible / LDB / LWB left blank.
Heater option left out - WP120 standard static 230-3-60: E54 54 kW printed MCA 150.6 / MOCP 175 - identical to the E36 row
Heater option left out - WP120 high static 230-3-60: E54 54 kW printed MCA 154.8 / MOCP 175 - identical to the E36 row
Heater option left out - WP120 standard static 460-3-60: E54 54 kW printed MCA 73.9 / MOCP 80 - identical to the E36 row
Heater option left out - WP120 high static 460-3-60: E54 54 kW printed MCA 75.4 / MOCP 80 - identical to the E36 row
Heater option left out - WP120 standard static 575-3-60: E54 54 kW printed MCA 60.1 / MOCP 70 - identical to the E36 row
Heater option left out - WP120 high static 575-3-60: E54 54 kW printed MCA 61.5 / MOCP 70 - identical to the E36 row
Heater option left out - WP150 standard static 208-3-60: E54 40.6 kW printed MCA 166.1 / MOCP 175 - identical to the E36 row
Heater option left out - WP150 standard static 230-3-60: E54 54 kW printed MCA 179.9 / MOCP 200 - identical to the E36 row
Heater option left out - WP150 high static 208-3-60: E54 40.6 kW printed MCA 173.3 / MOCP 175 - identical to the E36 row
Heater option left out - WP150 high static 230-3-60: E54 54 kW printed MCA 187.1 / MOCP 200 - identical to the E36 row
Heater option left out - WP150 standard static 460-3-60: E54 54 kW printed MCA 83.4 / MOCP 90 - identical to the E36 row
Heater option left out - WP150 high static 460-3-60: E54 54 kW printed MCA 87.5 / MOCP 90 - identical to the E36 row